## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_624_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_624_0_node_53 | 20 | n |  | TRUE
2 | bus_MV_624_0_node_51 | 20 | n |  | TRUE
3 | bus_MV_624_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_624_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_624_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_624_0_node_176 | 20 | n |  | TRUE
7 | bus_MV_624_0_node_125 | 20 | n |  | TRUE
8 | bus_MV_624_0_node_155 | 20 | n |  | TRUE
9 | bus_MV_624_0_node_178 | 20 | n |  | TRUE
10 | bus_MV_624_0_node_67 | 20 | n |  | TRUE
11 | bus_MV_624_0_node_63 | 20 | n |  | TRUE
12 | bus_MV_624_0_node_65 | 20 | n |  | TRUE
13 | bus_MV_624_0_node_66 | 20 | n |  | TRUE
14 | bus_MV_624_0_node_62 | 20 | n |  | TRUE
15 | bus_MV_624_0_node_124 | 20 | n |  | TRUE
16 | bus_MV_624_0_node_123 | 20 | n |  | TRUE
17 | bus_MV_624_0_node_126 | 20 | n |  | TRUE
18 | bus_MV_624_0_node_5 | 20 | n |  | TRUE
19 | bus_MV_624_0_node_6 | 20 | n |  | TRUE
20 | bus_MV_624_0_node_8 | 20 | n |  | TRUE
21 | bus_MV_624_0_node_163 | 20 | n |  | TRUE
22 | bus_MV_624_0_node_169 | 20 | n |  | TRUE
23 | bus_MV_624_0_node_37 | 20 | n |  | TRUE
24 | bus_MV_624_0_node_31 | 20 | n |  | TRUE
25 | bus_MV_624_0_node_32 | 20 | n |  | TRUE
26 | bus_MV_624_0_node_36 | 20 | n |  | TRUE
27 | bus_MV_624_0_node_7 | 20 | n |  | TRUE
28 | bus_MV_624_0_node_171 | 20 | n |  | TRUE
29 | bus_MV_624_0_node_167 | 20 | n |  | TRUE
30 | bus_MV_624_0_node_168 | 20 | n |  | TRUE
31 | bus_MV_624_0_node_172 | 20 | n |  | TRUE
32 | bus_MV_624_0_node_9 | 20 | n |  | TRUE
33 | bus_MV_624_0_node_166 | 20 | n |  | TRUE
34 | bus_MV_624_0_node_10 | 20 | n |  | TRUE
35 | bus_MV_624_0_node_12 | 20 | n |  | TRUE
36 | bus_MV_624_0_node_55 | 20 | n |  | TRUE
37 | bus_MV_624_0_node_175 | 20 | n |  | TRUE
38 | bus_MV_624_0_node_13 | 20 | n |  | TRUE
39 | bus_MV_624_0_node_95 | 20 | n |  | TRUE
40 | bus_MV_624_0_node_91 | 20 | n |  | TRUE
41 | bus_MV_624_0_node_92 | 20 | n |  | TRUE
42 | bus_MV_624_0_node_93 | 20 | n |  | TRUE
43 | bus_MV_624_0_node_94 | 20 | n |  | TRUE
44 | bus_MV_624_0_node_89 | 20 | n |  | TRUE
45 | bus_MV_624_0_node_88 | 20 | n |  | TRUE
46 | bus_MV_624_0_node_16 | 20 | n |  | TRUE
47 | bus_MV_624_0_node_17 | 20 | n |  | TRUE
48 | bus_MV_624_0_node_18 | 20 | n |  | TRUE
49 | bus_MV_624_0_node_87 | 20 | n |  | TRUE
50 | bus_MV_624_0_node_85 | 20 | n |  | TRUE
51 | bus_MV_624_0_node_86 | 20 | n |  | TRUE
52 | bus_MV_624_0_node_19 | 20 | n |  | TRUE
53 | bus_MV_624_0_node_20 | 20 | n |  | TRUE
54 | bus_MV_624_0_node_21 | 20 | n |  | TRUE
55 | bus_MV_624_0_node_83 | 20 | n |  | TRUE
56 | bus_MV_624_0_node_22 | 20 | n |  | TRUE
57 | bus_MV_624_0_node_23 | 20 | n |  | TRUE
58 | bus_MV_624_0_node_82 | 20 | n |  | TRUE
59 | bus_MV_624_0_node_107 | 20 | n |  | TRUE
60 | bus_MV_624_0_node_106 | 20 | n |  | TRUE
61 | bus_MV_624_0_node_133 | 20 | n |  | TRUE
62 | bus_MV_624_0_node_84 | 20 | n |  | TRUE
63 | bus_MV_624_0_node_120 | 20 | n |  | TRUE
64 | bus_MV_624_0_node_50 | 20 | n |  | TRUE
65 | bus_MV_624_0_node_54 | 20 | n |  | TRUE
66 | bus_MV_624_0_node_52 | 20 | n |  | TRUE
67 | bus_MV_624_0_node_136 | 20 | n |  | TRUE
68 | bus_MV_624_0_node_49 | 20 | n |  | TRUE
69 | bus_MV_624_0_node_72 | 20 | n |  | TRUE
70 | bus_MV_624_0_node_134 | 20 | n |  | TRUE
71 | bus_MV_624_0_node_24 | 20 | n |  | TRUE
72 | bus_MV_624_0_node_25 | 20 | n |  | TRUE
73 | bus_MV_624_0_node_26 | 20 | n |  | TRUE
74 | bus_MV_624_0_node_27 | 20 | n |  | TRUE
75 | bus_MV_624_0_node_170 | 20 | n |  | TRUE
76 | bus_MV_624_0_node_127 | 20 | n |  | TRUE
77 | bus_MV_624_0_node_130 | 20 | n |  | TRUE
78 | bus_MV_624_0_node_128 | 20 | n |  | TRUE
79 | bus_MV_624_0_node_28 | 20 | n |  | TRUE
80 | bus_MV_624_0_node_29 | 20 | n |  | TRUE
81 | bus_MV_624_0_node_30 | 20 | n |  | TRUE
82 | bus_MV_624_0_node_39 | 20 | n |  | TRUE
83 | bus_MV_624_0_node_40 | 20 | n |  | TRUE
84 | bus_MV_624_0_node_156 | 20 | n |  | TRUE
85 | bus_MV_624_0_node_38 | 20 | n |  | TRUE
86 | bus_MV_624_0_node_144 | 20 | n |  | TRUE
87 | bus_MV_624_0_node_179 | 20 | n |  | TRUE
88 | bus_MV_624_0_node_41 | 20 | n |  | TRUE
89 | bus_MV_624_0_node_34 | 20 | n |  | TRUE
90 | bus_MV_624_0_node_145 | 20 | n |  | TRUE
91 | bus_MV_624_0_node_77 | 20 | n |  | TRUE
92 | bus_MV_624_0_node_146 | 20 | n |  | TRUE
93 | bus_MV_624_0_node_147 | 20 | n |  | TRUE
94 | bus_MV_624_0_node_35 | 20 | n |  | TRUE
95 | bus_MV_624_0_node_151 | 20 | n |  | TRUE
96 | bus_MV_624_0_node_149 | 20 | n |  | TRUE
97 | bus_MV_624_0_node_174 | 20 | n |  | TRUE
98 | bus_MV_624_0_node_150 | 20 | n |  | TRUE
99 | bus_MV_624_0_node_152 | 20 | n |  | TRUE
100 | bus_MV_624_0_node_173 | 20 | n |  | TRUE
101 | bus_MV_624_0_node_143 | 20 | n |  | TRUE
102 | bus_MV_624_0_node_42 | 20 | n |  | TRUE
103 | bus_MV_624_0_node_75 | 20 | n |  | TRUE
104 | bus_MV_624_0_node_73 | 20 | n |  | TRUE
105 | bus_MV_624_0_node_74 | 20 | n |  | TRUE
106 | bus_MV_624_0_node_159 | 20 | n |  | TRUE
107 | bus_MV_624_0_node_58 | 20 | n |  | TRUE
108 | bus_MV_624_0_node_68 | 20 | n |  | TRUE
109 | bus_MV_624_0_node_44 | 20 | n |  | TRUE
110 | bus_MV_624_0_node_45 | 20 | n |  | TRUE
111 | bus_MV_624_0_node_46 | 20 | n |  | TRUE
112 | bus_MV_624_0_node_47 | 20 | n |  | TRUE
113 | bus_MV_624_0_node_119 | 20 | n |  | TRUE
114 | bus_MV_624_0_node_79 | 20 | n |  | TRUE
115 | bus_MV_624_0_node_111 | 20 | n |  | TRUE
116 | bus_MV_624_0_node_104 | 20 | n |  | TRUE
117 | bus_MV_624_0_node_80 | 20 | n |  | TRUE
118 | bus_MV_624_0_node_112 | 20 | n |  | TRUE
119 | bus_MV_624_0_node_48 | 20 | n |  | TRUE
120 | bus_MV_624_0_node_137 | 20 | n |  | TRUE
121 | bus_MV_624_0_node_71 | 20 | n |  | TRUE
122 | bus_MV_624_0_node_56 | 20 | n |  | TRUE
123 | bus_MV_624_0_node_57 | 20 | n |  | TRUE
124 | bus_MV_624_0_node_139 | 20 | n |  | TRUE
125 | bus_MV_624_0_node_70 | 20 | n |  | TRUE
126 | bus_MV_624_0_node_69 | 20 | n |  | TRUE
127 | bus_MV_624_0_node_59 | 20 | n |  | TRUE
128 | bus_MV_624_0_node_60 | 20 | n |  | TRUE
129 | bus_MV_624_0_node_61 | 20 | n |  | TRUE
130 | bus_MV_624_0_node_102 | 20 | n |  | TRUE
131 | bus_MV_624_0_node_101 | 20 | n |  | TRUE
132 | bus_MV_624_0_node_64 | 20 | n |  | TRUE
133 | bus_MV_624_0_node_138 | 20 | n |  | TRUE
134 | bus_MV_624_0_node_157 | 20 | n |  | TRUE
135 | bus_MV_624_0_node_177 | 20 | n |  | TRUE
136 | bus_MV_624_0_node_76 | 20 | n |  | TRUE
137 | bus_MV_624_0_node_78 | 20 | n |  | TRUE
138 | bus_MV_624_0_node_81 | 20 | n |  | TRUE
139 | bus_MV_624_0_node_141 | 20 | n |  | TRUE
140 | bus_MV_624_0_node_142 | 20 | n |  | TRUE
141 | bus_MV_624_0_node_140 | 20 | n |  | TRUE
142 | bus_MV_624_0_node_148 | 20 | n |  | TRUE
143 | bus_MV_624_0_node_110 | 20 | n |  | TRUE
144 | bus_MV_624_0_node_90 | 20 | n |  | TRUE
145 | bus_MV_624_0_node_98 | 20 | n |  | TRUE
146 | bus_MV_624_0_node_161 | 20 | n |  | TRUE
147 | bus_MV_624_0_node_96 | 20 | n |  | TRUE
148 | bus_MV_624_0_node_158 | 20 | n |  | TRUE
149 | bus_MV_624_0_node_115 | 20 | n |  | TRUE
150 | bus_MV_624_0_node_113 | 20 | n |  | TRUE
151 | bus_MV_624_0_node_99 | 20 | n |  | TRUE
152 | bus_MV_624_0_node_100 | 20 | n |  | TRUE
153 | bus_MV_624_0_node_103 | 20 | n |  | TRUE
154 | bus_MV_624_0_node_105 | 20 | n |  | TRUE
155 | bus_MV_624_0_node_118 | 20 | n |  | TRUE
156 | bus_MV_624_0_node_132 | 20 | n |  | TRUE
157 | bus_MV_624_0_node_108 | 20 | n |  | TRUE
158 | bus_MV_624_0_node_117 | 20 | n |  | TRUE
159 | bus_MV_624_0_node_109 | 20 | n |  | TRUE
160 | bus_MV_624_0_node_160 | 20 | n |  | TRUE
161 | bus_MV_624_0_node_122 | 20 | n |  | TRUE
162 | bus_MV_624_0_node_121 | 20 | n |  | TRUE
163 | bus_MV_624_0_node_114 | 20 | n |  | TRUE
164 | bus_MV_624_0_node_131 | 20 | n |  | TRUE
165 | bus_MV_624_0_node_129 | 20 | n |  | TRUE
166 | bus_MV_624_0_node_135 | 20 | n |  | TRUE
167 | bus_MV_624_0_node_153 | 20 | n |  | TRUE
168 | bus_MV_624_0_node_154 | 20 | n |  | TRUE
169 | bus_HV_624_0_node_28 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_624_0_load_0 | 0 | 0.21408 | 0.10368 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_624_0_load_53 | 1 | 0.38909 | 0.18845 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_624_0_load_51 | 2 | 0.32542 | 0.15761 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_624_0_load_176 | 6 | 0.40728 | 0.19726 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_624_0_load_155 | 8 | 0.735 | 0.35598 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_624_0_load_178 | 9 | 0.073377 | 0.035538 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_624_0_load_62 | 14 | 0.28481 | 0.13794 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_624_0_load_123 | 16 | 0.60337 | 0.29223 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_624_0_load_126 | 17 | 0.21707 | 0.10513 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_624_0_load_5 | 18 | 0.20764 | 0.10056 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_624_0_load_163 | 21 | 0.16926 | 0.081977 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_624_0_load_169 | 22 | 0.1918 | 0.092893 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_624_0_load_31 | 24 | 0.33277 | 0.16117 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_624_0_load_171 | 28 | 0.21517 | 0.10421 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_624_0_load_167 | 29 | 0.10962 | 0.053093 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_624_0_load_9 | 32 | 0.19039 | 0.092212 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_624_0_load_166 | 33 | 0.15303 | 0.074115 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_624_0_load_55 | 36 | 0.30325 | 0.14687 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_624_0_load_175 | 37 | 0.074584 | 0.036122 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_624_0_load_13 | 38 | 0.076684 | 0.03714 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_624_0_load_95 | 39 | 0.24427 | 0.11831 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_624_0_load_91 | 40 | 0.10376 | 0.050255 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_624_0_load_89 | 44 | 0.07474 | 0.036198 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_624_0_load_16 | 46 | 0.1482 | 0.071778 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_624_0_load_87 | 49 | 0.084157 | 0.040759 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_624_0_load_85 | 50 | 0.14873 | 0.072032 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_624_0_load_19 | 52 | 0.26108 | 0.12645 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_624_0_load_82 | 58 | 0.16654 | 0.080661 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_624_0_load_106 | 60 | 0.15568 | 0.075397 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_624_0_load_133 | 61 | 0.44722 | 0.2166 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_624_0_load_84 | 62 | 0.15135 | 0.073302 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_624_0_load_120 | 63 | 0.3925 | 0.1901 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_624_0_load_136 | 67 | 0.093903 | 0.045479 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_624_0_load_72 | 69 | 0.11315 | 0.054803 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_624_0_load_134 | 70 | 0.10833 | 0.052464 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_624_0_load_24 | 71 | 0.29897 | 0.1448 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_624_0_load_25 | 72 | 0.1549 | 0.075022 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_624_0_load_170 | 75 | 0.20986 | 0.10164 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_624_0_load_127 | 76 | 0.10359 | 0.050169 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_624_0_load_130 | 77 | 0.10509 | 0.050896 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_624_0_load_28 | 79 | 0.25841 | 0.12515 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_624_0_load_40 | 83 | 0.28294 | 0.13704 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_624_0_load_156 | 84 | 0.33624 | 0.16285 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_624_0_load_144 | 86 | 0.74191 | 0.35932 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_624_0_load_179 | 87 | 0.31496 | 0.15254 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_624_0_load_145 | 90 | 0.15626 | 0.075678 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_624_0_load_77 | 91 | 0.24705 | 0.11965 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_624_0_load_149 | 96 | 0.11116 | 0.053839 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_624_0_load_173 | 100 | 0.33745 | 0.16343 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_624_0_load_75 | 103 | 0.24623 | 0.11925 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_624_0_load_73 | 104 | 0.40021 | 0.19383 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_624_0_load_159 | 106 | 0.34267 | 0.16596 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_624_0_load_68 | 108 | 0.27006 | 0.1308 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_624_0_load_44 | 109 | 0.35574 | 0.17229 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_624_0_load_119 | 113 | 0.090656 | 0.043906 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_624_0_load_111 | 115 | 0.12064 | 0.058431 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_624_0_load_80 | 117 | 1.1068 | 0.53606 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_624_0_load_112 | 118 | 0.17409 | 0.084318 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_624_0_load_48 | 119 | 0.28086 | 0.13603 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_624_0_load_137 | 120 | 0.082265 | 0.039843 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_624_0_load_56 | 122 | 0.23248 | 0.11259 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_624_0_load_139 | 124 | 0.074849 | 0.036251 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_624_0_load_70 | 125 | 0.071695 | 0.034724 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_624_0_load_59 | 127 | 0.33504 | 0.16227 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_624_0_load_102 | 130 | 0.076651 | 0.037124 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_624_0_load_157 | 134 | 0.32246 | 0.15617 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_624_0_load_177 | 135 | 0.37668 | 0.18243 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_624_0_load_78 | 137 | 0.19513 | 0.094505 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_624_0_load_81 | 138 | 0.33674 | 0.16309 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_624_0_load_141 | 139 | 0.069342 | 0.033584 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_624_0_load_140 | 141 | 0.24658 | 0.11942 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_624_0_load_148 | 142 | 0.21181 | 0.10258 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_624_0_load_161 | 146 | 0.32402 | 0.15693 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_624_0_load_96 | 147 | 0.25367 | 0.12286 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_624_0_load_158 | 148 | 0.27772 | 0.13451 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_624_0_load_99 | 151 | 0.16289 | 0.078892 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_624_0_load_132 | 156 | 0.089325 | 0.043262 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_624_0_load_108 | 157 | 0.65225 | 0.3159 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_624_0_load_117 | 158 | 1.8813 | 0.91115 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_624_0_load_160 | 160 | 0.29806 | 0.14435 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_624_0_load_131 | 164 | 0.24875 | 0.12048 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_624_0_load_153 | 167 | 0.33031 | 0.15998 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_624_0_load_154 | 168 | 0.15066 | 0.072968 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_624_0_line_0 |  | 0 | 1 | 0.33397 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_624_0_line_1 |  | 1 | 2 | 0.098311 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_624_0_line_2 |  | 2 | 66 | 0.01082 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_624_0_line_3 |  | 3 | 4 | 0.28571 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_624_0_line_4 |  | 3 | 5 | 0.25931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_624_0_line_5 |  | 3 | 6 | 0.044762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_624_0_line_6 |  | 4 | 9 | 0.015469 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_624_0_line_7 |  | 5 | 7 | 0.11681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_624_0_line_8 |  | 5 | 8 | 0.045099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_624_0_line_9 |  | 6 | 10 | 0.027888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_624_0_line_10 |  | 7 | 17 | 0.030997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_624_0_line_11 |  | 7 | 15 | 0.069777 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_624_0_line_12 |  | 10 | 132 | 0.1482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_624_0_line_13 |  | 11 | 12 | 0.42197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_624_0_line_14 |  | 11 | 13 | 0.30531 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_624_0_line_15 |  | 11 | 14 | 0.1097 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_624_0_line_16 |  | 12 | 133 | 0.009027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_624_0_line_17 |  | 12 | 124 | 0.019885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_624_0_line_18 |  | 13 | 134 | 0.005129 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
19 | MV_624_0_line_19 |  | 13 | 135 | 0.2293 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_624_0_line_20 |  | 14 | 132 | 0.012509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_624_0_line_21 |  | 15 | 16 | 0.056035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_624_0_line_22 |  | 17 | 35 | 0.025931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_624_0_line_23 |  | 18 | 19 | 0.050811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_624_0_line_24 |  | 19 | 20 | 0.47561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_624_0_line_25 |  | 19 | 21 | 0.66651 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_624_0_line_26 |  | 20 | 29 | 0.10515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_624_0_line_27 |  | 20 | 30 | 0.10918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_624_0_line_28 |  | 22 | 23 | 0.073879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_624_0_line_29 |  | 23 | 26 | 0.078566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_624_0_line_30 |  | 23 | 27 | 0.22847 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_624_0_line_31 |  | 24 | 25 | 0.03695 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_624_0_line_32 |  | 24 | 26 | 0.29568 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_624_0_line_33 |  | 25 | 89 | 0.1653 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_624_0_line_34 |  | 26 | 91 | 0.030256 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_624_0_line_35 |  | 27 | 28 | 0.024882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_624_0_line_36 |  | 28 | 31 | 0.070983 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_624_0_line_37 |  | 30 | 32 | 0.29361 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_624_0_line_38 |  | 30 | 33 | 0.07777 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_624_0_line_39 |  | 31 | 97 | 0.14147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_624_0_line_40 |  | 32 | 34 | 0.20429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_624_0_line_41 |  | 33 | 37 | 0.62886 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_624_0_line_42 |  | 34 | 35 | 0.17916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_624_0_line_43 |  | 34 | 36 | 0.069726 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_624_0_line_44 |  | 38 | 39 | 0.23614 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_624_0_line_45 |  | 39 | 42 | 0.0065892 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_624_0_line_46 |  | 40 | 41 | 0.0144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_624_0_line_47 |  | 40 | 42 | 0.037853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_624_0_line_48 |  | 41 | 43 | 0.056338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_624_0_line_49 |  | 43 | 147 | 0.039411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_624_0_line_50 |  | 43 | 75 | 0.31338 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_624_0_line_51 |  | 43 | 145 | 0.42837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_624_0_line_52 |  | 44 | 45 | 0.045821 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_624_0_line_53 |  | 45 | 144 | 0.13618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_624_0_line_54 |  | 45 | 51 | 0.10169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_624_0_line_55 |  | 46 | 47 | 0.10937 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_624_0_line_56 |  | 47 | 48 | 0.17192 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_624_0_line_57 |  | 48 | 49 | 0.07501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_624_0_line_58 |  | 48 | 50 | 0.044347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_624_0_line_59 |  | 50 | 51 | 0.064558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_624_0_line_60 |  | 52 | 53 | 0.013347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_624_0_line_61 |  | 53 | 54 | 0.45665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_624_0_line_62 |  | 54 | 55 | 0.035298 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_624_0_line_63 |  | 54 | 56 | 0.11493 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_624_0_line_64 |  | 54 | 57 | 0.46637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_624_0_line_65 |  | 54 | 58 | 0.039311 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_624_0_line_66 |  | 55 | 62 | 0.014727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_624_0_line_67 |  | 56 | 59 | 0.040662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_624_0_line_68 |  | 56 | 60 | 0.070359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_624_0_line_69 |  | 57 | 61 | 0.047968 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_624_0_line_70 |  | 59 | 63 | 0.047731 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_624_0_line_71 |  | 61 | 70 | 0.017051 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_624_0_line_72 |  | 63 | 162 | 0.066817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_624_0_line_73 |  | 64 | 65 | 0.02125 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_624_0_line_74 |  | 64 | 66 | 0.109 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_624_0_line_75 |  | 64 | 67 | 0.025128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_624_0_line_76 |  | 64 | 68 | 0.19979 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_624_0_line_77 |  | 65 | 69 | 0.034206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_624_0_line_78 |  | 67 | 120 | 0.017191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_624_0_line_79 |  | 68 | 119 | 0.054873 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_624_0_line_80 |  | 69 | 121 | 0.034677 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_624_0_line_81 |  | 70 | 166 | 0.024367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_624_0_line_82 |  | 71 | 72 | 0.020706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_624_0_line_83 |  | 71 | 73 | 0.10676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_624_0_line_84 |  | 73 | 74 | 0.25705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_624_0_line_85 |  | 73 | 75 | 0.21399 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_624_0_line_86 |  | 74 | 76 | 0.091026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_624_0_line_87 |  | 76 | 77 | 0.061162 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_624_0_line_88 |  | 77 | 78 | 0.080892 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_624_0_line_89 |  | 78 | 165 | 0.040038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_624_0_line_90 |  | 79 | 80 | 0.029085 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
91 | MV_624_0_line_91 |  | 80 | 81 | 0.14236 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
92 | MV_624_0_line_92 |  | 81 | 82 | 0.17481 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_624_0_line_93 |  | 81 | 83 | 0.019821 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_624_0_line_94 |  | 82 | 84 | 0.044479 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_624_0_line_95 |  | 83 | 88 | 0.068352 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
96 | MV_624_0_line_96 |  | 84 | 101 | 0.0989 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
97 | MV_624_0_line_97 |  | 85 | 86 | 0.019283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_624_0_line_98 |  | 85 | 87 | 0.19047 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_624_0_line_99 |  | 87 | 95 | 0.006284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_624_0_line_100 |  | 88 | 102 | 0.20201 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_624_0_line_101 |  | 89 | 90 | 0.045782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_624_0_line_102 |  | 90 | 92 | 0.052835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_624_0_line_103 |  | 92 | 93 | 0.11397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_624_0_line_104 |  | 93 | 135 | 0.026246 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_624_0_line_105 |  | 94 | 95 | 0.14421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_624_0_line_106 |  | 94 | 96 | 0.050493 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_624_0_line_107 |  | 96 | 98 | 0.0534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_624_0_line_108 |  | 97 | 100 | 0.085472 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_624_0_line_109 |  | 98 | 99 | 0.28475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_624_0_line_110 |  | 99 | 100 | 0.016623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_624_0_line_111 |  | 101 | 140 | 0.20377 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
112 | MV_624_0_line_112 |  | 102 | 103 | 0.052547 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
113 | MV_624_0_line_113 |  | 103 | 104 | 0.084999 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
114 | MV_624_0_line_114 |  | 104 | 105 | 0.030784 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
115 | MV_624_0_line_115 |  | 105 | 136 | 0.25309 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
116 | MV_624_0_line_116 |  | 106 | 107 | 0.15024 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_624_0_line_117 |  | 107 | 108 | 0.016974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_624_0_line_118 |  | 108 | 125 | 0.019769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_624_0_line_119 |  | 108 | 126 | 0.082582 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_624_0_line_120 |  | 109 | 110 | 0.006897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_624_0_line_121 |  | 110 | 111 | 0.037707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_624_0_line_122 |  | 111 | 112 | 0.058844 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
123 | MV_624_0_line_123 |  | 111 | 113 | 0.045134 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
124 | MV_624_0_line_124 |  | 112 | 114 | 0.042285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_624_0_line_125 |  | 112 | 115 | 0.042228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_624_0_line_126 |  | 113 | 116 | 0.050614 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
127 | MV_624_0_line_127 |  | 114 | 117 | 0.072156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_624_0_line_128 |  | 115 | 118 | 0.12154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_624_0_line_129 |  | 116 | 131 | 0.10222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_624_0_line_130 |  | 116 | 153 | 0.080495 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
131 | MV_624_0_line_131 |  | 117 | 137 | 0.12135 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
132 | MV_624_0_line_132 |  | 118 | 150 | 0.039055 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_624_0_line_133 |  | 120 | 133 | 0.053481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_624_0_line_134 |  | 121 | 126 | 0.027888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_624_0_line_135 |  | 122 | 123 | 0.087696 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_624_0_line_136 |  | 123 | 124 | 0.10393 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_624_0_line_137 |  | 127 | 128 | 0.016544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_624_0_line_138 |  | 128 | 129 | 0.011168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_624_0_line_139 |  | 129 | 130 | 0.022095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_624_0_line_140 |  | 130 | 131 | 0.028061 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_624_0_line_141 |  | 131 | 152 | 0.02116 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_624_0_line_142 |  | 134 | 136 | 0.009155 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
143 | MV_624_0_line_143 |  | 138 | 139 | 0.24868 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
144 | MV_624_0_line_144 |  | 139 | 140 | 0.065597 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
145 | MV_624_0_line_145 |  | 139 | 141 | 0.15858 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
146 | MV_624_0_line_146 |  | 140 | 162 | 0.15431 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
147 | MV_624_0_line_147 |  | 141 | 161 | 0.044387 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
148 | MV_624_0_line_148 |  | 142 | 143 | 0.032826 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_624_0_line_149 |  | 143 | 154 | 0.22283 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
150 | MV_624_0_line_150 |  | 143 | 159 | 0.048145 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
151 | MV_624_0_line_151 |  | 144 | 145 | 0.026764 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
152 | MV_624_0_line_152 |  | 144 | 146 | 0.021442 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
153 | MV_624_0_line_153 |  | 148 | 149 | 0.069096 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
154 | MV_624_0_line_154 |  | 149 | 150 | 0.029097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_624_0_line_155 |  | 150 | 163 | 0.020611 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_624_0_line_156 |  | 151 | 152 | 0.031162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_624_0_line_157 |  | 153 | 154 | 0.12459 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
158 | MV_624_0_line_158 |  | 153 | 155 | 0.03681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_624_0_line_159 |  | 153 | 156 | 0.0057482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_624_0_line_160 |  | 154 | 157 | 0.0028163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_624_0_line_161 |  | 155 | 158 | 0.002402 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_624_0_line_162 |  | 159 | 160 | 0.005298 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_624_0_line_163 |  | 159 | 161 | 0.068729 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
164 | MV_624_0_line_164 |  | 163 | 164 | 0.098189 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_624_0_line_165 |  | 164 | 165 | 0.011275 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_624_0_line_166 |  | 166 | 167 | 0.01151 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
167 | MV_624_0_line_167 |  | 166 | 168 | 0.08566 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_624_0_trafo_28 | 25 MVA 110/20 kV | 169 | 79 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2534167.2618 | 1155019.3959
1 | 2534274.7077 | 1154703.1794
2 | 2534290.3542 | 1154606.1217
3 | 2534506.9683 | 1155179.9283
4 | 2534435.7461 | 1155279.0148
5 | 2534723.6012 | 1155120.4388
6 | 2534505.7595 | 1155135.1946
7 | 2534776.6844 | 1155076.0825
8 | 2534736.9339 | 1155154
9 | 2534448.7788 | 1155270.6236
10 | 2534505.5246 | 1155107.3152
11 | 2534557.8329 | 1154856.0741
12 | 2534400.5232 | 1154571.6882
13 | 2534634.3298 | 1154666.5153
14 | 2534525.3141 | 1154960.8413
15 | 2534789.769 | 1155029.2815
16 | 2534838.4451 | 1155052.3218
17 | 2534800.3553 | 1155096.0945
18 | 2535574.8929 | 1155585.3964
19 | 2535562.6716 | 1155634.4654
20 | 2535100.9042 | 1155587.7645
21 | 2535444.5549 | 1156290.4261
22 | 2535210.4669 | 1154999.1929
23 | 2535251.2402 | 1154937.5197
24 | 2535079.5961 | 1154672.8929
25 | 2535045.474 | 1154687.0693
26 | 2535293.6365 | 1154876.8854
27 | 2535451.8148 | 1155046.9221
28 | 2535469.2511 | 1155029.1251
29 | 2535120.7191 | 1155485.0831
30 | 2534996.0134 | 1155556.4365
31 | 2535512.2362 | 1154973.1775
32 | 2534846.2215 | 1155303.9089
33 | 2534977.8175 | 1155632.0416
34 | 2534917.2464 | 1155119.4826
35 | 2534820.1624 | 1155112.831
36 | 2534979.3317 | 1155151.2169
37 | 2535200.5896 | 1156220.1246
38 | 2535152.8354 | 1152387.4841
39 | 2535294.8493 | 1152576.1491
40 | 2535310.5199 | 1152608.6953
41 | 2535319.0478 | 1152620.2988
42 | 2535300.8234 | 1152573.3692
43 | 2535321.0866 | 1152675.685
44 | 2534867.364 | 1152863.3456
45 | 2534878.34 | 1152905.4678
46 | 2534861.8931 | 1153142.3647
47 | 2534795.8243 | 1153055.2109
48 | 2534710.0972 | 1152975.3975
49 | 2534679.9675 | 1152915.5748
50 | 2534744.8087 | 1152960.2265
51 | 2534809.364 | 1152960.7901
52 | 2534652.3731 | 1153573.9973
53 | 2534641.8409 | 1153565.7629
54 | 2534559.7495 | 1153763.6312
55 | 2534546.9497 | 1153796.533
56 | 2534646.6255 | 1153762.9746
57 | 2534390.3782 | 1153903.3207
58 | 2534596.6558 | 1153777.1703
59 | 2534682.3689 | 1153776.1378
60 | 2534672.547 | 1153697.6858
61 | 2534432.192 | 1153926.7903
62 | 2534541.6105 | 1153810.2576
63 | 2534729.4066 | 1153774.9478
64 | 2534306.7592 | 1154532.7909
65 | 2534307.9118 | 1154521.7389
66 | 2534286.202 | 1154596.1282
67 | 2534329.3087 | 1154543.8782
68 | 2534237.6164 | 1154420.0073
69 | 2534305.832 | 1154489.3099
70 | 2534446.9517 | 1153935.3276
71 | 2535714.685 | 1152977.6363
72 | 2535723.5989 | 1152996.3253
73 | 2535667.8034 | 1153061.7538
74 | 2535562.063 | 1153220.4397
75 | 2535493.8308 | 1152937.1498
76 | 2535480.5157 | 1153260.8838
77 | 2535451.1897 | 1153207.2107
78 | 2535379.3745 | 1153244.8362
79 | 2534891.8385 | 1154142.4996
80 | 2534917.6706 | 1154156.005
81 | 2535037.5764 | 1154221.3327
82 | 2535088.5512 | 1154075.3242
83 | 2535028.823 | 1154239.0926
84 | 2535059.0679 | 1154042.0133
85 | 2535323.6479 | 1154421.0905
86 | 2535336.6913 | 1154406.8878
87 | 2535329.4412 | 1154611.4769
88 | 2534986.2552 | 1154292.571
89 | 2534964.2143 | 1154812.6947
90 | 2534938.0728 | 1154850.2777
91 | 2535316.8316 | 1154857.4584
92 | 2534907.741 | 1154893.5393
93 | 2534815.9515 | 1154845.6634
94 | 2535435.1183 | 1154589.7066
95 | 2535334.0594 | 1154615.7517
96 | 2535480.9937 | 1154568.6963
97 | 2535592.5822 | 1154857.3637
98 | 2535527.9034 | 1154543.2074
99 | 2535662.7186 | 1154784.3058
100 | 2535655.1138 | 1154799.0953
101 | 2534999.6589 | 1153962.9454
102 | 2534824.5643 | 1154303.8727
103 | 2534800.9398 | 1154350.2696
104 | 2534777.1384 | 1154431.8685
105 | 2534761.7751 | 1154458.2719
106 | 2534521.6258 | 1154327.5559
107 | 2534372.0242 | 1154341.395
108 | 2534364.3587 | 1154356.4937
109 | 2535054.6018 | 1153242.6903
110 | 2535058.0884 | 1153248.6448
111 | 2535087.7446 | 1153240.0865
112 | 2535124.5353 | 1153222.1351
113 | 2535049.4727 | 1153264.0104
114 | 2535147.3253 | 1153257.7531
115 | 2535156.8862 | 1153196.7292
116 | 2535006.5595 | 1153290.847
117 | 2535113.306 | 1153303.0998
118 | 2535259.6052 | 1153131.7648
119 | 2534257.5787 | 1154368.8941
120 | 2534344.7354 | 1154551.4633
121 | 2534320.5934 | 1154457.9319
122 | 2534553.1634 | 1154528.1559
123 | 2534480.9534 | 1154478.3931
124 | 2534409.7034 | 1154554.0523
125 | 2534346.2071 | 1154348.6624
126 | 2534331.6443 | 1154432.3193
127 | 2534874.8583 | 1153347.4255
128 | 2534890.9537 | 1153351.4422
129 | 2534884.4026 | 1153342.386
130 | 2534901.79 | 1153329.0557
131 | 2534926.0544 | 1153315.0089
132 | 2534512.7837 | 1154960.4999
133 | 2534392.84 | 1154574.8294
134 | 2534637.4305 | 1154662.4238
135 | 2534794.1895 | 1154830.9025
136 | 2534642.9588 | 1154655.1152
137 | 2535208.6732 | 1153378.1353
138 | 2535220.8881 | 1153783.0142
139 | 2534972.3159 | 1153775.787
140 | 2534920.9321 | 1153815.4163
141 | 2534900.0265 | 1153634.6424
142 | 2535020.6257 | 1153560.6124
143 | 2534998.8959 | 1153553.4403
144 | 2534986.3993 | 1152853.0029
145 | 2535013.1629 | 1152852.8135
146 | 2534978.3648 | 1152833.1234
147 | 2535354.7707 | 1152655.3458
148 | 2535262.176 | 1153026.9667
149 | 2535291.235 | 1153089.6549
150 | 2535292.4977 | 1153110.7195
151 | 2534882.977 | 1153316.9853
152 | 2534909.8468 | 1153301.3546
153 | 2535013.0929 | 1153355.0337
154 | 2535075.1671 | 1153399.7431
155 | 2535029.796 | 1153328.6832
156 | 2535016.1279 | 1153359.9154
157 | 2535072.7269 | 1153401.148
158 | 2535028.5494 | 1153326.63
159 | 2534965.6481 | 1153559.6478
160 | 2534962.061 | 1153555.74
161 | 2534932.5133 | 1153604.6199
162 | 2534785.8477 | 1153740.8283
163 | 2535310.087 | 1153112.3422
164 | 2535355.5967 | 1153199.3473
165 | 2535360.8227 | 1153209.3384
166 | 2534469.655 | 1153943.3113
167 | 2534475.3952 | 1153953.2875
168 | 2534472.685 | 1154028.9178
169 | 2534891.8385 | 1154142.4996

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99495 | -0.032106 | 0.21408 | 0.10368
1 | 0.99508 | -0.031228 | 0.38909 | 0.18845
2 | 0.9952 | -0.030501 | 0.32542 | 0.15761
3 | 0.99528 | -0.043724 | 0 | 0
4 | 0.99525 | -0.04354 | 0 | 0
5 | 0.99436 | -0.035753 | 0 | 0
6 | 0.99544 | -0.045108 | 0.40728 | 0.19726
7 | 0.99406 | -0.033155 | 0 | 0
8 | 0.99432 | -0.035353 | 0.735 | 0.35598
9 | 0.99525 | -0.043527 | 0.073377 | 0.035538
10 | 0.99556 | -0.046105 | 0 | 0
11 | 0.99697 | -0.046553 | 0 | 0
12 | 0.99563 | -0.034433 | 0 | 0
13 | 0.99797 | -0.035568 | 0 | 0
14 | 0.99622 | -0.051824 | 0.28481 | 0.13794
15 | 0.99401 | -0.032655 | 0 | 0
16 | 0.99397 | -0.032248 | 0.60337 | 0.29223
17 | 0.99401 | -0.032683 | 0.21707 | 0.10513
18 | 0.99274 | -0.028634 | 0.20764 | 0.10056
19 | 0.99276 | -0.02876 | 0 | 0
20 | 0.99299 | -0.030703 | 0 | 0
21 | 0.99254 | -0.030166 | 0.16926 | 0.081977
22 | 0.99367 | -0.040617 | 0.1918 | 0.092893
23 | 0.99369 | -0.040785 | 0 | 0
24 | 0.99512 | -0.034078 | 0.33277 | 0.16117
25 | 0.9953 | -0.032877 | 0 | 0
26 | 0.99388 | -0.042494 | 0 | 0
27 | 0.99292 | -0.045996 | 0 | 0
28 | 0.99287 | -0.045507 | 0.21517 | 0.10421
29 | 0.99297 | -0.030571 | 0.10962 | 0.053093
30 | 0.99305 | -0.031228 | 0 | 0
31 | 0.99273 | -0.044291 | 0 | 0
32 | 0.99346 | -0.028127 | 0.19039 | 0.092212
33 | 0.99303 | -0.031021 | 0.15303 | 0.074115
34 | 0.99369 | -0.030058 | 0 | 0
35 | 0.99397 | -0.032355 | 0 | 0
36 | 0.99365 | -0.030317 | 0.30325 | 0.14687
37 | 0.99294 | -0.031616 | 0.074584 | 0.036122
38 | 0.99223 | -0.051342 | 0.076684 | 0.03714
39 | 0.99227 | -0.051117 | 0.24427 | 0.11831
40 | 0.99229 | -0.051288 | 0.10376 | 0.050255
41 | 0.99229 | -0.051361 | 0 | 0
42 | 0.99227 | -0.051143 | 0 | 0
43 | 0.99232 | -0.051644 | 0 | 0
44 | 0.99177 | -0.04776 | 0.07474 | 0.036198
45 | 0.99178 | -0.0478 | 0 | 0
46 | 0.99162 | -0.046932 | 0.1482 | 0.071778
47 | 0.99165 | -0.046733 | 0 | 0
48 | 0.99168 | -0.047019 | 0 | 0
49 | 0.99168 | -0.046946 | 0.084157 | 0.040759
50 | 0.9917 | -0.047126 | 0.14873 | 0.072032
51 | 0.99173 | -0.047393 | 0 | 0
52 | 0.99678 | -0.025674 | 0.26108 | 0.12645
53 | 0.99679 | -0.025716 | 0 | 0
54 | 0.99694 | -0.026983 | 0 | 0
55 | 0.99693 | -0.026921 | 0 | 0
56 | 0.99718 | -0.029018 | 0 | 0
57 | 0.99632 | -0.021393 | 0 | 0
58 | 0.99693 | -0.027063 | 0.16654 | 0.080661
59 | 0.99727 | -0.029805 | 0 | 0
60 | 0.99716 | -0.02889 | 0.15568 | 0.075397
61 | 0.99626 | -0.020799 | 0.44722 | 0.2166
62 | 0.99693 | -0.026894 | 0.15135 | 0.073302
63 | 0.99738 | -0.030725 | 0.3925 | 0.1901
64 | 0.99534 | -0.03183 | 0 | 0
65 | 0.99532 | -0.03163 | 0 | 0
66 | 0.99521 | -0.030622 | 0 | 0
67 | 0.99541 | -0.032419 | 0.093903 | 0.045479
68 | 0.99527 | -0.031183 | 0 | 0
69 | 0.99529 | -0.031307 | 0.11315 | 0.054803
70 | 0.99625 | -0.020679 | 0.10833 | 0.052464
71 | 0.99383 | -0.039748 | 0.29897 | 0.1448
72 | 0.99383 | -0.039709 | 0.1549 | 0.075022
73 | 0.9939 | -0.040323 | 0 | 0
74 | 0.99459 | -0.046343 | 0 | 0
75 | 0.99321 | -0.045242 | 0.20986 | 0.10164
76 | 0.99484 | -0.048449 | 0.10359 | 0.050169
77 | 0.9951 | -0.046567 | 0.10509 | 0.050896
78 | 0.99534 | -0.04863 | 0 | 0
79 | 1 | 0 | -22.1652 | -10.2885
80 | 0.9999 | -0.00047072 | 0 | 0
81 | 0.99938 | -0.0027649 | 0 | 0
82 | 0.99905 | -0.0042577 | 0 | 0
83 | 0.99935 | -0.0029122 | 0.28294 | 0.13704
84 | 0.99896 | -0.0046332 | 0.33624 | 0.16285
85 | 0.99113 | -0.037909 | 0 | 0
86 | 0.99111 | -0.037735 | 0.74191 | 0.35932
87 | 0.9914 | -0.036162 | 0.31496 | 0.15254
88 | 0.99912 | -0.015963 | 0 | 0
89 | 0.99582 | -0.037593 | 0 | 0
90 | 0.99597 | -0.038891 | 0.15626 | 0.075678
91 | 0.99386 | -0.042586 | 0.24705 | 0.11965
92 | 0.99615 | -0.040485 | 0 | 0
93 | 0.99653 | -0.043905 | 0 | 0
94 | 0.99161 | -0.038074 | 0 | 0
95 | 0.99141 | -0.036242 | 0 | 0
96 | 0.99168 | -0.038708 | 0.11116 | 0.053839
97 | 0.99246 | -0.041845 | 0 | 0
98 | 0.99176 | -0.039446 | 0 | 0
99 | 0.99218 | -0.043307 | 0 | 0
100 | 0.99221 | -0.043528 | 0.33745 | 0.16343
101 | 0.99858 | -0.02615 | 0 | 0
102 | 0.99879 | -0.017414 | 0 | 0
103 | 0.9987 | -0.017786 | 0.24623 | 0.11925
104 | 0.99842 | -0.033613 | 0.40021 | 0.19383
105 | 0.99838 | -0.033819 | 0 | 0
106 | 0.99501 | -0.032055 | 0.34267 | 0.16596
107 | 0.99511 | -0.031425 | 0 | 0
108 | 0.99512 | -0.031495 | 0.27006 | 0.1308
109 | 0.99679 | -0.058292 | 0.35574 | 0.17229
110 | 0.99679 | -0.058322 | 0 | 0
111 | 0.99681 | -0.058482 | 0 | 0
112 | 0.99667 | -0.060038 | 0 | 0
113 | 0.99685 | -0.058334 | 0.090656 | 0.043906
114 | 0.9966 | -0.059381 | 0 | 0
115 | 0.9965 | -0.058574 | 0.12064 | 0.058431
116 | 0.99689 | -0.058163 | 0 | 0
117 | 0.99648 | -0.058254 | 1.1068 | 0.53606
118 | 0.99603 | -0.054517 | 0.17409 | 0.084318
119 | 0.99524 | -0.031372 | 0.28086 | 0.13603
120 | 0.99545 | -0.032841 | 0.082265 | 0.039843
121 | 0.99526 | -0.031026 | 0 | 0
122 | 0.99553 | -0.034905 | 0.23248 | 0.11259
123 | 0.99557 | -0.034656 | 0 | 0
124 | 0.99562 | -0.03436 | 0.074849 | 0.036251
125 | 0.99512 | -0.031478 | 0.071695 | 0.034724
126 | 0.99523 | -0.030798 | 0 | 0
127 | 0.99678 | -0.057148 | 0.33504 | 0.16227
128 | 0.99678 | -0.057215 | 0 | 0
129 | 0.99679 | -0.057259 | 0 | 0
130 | 0.9968 | -0.057347 | 0.076651 | 0.037124
131 | 0.99681 | -0.057484 | 0 | 0
132 | 0.99617 | -0.051381 | 0 | 0
133 | 0.9956 | -0.034203 | 0 | 0
134 | 0.99797 | -0.035536 | 0.32246 | 0.15617
135 | 0.99662 | -0.044689 | 0.37668 | 0.18243
136 | 0.99799 | -0.035478 | 0 | 0
137 | 0.99643 | -0.058543 | 0.19513 | 0.094505
138 | 0.99794 | -0.029264 | 0.33674 | 0.16309
139 | 0.9981 | -0.028245 | 0.069342 | 0.033584
140 | 0.9982 | -0.027816 | 0 | 0
141 | 0.99763 | -0.055 | 0.24658 | 0.11942
142 | 0.9974 | -0.055891 | 0.21181 | 0.10258
143 | 0.99741 | -0.055973 | 0 | 0
144 | 0.99186 | -0.048436 | 0 | 0
145 | 0.9919 | -0.048144 | 0 | 0
146 | 0.99184 | -0.048521 | 0.32402 | 0.15693
147 | 0.99231 | -0.051523 | 0.25367 | 0.12286
148 | 0.99584 | -0.053427 | 0.27772 | 0.13451
149 | 0.99588 | -0.053193 | 0 | 0
150 | 0.99589 | -0.05329 | 0 | 0
151 | 0.9968 | -0.057383 | 0.16289 | 0.078892
152 | 0.99681 | -0.057443 | 0 | 0
153 | 0.99696 | -0.057855 | 0 | 0
154 | 0.99711 | -0.057224 | 0 | 0
155 | 0.99687 | -0.057023 | 0 | 0
156 | 0.99696 | -0.057849 | 0.089325 | 0.043262
157 | 0.99711 | -0.057202 | 0.65225 | 0.3159
158 | 0.99686 | -0.056969 | 1.8813 | 0.91115
159 | 0.99747 | -0.055691 | 0 | 0
160 | 0.99747 | -0.055672 | 0.29806 | 0.14435
161 | 0.99757 | -0.055272 | 0 | 0
162 | 0.99756 | -0.032322 | 0 | 0
163 | 0.99582 | -0.052709 | 0 | 0
164 | 0.9955 | -0.049933 | 0.24875 | 0.12048
165 | 0.99546 | -0.049647 | 0 | 0
166 | 0.99623 | -0.020538 | 0 | 0
167 | 0.99623 | -0.020584 | 0.33031 | 0.15998
168 | 0.99621 | -0.020695 | 0.15066 | 0.072968
169 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.21408 | -0.10368 | 0.21411 | 0.10331 | 2.8322e-05 | -0.00037699 | 0.0069015 | 0.0068966 | 0.0069015 | 0.99495 | -0.032106 | 0.99508 | -0.031228 | 3.2865
1 | -0.6032 | -0.29175 | 0.60327 | 0.29168 | 6.6179e-05 | -7.4774e-05 | 0.019438 | 0.019437 | 0.019438 | 0.99508 | -0.031228 | 0.9952 | -0.030501 | 9.2563
2 | -0.92869 | -0.44929 | 0.92871 | 0.44904 | 1.2934e-05 | -0.00025203 | 0.029925 | 0.029922 | 0.029925 | 0.9952 | -0.030501 | 0.99521 | -0.030622 | 13.6024
3 | 0.073379 | 0.028416 | -0.073377 | -0.035172 | 2.0521e-06 | -0.0067566 | 0.0022823 | 0.0023602 | 0.0023602 | 0.99528 | -0.043724 | 0.99525 | -0.04354 | 1.0728
4 | 2.7679 | 1.2953 | -2.7652 | -1.3006 | 0.0027221 | -0.00532 | 0.088637 | 0.088712 | 0.088712 | 0.99528 | -0.043724 | 0.99436 | -0.035753 | 40.3238
5 | -2.8413 | -1.3237 | 2.8418 | 1.3228 | 0.00049384 | -0.00091236 | 0.090914 | 0.090901 | 0.090914 | 0.99528 | -0.043724 | 0.99544 | -0.045108 | 41.3245
6 | 0.073377 | 0.035172 | -0.073377 | -0.035538 | 1.1526e-07 | -0.00036581 | 0.0023602 | 0.0023648 | 0.0023648 | 0.99525 | -0.04354 | 0.99525 | -0.043527 | 1.0749
7 | 2.0301 | 0.94566 | -2.0295 | -0.94822 | 0.00065954 | -0.0025611 | 0.065018 | 0.065051 | 0.065051 | 0.99436 | -0.035753 | 0.99406 | -0.033155 | 29.5689
8 | 0.73504 | 0.35492 | -0.735 | -0.35598 | 3.3827e-05 | -0.0010546 | 0.023696 | 0.02371 | 0.02371 | 0.99436 | -0.035753 | 0.99432 | -0.035353 | 10.7772
9 | -3.2491 | -1.52 | 3.2495 | 1.5195 | 0.00040283 | -0.00054038 | 0.10402 | 0.10401 | 0.10402 | 0.99544 | -0.045108 | 0.99556 | -0.046105 | 47.2832
10 | 1.426 | 0.65895 | -1.426 | -0.65965 | 8.6136e-05 | -0.00070572 | 0.04562 | 0.045629 | 0.045629 | 0.99406 | -0.033155 | 0.99401 | -0.032683 | 20.7402
11 | 0.60344 | 0.28928 | -0.6034 | -0.29091 | 3.5217e-05 | -0.0016357 | 0.019433 | 0.019454 | 0.019454 | 0.99406 | -0.033155 | 0.99401 | -0.032655 | 8.8427
12 | -3.2495 | -1.5195 | 3.2516 | 1.5166 | 0.0021397 | -0.0028746 | 0.10401 | 0.10397 | 0.10401 | 0.99556 | -0.046105 | 0.99617 | -0.051381 | 47.2795
13 | 2.4953 | 1.1825 | -2.4917 | -1.1914 | 0.0036067 | -0.0089307 | 0.079953 | 0.080078 | 0.080078 | 0.99697 | -0.046553 | 0.99563 | -0.034433 | 36.3991
14 | -6.0344 | -2.8382 | 6.0399 | 2.8318 | 0.0054944 | -0.0064283 | 0.19309 | 0.19296 | 0.19309 | 0.99697 | -0.046553 | 0.99797 | -0.035568 | 53.3394
15 | 3.5391 | 1.6557 | -3.5366 | -1.6543 | 0.0025017 | 0.0014369 | 0.11314 | 0.11314 | 0.11314 | 0.99697 | -0.046553 | 0.99622 | -0.051824 | 53.8749
16 | 2.1843 | 1.0432 | -2.1843 | -1.0434 | 5.9365e-05 | -0.00019603 | 0.070185 | 0.070188 | 0.070188 | 0.99563 | -0.034433 | 0.9956 | -0.034203 | 31.9036
17 | 0.30735 | 0.14816 | -0.30735 | -0.14863 | 2.5996e-06 | -0.00046986 | 0.0098928 | 0.0098987 | 0.0098987 | 0.99563 | -0.034433 | 0.99562 | -0.03436 | 4.4994
18 | -9.0796 | -4.2705 | 9.0796 | 4.2699 | 6.6752e-05 | -0.00060433 | 0.29024 | 0.29023 | 0.29024 | 0.99797 | -0.035568 | 0.99797 | -0.035536 | 22.7461
19 | 3.0397 | 1.4388 | -3.0358 | -1.4366 | 0.0038663 | 0.0021495 | 0.09728 | 0.097283 | 0.097283 | 0.99797 | -0.035568 | 0.99662 | -0.044689 | 46.3253
20 | 3.2518 | 1.5164 | -3.2516 | -1.5166 | 0.00018052 | -0.00024285 | 0.10397 | 0.10397 | 0.10397 | 0.99622 | -0.051824 | 0.99617 | -0.051381 | 47.26
21 | 0.6034 | 0.29091 | -0.60337 | -0.29223 | 2.8336e-05 | -0.0013135 | 0.019454 | 0.019471 | 0.019471 | 0.99401 | -0.032655 | 0.99397 | -0.032248 | 8.8503
22 | 1.2089 | 0.55452 | -1.2088 | -0.55511 | 5.1657e-05 | -0.00059639 | 0.038625 | 0.038633 | 0.038633 | 0.99401 | -0.032683 | 0.99397 | -0.032355 | 17.5603
23 | -0.20764 | -0.10056 | 0.20764 | 0.09937 | 3.0461e-06 | -0.0011947 | 0.0067087 | 0.0066937 | 0.0067087 | 0.99274 | -0.028634 | 0.99276 | -0.02876 | 3.0494
24 | -0.37694 | -0.18058 | 0.37703 | 0.16942 | 9.2719e-05 | -0.011167 | 0.012154 | 0.012017 | 0.012154 | 0.99276 | -0.02876 | 0.99299 | -0.030703 | 5.5244
25 | 0.1693 | 0.081215 | -0.16926 | -0.081977 | 3.5465e-05 | -0.00076181 | 0.0054599 | 0.0054698 | 0.0054698 | 0.99276 | -0.02876 | 0.99254 | -0.030166 | 2.6047
26 | 0.10963 | 0.050618 | -0.10962 | -0.053093 | 1.7449e-06 | -0.002475 | 0.0035103 | 0.0035411 | 0.0035411 | 0.99299 | -0.030703 | 0.99297 | -0.030571 | 1.6096
27 | -0.48666 | -0.22004 | 0.48669 | 0.21748 | 3.5069e-05 | -0.0025601 | 0.015527 | 0.015496 | 0.015527 | 0.99299 | -0.030703 | 0.99305 | -0.031228 | 7.0576
28 | -0.1918 | -0.092893 | 0.1918 | 0.091153 | 3.7671e-06 | -0.0017406 | 0.0061912 | 0.0061693 | 0.0061912 | 0.99367 | -0.040617 | 0.99369 | -0.040785 | 2.8142
29 | -1.916 | -0.90648 | 1.9164 | 0.90474 | 0.00039756 | -0.0017347 | 0.061578 | 0.061555 | 0.061578 | 0.99369 | -0.040785 | 0.99388 | -0.042494 | 27.9898
30 | 1.7242 | 0.81532 | -1.723 | -0.81481 | 0.0012498 | 0.00051373 | 0.055408 | 0.055412 | 0.055412 | 0.99369 | -0.040785 | 0.99292 | -0.045996 | 26.3865
31 | -2.4988 | -1.1868 | 2.4992 | 1.187 | 0.00042395 | 0.00022186 | 0.080248 | 0.080248 | 0.080248 | 0.99512 | -0.034078 | 0.9953 | -0.032877 | 38.2134
32 | 2.166 | 1.0256 | -2.1635 | -1.0244 | 0.0025464 | 0.0012459 | 0.069523 | 0.069527 | 0.069527 | 0.99512 | -0.034078 | 0.99388 | -0.042494 | 33.1081
33 | -2.4992 | -1.187 | 2.5006 | 1.1835 | 0.0014202 | -0.0034904 | 0.080248 | 0.080199 | 0.080248 | 0.9953 | -0.032877 | 0.99582 | -0.037593 | 36.4762
34 | 0.24706 | 0.11962 | -0.24705 | -0.11965 | 3.4268e-06 | -3.3532e-05 | 0.0079727 | 0.0079732 | 0.0079732 | 0.99388 | -0.042494 | 0.99386 | -0.042586 | 3.7968
35 | 1.723 | 0.81481 | -1.7229 | -0.81536 | 0.00010201 | -0.00055542 | 0.055412 | 0.055419 | 0.055419 | 0.99292 | -0.045996 | 0.99287 | -0.045507 | 25.1904
36 | 1.5077 | 0.71115 | -1.5075 | -0.71276 | 0.00022271 | -0.0016044 | 0.048468 | 0.048489 | 0.048489 | 0.99287 | -0.045507 | 0.99273 | -0.044291 | 22.0403
37 | -0.71432 | -0.32515 | 0.71459 | 0.32497 | 0.00027225 | -0.00017528 | 0.022815 | 0.022811 | 0.022815 | 0.99305 | -0.031228 | 0.99346 | -0.028127 | 10.8642
38 | 0.22762 | 0.10767 | -0.22762 | -0.1095 | 5.5802e-06 | -0.0018294 | 0.0073198 | 0.0073428 | 0.0073428 | 0.99305 | -0.031228 | 0.99303 | -0.031021 | 3.3376
39 | 1.5075 | 0.71276 | -1.507 | -0.71595 | 0.00044442 | -0.0031961 | 0.048489 | 0.04853 | 0.04853 | 0.99273 | -0.044291 | 0.99246 | -0.041845 | 22.0592
40 | -0.90498 | -0.41718 | 0.90521 | 0.41244 | 0.00022821 | -0.0047475 | 0.028956 | 0.028898 | 0.028956 | 0.99346 | -0.028127 | 0.99369 | -0.030058 | 13.162
41 | 0.07459 | 0.035386 | -0.074584 | -0.036122 | 6.4786e-06 | -0.00073619 | 0.0024 | 0.0024093 | 0.0024093 | 0.99303 | -0.031021 | 0.99294 | -0.031616 | 1.1473
42 | -1.2085 | -0.55923 | 1.2088 | 0.55511 | 0.00035744 | -0.004119 | 0.038684 | 0.038633 | 0.038684 | 0.99369 | -0.030058 | 0.99397 | -0.032355 | 17.5836
43 | 0.30326 | 0.1468 | -0.30325 | -0.14687 | 1.1903e-05 | -7.4733e-05 | 0.0097879 | 0.009789 | 0.009789 | 0.99369 | -0.030058 | 0.99365 | -0.030317 | 4.6614
44 | -0.076684 | -0.03714 | 0.076687 | 0.036864 | 2.5817e-06 | -0.00027594 | 0.0024789 | 0.0024754 | 0.0024789 | 0.99223 | -0.051342 | 0.99227 | -0.051117 | 1.1804
45 | -0.32096 | -0.15517 | 0.32096 | 0.15501 | 9.4603e-07 | -0.00015462 | 0.010371 | 0.010369 | 0.010371 | 0.99227 | -0.051117 | 0.99227 | -0.051143 | 4.7143
46 | -0.42473 | -0.20438 | 0.42473 | 0.20404 | 3.6135e-06 | -0.00033747 | 0.013712 | 0.013708 | 0.013712 | 0.99229 | -0.051288 | 0.99229 | -0.051361 | 6.2329
47 | 0.32096 | 0.15413 | -0.32096 | -0.15501 | 5.4279e-06 | -0.00088828 | 0.010358 | 0.010369 | 0.010369 | 0.99229 | -0.051288 | 0.99227 | -0.051143 | 4.7134
48 | -0.42473 | -0.20404 | 0.42474 | 0.20272 | 1.4116e-05 | -0.0013203 | 0.013708 | 0.013691 | 0.013708 | 0.99229 | -0.051361 | 0.99232 | -0.051644 | 6.2309
49 | 0.25367 | 0.12193 | -0.25367 | -0.12286 | 3.5322e-06 | -0.00092552 | 0.0081878 | 0.0081995 | 0.0081995 | 0.99232 | -0.051644 | 0.99231 | -0.051523 | 3.7271
50 | -1.4587 | -0.67724 | 1.46 | 0.67763 | 0.0012221 | 0.00039675 | 0.046786 | 0.046782 | 0.046786 | 0.99232 | -0.051644 | 0.99321 | -0.045242 | 22.2792
51 | 0.78032 | 0.35258 | -0.77997 | -0.36254 | 0.00035658 | -0.0099613 | 0.02491 | 0.025032 | 0.025032 | 0.99232 | -0.051644 | 0.9919 | -0.048144 | 11.3782
52 | -0.07474 | -0.036198 | 0.074741 | 0.035122 | 3.5541e-07 | -0.001076 | 0.0024172 | 0.0024037 | 0.0024172 | 0.99177 | -0.04776 | 0.99178 | -0.0478 | 1.0987
53 | -0.45587 | -0.20884 | 0.45591 | 0.20565 | 3.8623e-05 | -0.0031869 | 0.014595 | 0.014557 | 0.014595 | 0.99178 | -0.0478 | 0.99186 | -0.048436 | 6.6341
54 | 0.38113 | 0.17371 | -0.38111 | -0.17609 | 2.0225e-05 | -0.002382 | 0.012192 | 0.012221 | 0.012221 | 0.99178 | -0.0478 | 0.99173 | -0.047393 | 5.5548
55 | -0.1482 | -0.071778 | 0.14821 | 0.071652 | 4.4763e-06 | -0.00012558 | 0.0047938 | 0.0047921 | 0.0047938 | 0.99162 | -0.046932 | 0.99165 | -0.046733 | 2.2827
56 | -0.14821 | -0.071652 | 0.14821 | 0.067617 | 5.2151e-06 | -0.0040351 | 0.0047921 | 0.0047422 | 0.0047921 | 0.99165 | -0.046733 | 0.99168 | -0.047019 | 2.1782
57 | 0.084158 | 0.038998 | -0.084157 | -0.040759 | 7.3592e-07 | -0.001761 | 0.0027 | 0.002722 | 0.002722 | 0.99168 | -0.047019 | 0.99168 | -0.046946 | 1.2373
58 | -0.23237 | -0.10662 | 0.23237 | 0.10557 | 3.2735e-06 | -0.0010403 | 0.0074422 | 0.0074296 | 0.0074422 | 0.99168 | -0.047019 | 0.9917 | -0.047126 | 3.3828
59 | -0.3811 | -0.17761 | 0.38111 | 0.17609 | 1.289e-05 | -0.0015121 | 0.012239 | 0.012221 | 0.012239 | 0.9917 | -0.047126 | 0.99173 | -0.047393 | 5.5632
60 | -0.26108 | -0.12645 | 0.26109 | 0.12613 | 1.257e-06 | -0.00031626 | 0.0084013 | 0.0083973 | 0.0084013 | 0.99678 | -0.025674 | 0.99679 | -0.025716 | 3.8188
61 | -0.26109 | -0.12613 | 0.26113 | 0.11531 | 4.2304e-05 | -0.010822 | 0.0083973 | 0.0082657 | 0.0083973 | 0.99679 | -0.025716 | 0.99694 | -0.026983 | 3.817
62 | 0.15135 | 0.072115 | -0.15135 | -0.072952 | 1.1129e-06 | -0.00083729 | 0.0048546 | 0.0048651 | 0.0048651 | 0.99694 | -0.026983 | 0.99693 | -0.026921 | 2.2114
63 | -1.6163 | -0.75699 | 1.6167 | 0.75438 | 0.00040953 | -0.0026064 | 0.051681 | 0.051648 | 0.051681 | 0.99694 | -0.026983 | 0.99718 | -0.029018 | 23.4914
64 | 1.0373 | 0.48895 | -1.0366 | -0.49981 | 0.00068933 | -0.010856 | 0.033206 | 0.033344 | 0.033344 | 0.99694 | -0.026983 | 0.99632 | -0.021393 | 15.1562
65 | 0.16655 | 0.080615 | -0.16654 | -0.080661 | 2.0108e-06 | -4.5383e-05 | 0.0053577 | 0.0053583 | 0.0053583 | 0.99694 | -0.026983 | 0.99693 | -0.027063 | 2.5516
66 | 0.15135 | 0.072952 | -0.15135 | -0.073302 | 4.6574e-07 | -0.00034932 | 0.0048651 | 0.0048695 | 0.0048695 | 0.99693 | -0.026921 | 0.99693 | -0.026894 | 2.2134
67 | -1.7724 | -0.82811 | 1.7726 | 0.8272 | 0.00017408 | -0.00091384 | 0.056634 | 0.056622 | 0.056634 | 0.99718 | -0.029018 | 0.99727 | -0.029805 | 25.7428
68 | 0.15568 | 0.073728 | -0.15568 | -0.075397 | 2.3454e-06 | -0.0016697 | 0.0049866 | 0.0050075 | 0.0050075 | 0.99718 | -0.029018 | 0.99716 | -0.02889 | 2.2761
69 | 1.0366 | 0.49981 | -1.0365 | -0.50092 | 7.1227e-05 | -0.0011157 | 0.033344 | 0.033358 | 0.033358 | 0.99632 | -0.021393 | 0.99626 | -0.020799 | 15.1627
70 | -1.7726 | -0.8272 | 1.7728 | 0.82613 | 0.00020425 | -0.001073 | 0.056622 | 0.056609 | 0.056622 | 0.99727 | -0.029805 | 0.99738 | -0.030725 | 25.7375
71 | 0.58932 | 0.28432 | -0.58931 | -0.28472 | 8.1846e-06 | -0.00040164 | 0.018959 | 0.018965 | 0.018965 | 0.99626 | -0.020799 | 0.99625 | -0.020679 | 8.6203
72 | -2.1653 | -1.0162 | 2.1657 | 1.0148 | 0.0004274 | -0.0014605 | 0.06923 | 0.06921 | 0.06923 | 0.99738 | -0.030725 | 0.99756 | -0.032322 | 31.4682
73 | 0.79777 | 0.38244 | -0.79776 | -0.38294 | 1.8682e-05 | -0.0004971 | 0.025659 | 0.025665 | 0.025665 | 0.99534 | -0.03183 | 0.99532 | -0.03163 | 11.666
74 | 0.92884 | 0.4465 | -0.92871 | -0.44904 | 0.00013014 | -0.0025393 | 0.029889 | 0.029922 | 0.029922 | 0.99534 | -0.03183 | 0.99521 | -0.030622 | 13.6009
75 | -2.0075 | -0.96019 | 2.0076 | 0.95963 | 0.00013971 | -0.00055297 | 0.06454 | 0.064532 | 0.06454 | 0.99534 | -0.03183 | 0.99541 | -0.032419 | 29.3363
76 | 0.28089 | 0.13125 | -0.28087 | -0.13597 | 2.1706e-05 | -0.0047191 | 0.0089919 | 0.0090508 | 0.0090508 | 0.99534 | -0.03183 | 0.99527 | -0.031183 | 4.114
77 | 0.79776 | 0.38294 | -0.79773 | -0.38374 | 3.0091e-05 | -0.00080012 | 0.025665 | 0.025675 | 0.025675 | 0.99532 | -0.03163 | 0.99529 | -0.031307 | 11.6706
78 | -2.1015 | -1.0051 | 2.1016 | 1.0047 | 0.00010474 | -0.00037563 | 0.067558 | 0.067553 | 0.067558 | 0.99541 | -0.032419 | 0.99545 | -0.032841 | 30.7083
79 | 0.28087 | 0.13597 | -0.28086 | -0.13603 | 8.0095e-06 | -5.9871e-05 | 0.0090508 | 0.0090516 | 0.0090516 | 0.99527 | -0.031183 | 0.99524 | -0.031372 | 4.3103
80 | 0.68457 | 0.32894 | -0.68455 | -0.32975 | 2.2475e-05 | -0.00081347 | 0.022029 | 0.022039 | 0.022039 | 0.99529 | -0.031307 | 0.99526 | -0.031026 | 10.0177
81 | 0.48098 | 0.23226 | -0.48098 | -0.23283 | 7.7957e-06 | -0.0005751 | 0.015477 | 0.015484 | 0.015484 | 0.99625 | -0.020679 | 0.99623 | -0.020538 | 7.0383
82 | 0.1549 | 0.074534 | -0.1549 | -0.075022 | 6.9002e-07 | -0.00048809 | 0.0049931 | 0.0049993 | 0.0049993 | 0.99383 | -0.039748 | 0.99383 | -0.039709 | 2.2724
83 | -0.45387 | -0.21933 | 0.4539 | 0.21682 | 3.0489e-05 | -0.0025087 | 0.014642 | 0.01461 | 0.014642 | 0.99383 | -0.039748 | 0.9939 | -0.040323 | 6.6555
84 | -2.1248 | -0.99653 | 2.1264 | 0.99094 | 0.0015927 | -0.0055944 | 0.068165 | 0.068091 | 0.068165 | 0.9939 | -0.040323 | 0.99459 | -0.046343 | 30.9842
85 | 1.6709 | 0.77971 | -1.6698 | -0.77928 | 0.0010936 | 0.00043282 | 0.053555 | 0.053558 | 0.053558 | 0.9939 | -0.040323 | 0.99321 | -0.045242 | 25.504
86 | -2.1264 | -0.99094 | 2.127 | 0.98895 | 0.00056319 | -0.0019834 | 0.068091 | 0.068064 | 0.068091 | 0.99459 | -0.046343 | 0.99484 | -0.048449 | 30.9503
87 | -2.2306 | -1.0391 | 2.2311 | 1.0394 | 0.00055559 | 0.00027572 | 0.071404 | 0.071403 | 0.071404 | 0.99484 | -0.048449 | 0.9951 | -0.046567 | 34.0017
88 | -2.3362 | -1.0903 | 2.3368 | 1.0886 | 0.00060386 | -0.0017339 | 0.07479 | 0.074766 | 0.07479 | 0.9951 | -0.046567 | 0.99534 | -0.04863 | 33.9953
89 | -2.3368 | -1.0886 | 2.3371 | 1.0877 | 0.00029874 | -0.00085857 | 0.074766 | 0.074755 | 0.074766 | 0.99534 | -0.04863 | 0.99546 | -0.049647 | 33.9846
90 | 22.1512 | 10.278 | -22.149 | -10.2804 | 0.0022331 | -0.002397 | 0.70493 | 0.70497 | 0.70497 | 1 | 0 | 0.9999 | -0.00047072 | 55.2488
91 | 22.149 | 10.2804 | -22.138 | -10.2921 | 0.010935 | -0.01172 | 0.70497 | 0.70519 | 0.70519 | 0.9999 | -0.00047072 | 0.99938 | -0.0027649 | 55.2658
92 | 11.7953 | 5.4752 | -11.7915 | -5.495 | 0.0038135 | -0.019786 | 0.37563 | 0.3759 | 0.3759 | 0.99938 | -0.0027649 | 0.99905 | -0.0042577 | 29.459
93 | 10.3427 | 4.8168 | -10.3423 | -4.8191 | 0.00033264 | -0.0023003 | 0.32956 | 0.32959 | 0.32959 | 0.99938 | -0.0027649 | 0.99935 | -0.0029122 | 25.8301
94 | 11.7915 | 5.495 | -11.7906 | -5.5 | 0.00097118 | -0.0050314 | 0.3759 | 0.37596 | 0.37596 | 0.99905 | -0.0042577 | 0.99896 | -0.0046332 | 29.4643
95 | 10.0594 | 4.6821 | -10.0581 | -4.6789 | 0.0012534 | 0.0031817 | 0.32051 | 0.32051 | 0.32051 | 0.99935 | -0.0029122 | 0.99912 | -0.015963 | 24.8461
96 | 11.4543 | 5.3372 | -11.452 | -5.3311 | 0.0023541 | 0.0060576 | 0.36517 | 0.36517 | 0.36517 | 0.99896 | -0.0046332 | 0.99858 | -0.02615 | 28.308
97 | 0.74193 | 0.35888 | -0.74191 | -0.35932 | 1.4837e-05 | -0.00044787 | 0.024004 | 0.02401 | 0.02401 | 0.99113 | -0.037909 | 0.99111 | -0.037735 | 10.9137
98 | -0.74193 | -0.35888 | 0.74212 | 0.35877 | 0.00019553 | -0.00010096 | 0.024004 | 0.024002 | 0.024004 | 0.99113 | -0.037909 | 0.9914 | -0.036162 | 11.4307
99 | -1.0571 | -0.51132 | 1.0571 | 0.51117 | 9.8069e-06 | -0.00014456 | 0.034191 | 0.03419 | 0.034191 | 0.9914 | -0.036162 | 0.99141 | -0.036242 | 15.5416
100 | 10.0581 | 4.6789 | -10.0549 | -4.7025 | 0.0032094 | -0.023526 | 0.32051 | 0.32082 | 0.32082 | 0.99912 | -0.015963 | 0.99879 | -0.017414 | 25.143
101 | -2.5006 | -1.1835 | 2.501 | 1.1825 | 0.00039304 | -0.00096755 | 0.080199 | 0.080186 | 0.080199 | 0.99582 | -0.037593 | 0.99597 | -0.038891 | 36.4541
102 | -2.6573 | -1.2582 | 2.6578 | 1.2571 | 0.00051214 | -0.0010997 | 0.085218 | 0.085202 | 0.085218 | 0.99597 | -0.038891 | 0.99615 | -0.040485 | 38.7353
103 | -2.6578 | -1.2571 | 2.6589 | 1.2547 | 0.0011041 | -0.0023737 | 0.085202 | 0.085169 | 0.085202 | 0.99615 | -0.040485 | 0.99653 | -0.043905 | 38.7282
104 | -2.6589 | -1.2547 | 2.6592 | 1.2542 | 0.00025413 | -0.00054699 | 0.085169 | 0.085161 | 0.085169 | 0.99653 | -0.043905 | 0.99662 | -0.044689 | 38.713
105 | 1.0573 | 0.50785 | -1.0571 | -0.51117 | 0.00022476 | -0.0033183 | 0.034147 | 0.03419 | 0.03419 | 0.99161 | -0.038074 | 0.99141 | -0.036242 | 15.5407
106 | -1.0573 | -0.50785 | 1.0574 | 0.50669 | 7.8564e-05 | -0.0011622 | 0.034147 | 0.034132 | 0.034147 | 0.99161 | -0.038074 | 0.99168 | -0.038708 | 15.5213
107 | -1.1686 | -0.56053 | 1.1687 | 0.55931 | 0.00010143 | -0.0012239 | 0.037727 | 0.037712 | 0.037727 | 0.99168 | -0.038708 | 0.99176 | -0.039446 | 17.1488
108 | 1.507 | 0.71595 | -1.5067 | -0.71583 | 0.00035867 | 0.00012418 | 0.04853 | 0.048531 | 0.048531 | 0.99246 | -0.041845 | 0.99221 | -0.043528 | 23.1102
109 | -1.1687 | -0.55931 | 1.1692 | 0.55278 | 0.00053942 | -0.00653 | 0.037712 | 0.037628 | 0.037712 | 0.99176 | -0.039446 | 0.99218 | -0.043307 | 17.1416
110 | -1.1692 | -0.55278 | 1.1692 | 0.55239 | 3.1416e-05 | -0.0003814 | 0.037628 | 0.037623 | 0.037628 | 0.99218 | -0.043307 | 0.99221 | -0.043528 | 17.1036
111 | 11.452 | 5.3311 | -11.4478 | -5.3543 | 0.0042017 | -0.023158 | 0.36517 | 0.36549 | 0.36549 | 0.99858 | -0.02615 | 0.9982 | -0.027816 | 28.6431
112 | 10.0549 | 4.7025 | -10.0541 | -4.7086 | 0.00083584 | -0.0061161 | 0.32082 | 0.3209 | 0.3209 | 0.99879 | -0.017414 | 0.9987 | -0.017786 | 25.1493
113 | 9.8079 | 4.5893 | -9.8064 | -4.5856 | 0.0014864 | 0.0037628 | 0.313 | 0.313 | 0.313 | 0.9987 | -0.017786 | 0.99842 | -0.033613 | 24.2636
114 | 9.4062 | 4.3917 | -9.4057 | -4.3953 | 0.00042853 | -0.0036147 | 0.30014 | 0.30019 | 0.30019 | 0.99842 | -0.033613 | 0.99838 | -0.033819 | 23.526
115 | 9.4057 | 4.3953 | -9.4022 | -4.425 | 0.0035283 | -0.029702 | 0.30019 | 0.30058 | 0.30058 | 0.99838 | -0.033819 | 0.99799 | -0.035478 | 23.5565
116 | -0.34267 | -0.16596 | 0.3427 | 0.16581 | 3.2656e-05 | -0.00015714 | 0.011046 | 0.011044 | 0.011046 | 0.99501 | -0.032055 | 0.99511 | -0.031425 | 5.2601
117 | -0.3427 | -0.16581 | 0.34271 | 0.16541 | 2.7626e-06 | -0.0004005 | 0.011044 | 0.011039 | 0.011044 | 0.99511 | -0.031425 | 0.99512 | -0.031495 | 5.02
118 | 0.071695 | 0.034256 | -0.071695 | -0.034724 | 1.4058e-07 | -0.00046737 | 0.002305 | 0.0023109 | 0.0023109 | 0.99512 | -0.031495 | 0.99512 | -0.031478 | 1.0504
119 | -0.68446 | -0.33046 | 0.68453 | 0.3304 | 7.1524e-05 | -5.2837e-05 | 0.022049 | 0.022047 | 0.022049 | 0.99512 | -0.031495 | 0.99523 | -0.030798 | 10.4993
120 | -0.35574 | -0.17229 | 0.35574 | 0.17213 | 1.2063e-06 | -0.00016326 | 0.011447 | 0.011445 | 0.011447 | 0.99679 | -0.058292 | 0.99679 | -0.058322 | 5.2033
121 | -0.35574 | -0.17213 | 0.35575 | 0.17124 | 6.5875e-06 | -0.0008926 | 0.011445 | 0.011434 | 0.011445 | 0.99679 | -0.058322 | 0.99681 | -0.058482 | 5.2023
122 | 4.4649 | 2.1041 | -4.4643 | -2.1057 | 0.00058081 | -0.0015835 | 0.14294 | 0.14297 | 0.14297 | 0.99681 | -0.058482 | 0.99667 | -0.060038 | 39.4932
123 | -4.8206 | -2.2753 | 4.8208 | 2.2698 | 0.00016611 | -0.0055423 | 0.15437 | 0.1543 | 0.15437 | 0.99681 | -0.058482 | 0.99685 | -0.058334 | 12.0983
124 | 1.3022 | 0.62779 | -1.3021 | -0.62877 | 9.9003e-05 | -0.00097345 | 0.041872 | 0.041885 | 0.041885 | 0.99667 | -0.060038 | 0.9966 | -0.059381 | 19.0385
125 | 3.1621 | 1.4779 | -3.1615 | -1.4787 | 0.00057623 | -0.00083043 | 0.1011 | 0.10111 | 0.10111 | 0.99667 | -0.060038 | 0.9965 | -0.058574 | 45.958
126 | -4.9114 | -2.3137 | 4.9116 | 2.3075 | 0.0001932 | -0.0062117 | 0.15722 | 0.15714 | 0.15722 | 0.99685 | -0.058334 | 0.99689 | -0.058163 | 12.3214
127 | 1.3021 | 0.62877 | -1.302 | -0.63043 | 0.00016908 | -0.0016607 | 0.041885 | 0.041906 | 0.041906 | 0.9966 | -0.059381 | 0.99648 | -0.058254 | 19.0483
128 | 3.0408 | 1.4203 | -3.0393 | -1.4227 | 0.0015343 | -0.0024251 | 0.097225 | 0.09726 | 0.09726 | 0.9965 | -0.058574 | 0.99603 | -0.054517 | 44.2091
129 | 0.57465 | 0.27279 | -0.5746 | -0.2752 | 4.6377e-05 | -0.0024114 | 0.01842 | 0.018451 | 0.018451 | 0.99689 | -0.058163 | 0.99681 | -0.057484 | 8.3866
130 | -5.4863 | -2.5803 | 5.4867 | 2.5704 | 0.00038305 | -0.0098375 | 0.17556 | 0.17544 | 0.17556 | 0.99689 | -0.058163 | 0.99696 | -0.057855 | 13.7589
131 | 0.19514 | 0.094366 | -0.19513 | -0.094505 | 8.5274e-06 | -0.0001385 | 0.0062793 | 0.0062811 | 0.0062811 | 0.99648 | -0.058254 | 0.99643 | -0.058543 | 2.991
132 | 2.8652 | 1.3384 | -2.8648 | -1.3392 | 0.00043805 | -0.00079503 | 0.091654 | 0.091666 | 0.091666 | 0.99603 | -0.054517 | 0.99589 | -0.05329 | 41.6662
133 | -2.1839 | -1.0446 | 2.1843 | 1.0434 | 0.0003518 | -0.0011612 | 0.070204 | 0.070188 | 0.070204 | 0.99545 | -0.032841 | 0.9956 | -0.034203 | 31.9108
134 | 0.68455 | 0.32975 | -0.68453 | -0.3304 | 1.809e-05 | -0.00065417 | 0.022039 | 0.022047 | 0.022047 | 0.99526 | -0.031026 | 0.99523 | -0.030798 | 10.0215
135 | -0.23248 | -0.11259 | 0.23249 | 0.1125 | 8.7645e-06 | -9.8273e-05 | 0.0074902 | 0.0074889 | 0.0074902 | 0.99553 | -0.034905 | 0.99557 | -0.034656 | 3.5668
136 | -0.23249 | -0.1125 | 0.2325 | 0.11238 | 1.0383e-05 | -0.00011648 | 0.0074889 | 0.0074873 | 0.0074889 | 0.99557 | -0.034656 | 0.99562 | -0.03436 | 3.5661
137 | -0.33504 | -0.16227 | 0.33505 | 0.16188 | 2.5661e-06 | -0.0003917 | 0.010781 | 0.010776 | 0.010781 | 0.99678 | -0.057148 | 0.99678 | -0.057215 | 4.9006
138 | -0.33505 | -0.16188 | 0.33505 | 0.16161 | 1.7309e-06 | -0.00026442 | 0.010776 | 0.010773 | 0.010776 | 0.99678 | -0.057215 | 0.99679 | -0.057259 | 4.8984
139 | -0.33505 | -0.16161 | 0.33505 | 0.16109 | 3.4212e-06 | -0.00052314 | 0.010773 | 0.010766 | 0.010773 | 0.99679 | -0.057259 | 0.9968 | -0.057347 | 4.8968
140 | -0.4117 | -0.19821 | 0.41171 | 0.19755 | 6.5557e-06 | -0.00066377 | 0.013233 | 0.013225 | 0.013233 | 0.9968 | -0.057347 | 0.99681 | -0.057484 | 6.015
141 | 0.16289 | 0.077651 | -0.16289 | -0.078153 | 7.7241e-07 | -0.00050177 | 0.0052259 | 0.0052322 | 0.0052322 | 0.99681 | -0.057484 | 0.99681 | -0.057443 | 2.3783
142 | -9.4021 | -4.4261 | 9.4022 | 4.425 | 0.0001278 | -0.0010738 | 0.3006 | 0.30058 | 0.3006 | 0.99797 | -0.035536 | 0.99799 | -0.035478 | 23.5576
143 | -0.33674 | -0.16309 | 0.33679 | 0.16283 | 5.1883e-05 | -0.0002632 | 0.010823 | 0.010819 | 0.010823 | 0.99794 | -0.029264 | 0.9981 | -0.028245 | 5.1539
144 | -9.2798 | -4.3466 | 9.2807 | 4.3389 | 0.00088994 | -0.0077117 | 0.29638 | 0.29628 | 0.29638 | 0.9981 | -0.028245 | 0.9982 | -0.027816 | 23.2271
145 | 8.8737 | 4.1502 | -8.8714 | -4.1445 | 0.0022724 | 0.0056741 | 0.28333 | 0.28334 | 0.28334 | 0.9981 | -0.028245 | 0.99763 | -0.055 | 21.9641
146 | 2.167 | 1.0154 | -2.1657 | -1.0148 | 0.0013169 | 0.00064143 | 0.069208 | 0.06921 | 0.06921 | 0.9982 | -0.027816 | 0.99756 | -0.032322 | 32.9574
147 | 8.6249 | 4.0251 | -8.6243 | -4.0304 | 0.0005203 | -0.0052581 | 0.27541 | 0.27548 | 0.27548 | 0.99763 | -0.055 | 0.99757 | -0.055272 | 21.5891
148 | -0.21181 | -0.10258 | 0.21181 | 0.10181 | 2.0303e-06 | -0.00077909 | 0.0068116 | 0.0068017 | 0.0068116 | 0.9974 | -0.055891 | 0.99741 | -0.055973 | 3.0962
149 | 8.1131 | 3.7982 | -8.1108 | -3.8247 | 0.0023173 | -0.026543 | 0.25927 | 0.25962 | 0.25962 | 0.99741 | -0.055973 | 0.99711 | -0.057224 | 20.3461
150 | -8.3249 | -3.9 | 8.3255 | 3.8943 | 0.00052646 | -0.0057226 | 0.26607 | 0.266 | 0.26607 | 0.99741 | -0.055973 | 0.99747 | -0.055691 | 20.8522
151 | -0.77994 | -0.36256 | 0.77997 | 0.36254 | 2.9881e-05 | -1.2718e-05 | 0.025032 | 0.025032 | 0.025032 | 0.99186 | -0.048436 | 0.9919 | -0.048144 | 11.9202
152 | 0.32402 | 0.15691 | -0.32402 | -0.15693 | 4.1945e-06 | -2.2555e-05 | 0.010478 | 0.010478 | 0.010478 | 0.99186 | -0.048436 | 0.99184 | -0.048521 | 4.9897
153 | -0.27772 | -0.13451 | 0.27773 | 0.13443 | 9.8494e-06 | -7.5635e-05 | 0.0089451 | 0.0089441 | 0.0089451 | 0.99584 | -0.053427 | 0.99588 | -0.053193 | 4.2596
154 | -0.27773 | -0.13443 | 0.27773 | 0.13374 | 3.1044e-06 | -0.00068809 | 0.0089441 | 0.0089354 | 0.0089441 | 0.99588 | -0.053193 | 0.99589 | -0.05329 | 4.0655
155 | 2.587 | 1.2054 | -2.5868 | -1.2059 | 0.00018834 | -0.00043216 | 0.082731 | 0.082737 | 0.082737 | 0.99589 | -0.05329 | 0.99582 | -0.052709 | 37.6076
156 | -0.16289 | -0.078892 | 0.16289 | 0.078153 | 1.1409e-06 | -0.00073895 | 0.0052415 | 0.0052322 | 0.0052415 | 0.9968 | -0.057383 | 0.99681 | -0.057443 | 2.3825
157 | -7.4575 | -3.5238 | 7.4586 | 3.5089 | 0.0010971 | -0.014946 | 0.23883 | 0.23864 | 0.23883 | 0.99696 | -0.057855 | 0.99711 | -0.057224 | 18.717
158 | 1.8815 | 0.91028 | -1.8813 | -0.9111 | 0.00018002 | -0.00082006 | 0.06052 | 0.060531 | 0.060531 | 0.99696 | -0.057855 | 0.99687 | -0.057023 | 27.5143
159 | 0.089326 | 0.043126 | -0.089325 | -0.043262 | 6.337e-08 | -0.00013639 | 0.0028721 | 0.0028739 | 0.0028739 | 0.99696 | -0.057855 | 0.99696 | -0.057849 | 1.3063
160 | 0.65225 | 0.31583 | -0.65225 | -0.3159 | 1.6551e-06 | -6.6364e-05 | 0.020981 | 0.020982 | 0.020982 | 0.99711 | -0.057224 | 0.99711 | -0.057202 | 9.5371
161 | 1.8813 | 0.9111 | -1.8813 | -0.91115 | 1.1749e-05 | -5.3506e-05 | 0.060531 | 0.060532 | 0.060532 | 0.99687 | -0.057023 | 0.99686 | -0.056969 | 27.5146
162 | 0.29806 | 0.14423 | -0.29806 | -0.14435 | 6.496e-07 | -0.00012566 | 0.0095828 | 0.0095844 | 0.0095844 | 0.99747 | -0.055691 | 0.99747 | -0.055672 | 4.3565
163 | -8.6235 | -4.0385 | 8.6243 | 4.0304 | 0.00080614 | -0.00814 | 0.27558 | 0.27548 | 0.27558 | 0.99747 | -0.055691 | 0.99757 | -0.055272 | 21.5974
164 | 2.5868 | 1.2059 | -2.5859 | -1.2079 | 0.00089761 | -0.0020578 | 0.082737 | 0.082765 | 0.082765 | 0.99582 | -0.052709 | 0.9955 | -0.049933 | 37.6206
165 | 2.3372 | 1.0875 | -2.3371 | -1.0877 | 8.4114e-05 | -0.00024183 | 0.074751 | 0.074755 | 0.074755 | 0.9955 | -0.049933 | 0.99546 | -0.049647 | 33.9793
166 | 0.33031 | 0.15996 | -0.33031 | -0.15998 | 2.3193e-06 | -1.2184e-05 | 0.010635 | 0.010635 | 0.010635 | 0.99623 | -0.020538 | 0.99623 | -0.020584 | 5.0642
167 | 0.15066 | 0.072869 | -0.15066 | -0.072968 | 3.5903e-06 | -9.9241e-05 | 0.0048496 | 0.0048508 | 0.0048508 | 0.99623 | -0.020538 | 0.99621 | -0.020695 | 2.3099

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 22.4236 | 10.4136

## res_load
| p_mw | q_mvar
0 | 0.21408 | 0.10368
1 | 0.38909 | 0.18845
2 | 0.32542 | 0.15761
3 | 0.40728 | 0.19726
4 | 0.735 | 0.35598
5 | 0.073377 | 0.035538
6 | 0.28481 | 0.13794
7 | 0.60337 | 0.29223
8 | 0.21707 | 0.10513
9 | 0.20764 | 0.10056
10 | 0.16926 | 0.081977
11 | 0.1918 | 0.092893
12 | 0.33277 | 0.16117
13 | 0.21517 | 0.10421
14 | 0.10962 | 0.053093
15 | 0.19039 | 0.092212
16 | 0.15303 | 0.074115
17 | 0.30325 | 0.14687
18 | 0.074584 | 0.036122
19 | 0.076684 | 0.03714
20 | 0.24427 | 0.11831
21 | 0.10376 | 0.050255
22 | 0.07474 | 0.036198
23 | 0.1482 | 0.071778
24 | 0.084157 | 0.040759
25 | 0.14873 | 0.072032
26 | 0.26108 | 0.12645
27 | 0.16654 | 0.080661
28 | 0.15568 | 0.075397
29 | 0.44722 | 0.2166
30 | 0.15135 | 0.073302
31 | 0.3925 | 0.1901
32 | 0.093903 | 0.045479
33 | 0.11315 | 0.054803
34 | 0.10833 | 0.052464
35 | 0.29897 | 0.1448
36 | 0.1549 | 0.075022
37 | 0.20986 | 0.10164
38 | 0.10359 | 0.050169
39 | 0.10509 | 0.050896
40 | 0.25841 | 0.12515
41 | 0.28294 | 0.13704
42 | 0.33624 | 0.16285
43 | 0.74191 | 0.35932
44 | 0.31496 | 0.15254
45 | 0.15626 | 0.075678
46 | 0.24705 | 0.11965
47 | 0.11116 | 0.053839
48 | 0.33745 | 0.16343
49 | 0.24623 | 0.11925
50 | 0.40021 | 0.19383
51 | 0.34267 | 0.16596
52 | 0.27006 | 0.1308
53 | 0.35574 | 0.17229
54 | 0.090656 | 0.043906
55 | 0.12064 | 0.058431
56 | 1.1068 | 0.53606
57 | 0.17409 | 0.084318
58 | 0.28086 | 0.13603
59 | 0.082265 | 0.039843
60 | 0.23248 | 0.11259
61 | 0.074849 | 0.036251
62 | 0.071695 | 0.034724
63 | 0.33504 | 0.16227
64 | 0.076651 | 0.037124
65 | 0.32246 | 0.15617
66 | 0.37668 | 0.18243
67 | 0.19513 | 0.094505
68 | 0.33674 | 0.16309
69 | 0.069342 | 0.033584
70 | 0.24658 | 0.11942
71 | 0.21181 | 0.10258
72 | 0.32402 | 0.15693
73 | 0.25367 | 0.12286
74 | 0.27772 | 0.13451
75 | 0.16289 | 0.078892
76 | 0.089325 | 0.043262
77 | 0.65225 | 0.3159
78 | 1.8813 | 0.91115
79 | 0.29806 | 0.14435
80 | 0.24875 | 0.12048
81 | 0.33031 | 0.15998
82 | 0.15066 | 0.072968

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1