## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_625_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_625_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_625_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_625_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_625_0_node_5 | 20 | n |  | TRUE
5 | bus_MV_625_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_625_0_node_95 | 20 | n |  | TRUE
7 | bus_MV_625_0_node_96 | 20 | n |  | TRUE
8 | bus_MV_625_0_node_150 | 20 | n |  | TRUE
9 | bus_MV_625_0_node_10 | 20 | n |  | TRUE
10 | bus_MV_625_0_node_93 | 20 | n |  | TRUE
11 | bus_MV_625_0_node_152 | 20 | n |  | TRUE
12 | bus_MV_625_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_625_0_node_166 | 20 | n |  | TRUE
14 | bus_MV_625_0_node_56 | 20 | n |  | TRUE
15 | bus_MV_625_0_node_7 | 20 | n |  | TRUE
16 | bus_MV_625_0_node_55 | 20 | n |  | TRUE
17 | bus_MV_625_0_node_14 | 20 | n |  | TRUE
18 | bus_MV_625_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_625_0_node_171 | 20 | n |  | TRUE
20 | bus_MV_625_0_node_12 | 20 | n |  | TRUE
21 | bus_MV_625_0_node_9 | 20 | n |  | TRUE
22 | bus_MV_625_0_node_161 | 20 | n |  | TRUE
23 | bus_MV_625_0_node_11 | 20 | n |  | TRUE
24 | bus_MV_625_0_node_198 | 20 | n |  | TRUE
25 | bus_MV_625_0_node_13 | 20 | n |  | TRUE
26 | bus_MV_625_0_node_94 | 20 | n |  | TRUE
27 | bus_MV_625_0_node_180 | 20 | n |  | TRUE
28 | bus_MV_625_0_node_165 | 20 | n |  | TRUE
29 | bus_MV_625_0_node_186 | 20 | n |  | TRUE
30 | bus_MV_625_0_node_54 | 20 | n |  | TRUE
31 | bus_MV_625_0_node_167 | 20 | n |  | TRUE
32 | bus_MV_625_0_node_52 | 20 | n |  | TRUE
33 | bus_MV_625_0_node_49 | 20 | n |  | TRUE
34 | bus_MV_625_0_node_51 | 20 | n |  | TRUE
35 | bus_MV_625_0_node_101 | 20 | n |  | TRUE
36 | bus_MV_625_0_node_181 | 20 | n |  | TRUE
37 | bus_MV_625_0_node_17 | 20 | n |  | TRUE
38 | bus_MV_625_0_node_35 | 20 | n |  | TRUE
39 | bus_MV_625_0_node_16 | 20 | n |  | TRUE
40 | bus_MV_625_0_node_163 | 20 | n |  | TRUE
41 | bus_MV_625_0_node_15 | 20 | n |  | TRUE
42 | bus_MV_625_0_node_158 | 20 | n |  | TRUE
43 | bus_MV_625_0_node_28 | 20 | n |  | TRUE
44 | bus_MV_625_0_node_126 | 20 | n |  | TRUE
45 | bus_MV_625_0_node_127 | 20 | n |  | TRUE
46 | bus_MV_625_0_node_62 | 20 | n |  | TRUE
47 | bus_MV_625_0_node_105 | 20 | n |  | TRUE
48 | bus_MV_625_0_node_104 | 20 | n |  | TRUE
49 | bus_MV_625_0_node_106 | 20 | n |  | TRUE
50 | bus_MV_625_0_node_136 | 20 | n |  | TRUE
51 | bus_MV_625_0_node_137 | 20 | n |  | TRUE
52 | bus_MV_625_0_node_138 | 20 | n |  | TRUE
53 | bus_MV_625_0_node_139 | 20 | n |  | TRUE
54 | bus_MV_625_0_node_140 | 20 | n |  | TRUE
55 | bus_MV_625_0_node_141 | 20 | n |  | TRUE
56 | bus_MV_625_0_node_184 | 20 | n |  | TRUE
57 | bus_MV_625_0_node_19 | 20 | n |  | TRUE
58 | bus_MV_625_0_node_20 | 20 | n |  | TRUE
59 | bus_MV_625_0_node_23 | 20 | n |  | TRUE
60 | bus_MV_625_0_node_24 | 20 | n |  | TRUE
61 | bus_MV_625_0_node_21 | 20 | n |  | TRUE
62 | bus_MV_625_0_node_120 | 20 | n |  | TRUE
63 | bus_MV_625_0_node_119 | 20 | n |  | TRUE
64 | bus_MV_625_0_node_22 | 20 | n |  | TRUE
65 | bus_MV_625_0_node_170 | 20 | n |  | TRUE
66 | bus_MV_625_0_node_103 | 20 | n |  | TRUE
67 | bus_MV_625_0_node_169 | 20 | n |  | TRUE
68 | bus_MV_625_0_node_25 | 20 | n |  | TRUE
69 | bus_MV_625_0_node_151 | 20 | n |  | TRUE
70 | bus_MV_625_0_node_118 | 20 | n |  | TRUE
71 | bus_MV_625_0_node_102 | 20 | n |  | TRUE
72 | bus_MV_625_0_node_26 | 20 | n |  | TRUE
73 | bus_MV_625_0_node_27 | 20 | n |  | TRUE
74 | bus_MV_625_0_node_113 | 20 | n |  | TRUE
75 | bus_MV_625_0_node_193 | 20 | n |  | TRUE
76 | bus_MV_625_0_node_60 | 20 | n |  | TRUE
77 | bus_MV_625_0_node_112 | 20 | n |  | TRUE
78 | bus_MV_625_0_node_159 | 20 | n |  | TRUE
79 | bus_MV_625_0_node_63 | 20 | n |  | TRUE
80 | bus_MV_625_0_node_176 | 20 | n |  | TRUE
81 | bus_MV_625_0_node_196 | 20 | n |  | TRUE
82 | bus_MV_625_0_node_183 | 20 | n |  | TRUE
83 | bus_MV_625_0_node_59 | 20 | n |  | TRUE
84 | bus_MV_625_0_node_29 | 20 | n |  | TRUE
85 | bus_MV_625_0_node_31 | 20 | n |  | TRUE
86 | bus_MV_625_0_node_142 | 20 | n |  | TRUE
87 | bus_MV_625_0_node_172 | 20 | n |  | TRUE
88 | bus_MV_625_0_node_32 | 20 | n |  | TRUE
89 | bus_MV_625_0_node_30 | 20 | n |  | TRUE
90 | bus_MV_625_0_node_57 | 20 | n |  | TRUE
91 | bus_MV_625_0_node_109 | 20 | n |  | TRUE
92 | bus_MV_625_0_node_143 | 20 | n |  | TRUE
93 | bus_MV_625_0_node_33 | 20 | n |  | TRUE
94 | bus_MV_625_0_node_107 | 20 | n |  | TRUE
95 | bus_MV_625_0_node_144 | 20 | n |  | TRUE
96 | bus_MV_625_0_node_145 | 20 | n |  | TRUE
97 | bus_MV_625_0_node_148 | 20 | n |  | TRUE
98 | bus_MV_625_0_node_34 | 20 | n |  | TRUE
99 | bus_MV_625_0_node_115 | 20 | n |  | TRUE
100 | bus_MV_625_0_node_36 | 20 | n |  | TRUE
101 | bus_MV_625_0_node_38 | 20 | n |  | TRUE
102 | bus_MV_625_0_node_40 | 20 | n |  | TRUE
103 | bus_MV_625_0_node_37 | 20 | n |  | TRUE
104 | bus_MV_625_0_node_65 | 20 | n |  | TRUE
105 | bus_MV_625_0_node_64 | 20 | n |  | TRUE
106 | bus_MV_625_0_node_123 | 20 | n |  | TRUE
107 | bus_MV_625_0_node_46 | 20 | n |  | TRUE
108 | bus_MV_625_0_node_153 | 20 | n |  | TRUE
109 | bus_MV_625_0_node_69 | 20 | n |  | TRUE
110 | bus_MV_625_0_node_117 | 20 | n |  | TRUE
111 | bus_MV_625_0_node_67 | 20 | n |  | TRUE
112 | bus_MV_625_0_node_121 | 20 | n |  | TRUE
113 | bus_MV_625_0_node_122 | 20 | n |  | TRUE
114 | bus_MV_625_0_node_116 | 20 | n |  | TRUE
115 | bus_MV_625_0_node_41 | 20 | n |  | TRUE
116 | bus_MV_625_0_node_42 | 20 | n |  | TRUE
117 | bus_MV_625_0_node_43 | 20 | n |  | TRUE
118 | bus_MV_625_0_node_48 | 20 | n |  | TRUE
119 | bus_MV_625_0_node_44 | 20 | n |  | TRUE
120 | bus_MV_625_0_node_189 | 20 | n |  | TRUE
121 | bus_MV_625_0_node_173 | 20 | n |  | TRUE
122 | bus_MV_625_0_node_45 | 20 | n |  | TRUE
123 | bus_MV_625_0_node_195 | 20 | n |  | TRUE
124 | bus_MV_625_0_node_47 | 20 | n |  | TRUE
125 | bus_MV_625_0_node_50 | 20 | n |  | TRUE
126 | bus_MV_625_0_node_135 | 20 | n |  | TRUE
127 | bus_MV_625_0_node_114 | 20 | n |  | TRUE
128 | bus_MV_625_0_node_168 | 20 | n |  | TRUE
129 | bus_MV_625_0_node_191 | 20 | n |  | TRUE
130 | bus_MV_625_0_node_154 | 20 | n |  | TRUE
131 | bus_MV_625_0_node_157 | 20 | n |  | TRUE
132 | bus_MV_625_0_node_134 | 20 | n |  | TRUE
133 | bus_MV_625_0_node_90 | 20 | n |  | TRUE
134 | bus_MV_625_0_node_174 | 20 | n |  | TRUE
135 | bus_MV_625_0_node_194 | 20 | n |  | TRUE
136 | bus_MV_625_0_node_53 | 20 | n |  | TRUE
137 | bus_MV_625_0_node_58 | 20 | n |  | TRUE
138 | bus_MV_625_0_node_190 | 20 | n |  | TRUE
139 | bus_MV_625_0_node_100 | 20 | n |  | TRUE
140 | bus_MV_625_0_node_108 | 20 | n |  | TRUE
141 | bus_MV_625_0_node_147 | 20 | n |  | TRUE
142 | bus_MV_625_0_node_149 | 20 | n |  | TRUE
143 | bus_MV_625_0_node_177 | 20 | n |  | TRUE
144 | bus_MV_625_0_node_178 | 20 | n |  | TRUE
145 | bus_MV_625_0_node_179 | 20 | n |  | TRUE
146 | bus_MV_625_0_node_66 | 20 | n |  | TRUE
147 | bus_MV_625_0_node_70 | 20 | n |  | TRUE
148 | bus_MV_625_0_node_68 | 20 | n |  | TRUE
149 | bus_MV_625_0_node_124 | 20 | n |  | TRUE
150 | bus_MV_625_0_node_125 | 20 | n |  | TRUE
151 | bus_MV_625_0_node_71 | 20 | n |  | TRUE
152 | bus_MV_625_0_node_72 | 20 | n |  | TRUE
153 | bus_MV_625_0_node_75 | 20 | n |  | TRUE
154 | bus_MV_625_0_node_73 | 20 | n |  | TRUE
155 | bus_MV_625_0_node_160 | 20 | n |  | TRUE
156 | bus_MV_625_0_node_74 | 20 | n |  | TRUE
157 | bus_MV_625_0_node_78 | 20 | n |  | TRUE
158 | bus_MV_625_0_node_82 | 20 | n |  | TRUE
159 | bus_MV_625_0_node_128 | 20 | n |  | TRUE
160 | bus_MV_625_0_node_76 | 20 | n |  | TRUE
161 | bus_MV_625_0_node_111 | 20 | n |  | TRUE
162 | bus_MV_625_0_node_192 | 20 | n |  | TRUE
163 | bus_MV_625_0_node_77 | 20 | n |  | TRUE
164 | bus_MV_625_0_node_79 | 20 | n |  | TRUE
165 | bus_MV_625_0_node_131 | 20 | n |  | TRUE
166 | bus_MV_625_0_node_81 | 20 | n |  | TRUE
167 | bus_MV_625_0_node_83 | 20 | n |  | TRUE
168 | bus_MV_625_0_node_80 | 20 | n |  | TRUE
169 | bus_MV_625_0_node_129 | 20 | n |  | TRUE
170 | bus_MV_625_0_node_187 | 20 | n |  | TRUE
171 | bus_MV_625_0_node_132 | 20 | n |  | TRUE
172 | bus_MV_625_0_node_130 | 20 | n |  | TRUE
173 | bus_MV_625_0_node_84 | 20 | n |  | TRUE
174 | bus_MV_625_0_node_85 | 20 | n |  | TRUE
175 | bus_MV_625_0_node_86 | 20 | n |  | TRUE
176 | bus_MV_625_0_node_188 | 20 | n |  | TRUE
177 | bus_MV_625_0_node_88 | 20 | n |  | TRUE
178 | bus_MV_625_0_node_89 | 20 | n |  | TRUE
179 | bus_MV_625_0_node_91 | 20 | n |  | TRUE
180 | bus_MV_625_0_node_156 | 20 | n |  | TRUE
181 | bus_MV_625_0_node_92 | 20 | n |  | TRUE
182 | bus_MV_625_0_node_97 | 20 | n |  | TRUE
183 | bus_MV_625_0_node_98 | 20 | n |  | TRUE
184 | bus_MV_625_0_node_99 | 20 | n |  | TRUE
185 | bus_MV_625_0_node_185 | 20 | n |  | TRUE
186 | bus_MV_625_0_node_197 | 20 | n |  | TRUE
187 | bus_MV_625_0_node_182 | 20 | n |  | TRUE
188 | bus_MV_625_0_node_110 | 20 | n |  | TRUE
189 | bus_MV_625_0_node_162 | 20 | n |  | TRUE
190 | bus_MV_625_0_node_164 | 20 | n |  | TRUE
191 | bus_MV_625_0_node_175 | 20 | n |  | TRUE
192 | bus_HV_625_0_node_41 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_625_0_load_0 | 0 | 0.31021 | 0.15024 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_625_0_load_95 | 6 | 0.068118 | 0.032991 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_625_0_load_96 | 7 | 0.37386 | 0.18107 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_625_0_load_150 | 8 | 0.21722 | 0.1052 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_625_0_load_93 | 10 | 0.24722 | 0.11974 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_625_0_load_152 | 11 | 0.27779 | 0.13454 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_625_0_load_166 | 13 | 0.36116 | 0.17492 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_625_0_load_14 | 17 | 0.39398 | 0.19081 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_625_0_load_171 | 19 | 0.21717 | 0.10518 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_625_0_load_161 | 22 | 0.33875 | 0.16406 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_625_0_load_198 | 24 | 0.41075 | 0.19894 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_625_0_load_94 | 26 | 0.11486 | 0.05563 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_625_0_load_180 | 27 | 0.26716 | 0.12939 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_625_0_load_165 | 28 | 0.36853 | 0.17849 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_625_0_load_186 | 29 | 0.40101 | 0.19422 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_625_0_load_167 | 31 | 0.4044 | 0.19586 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_625_0_load_51 | 34 | 0.38069 | 0.18438 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_625_0_load_101 | 35 | 0.11538 | 0.055879 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_625_0_load_16 | 39 | 0.31337 | 0.15177 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_625_0_load_15 | 41 | 0.22748 | 0.11018 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_625_0_load_158 | 42 | 0.40916 | 0.19816 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_625_0_load_126 | 44 | 0.1418 | 0.068675 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_625_0_load_127 | 45 | 0.16761 | 0.081177 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_625_0_load_104 | 48 | 0.26228 | 0.12703 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_625_0_load_106 | 49 | 0.10723 | 0.051935 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_625_0_load_136 | 50 | 0.074973 | 0.036311 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_625_0_load_139 | 53 | 0.11527 | 0.055826 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_625_0_load_184 | 56 | 0.12107 | 0.058637 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_625_0_load_19 | 57 | 0.20757 | 0.10053 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_625_0_load_119 | 63 | 0.1881 | 0.091101 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_625_0_load_170 | 65 | 0.16822 | 0.081473 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_625_0_load_169 | 67 | 0.31282 | 0.1515 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_625_0_load_25 | 68 | 0.33383 | 0.16168 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_625_0_load_151 | 69 | 0.11063 | 0.053583 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_625_0_load_102 | 71 | 0.11814 | 0.057218 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_625_0_load_26 | 72 | 0.32222 | 0.15606 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_625_0_load_193 | 75 | 0.23354 | 0.11311 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_625_0_load_176 | 80 | 0.3802 | 0.18414 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_625_0_load_196 | 81 | 0.29681 | 0.14375 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_625_0_load_183 | 82 | 0.24566 | 0.11898 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_625_0_load_59 | 83 | 0.37279 | 0.18055 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_625_0_load_29 | 84 | 0.38812 | 0.18797 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_625_0_load_142 | 86 | 0.091409 | 0.044272 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_625_0_load_172 | 87 | 0.22139 | 0.10722 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_625_0_load_109 | 91 | 0.079972 | 0.038732 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_625_0_load_143 | 92 | 0.076024 | 0.03682 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_625_0_load_107 | 94 | 0.10394 | 0.05034 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_625_0_load_145 | 96 | 0.097628 | 0.047284 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_625_0_load_148 | 97 | 0.078333 | 0.037938 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_625_0_load_115 | 99 | 0.069255 | 0.033542 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_625_0_load_40 | 102 | 0.21599 | 0.10461 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_625_0_load_64 | 105 | 0.2054 | 0.099478 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_625_0_load_123 | 106 | 0.077355 | 0.037465 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_625_0_load_153 | 108 | 0.37284 | 0.18057 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_625_0_load_121 | 112 | 0.16514 | 0.079982 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_625_0_load_122 | 113 | 0.32183 | 0.15587 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_625_0_load_116 | 114 | 0.17146 | 0.083041 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_625_0_load_41 | 115 | 0.30169 | 0.14611 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_625_0_load_189 | 120 | 0.36631 | 0.17741 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_625_0_load_173 | 121 | 0.37868 | 0.1834 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_625_0_load_195 | 123 | 0.57333 | 0.27768 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_625_0_load_135 | 126 | 0.092756 | 0.044924 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_625_0_load_114 | 127 | 0.104 | 0.050368 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_625_0_load_191 | 129 | 0.29142 | 0.14114 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_625_0_load_157 | 131 | 0.23227 | 0.11249 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_625_0_load_194 | 135 | 0.32152 | 0.15572 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_625_0_load_190 | 138 | 0.078953 | 0.038239 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_625_0_load_108 | 140 | 0.084463 | 0.040907 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_625_0_load_149 | 142 | 0.11632 | 0.056334 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_625_0_load_177 | 143 | 0.33418 | 0.16185 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_625_0_load_66 | 146 | 0.21089 | 0.10214 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_625_0_load_124 | 149 | 0.141 | 0.06829 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_625_0_load_125 | 150 | 0.084866 | 0.041102 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_625_0_load_71 | 151 | 0.24739 | 0.11982 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_625_0_load_160 | 155 | 0.40576 | 0.19652 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_625_0_load_128 | 159 | 0.073735 | 0.035711 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_625_0_load_111 | 161 | 0.068063 | 0.032964 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_625_0_load_192 | 162 | 0.25737 | 0.12465 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_625_0_load_131 | 165 | 0.1047 | 0.050709 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_625_0_load_83 | 167 | 0.34597 | 0.16756 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_625_0_load_129 | 169 | 0.089834 | 0.043509 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_625_0_load_187 | 170 | 0.2606 | 0.12622 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_625_0_load_132 | 171 | 0.45937 | 0.22248 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_625_0_load_130 | 172 | 0.083448 | 0.040416 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_625_0_load_84 | 173 | 0.3882 | 0.18801 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_625_0_load_188 | 176 | 0.25139 | 0.12175 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_625_0_load_88 | 177 | 0.28972 | 0.14032 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_625_0_load_156 | 180 | 0.30102 | 0.14579 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_625_0_load_92 | 181 | 0.21543 | 0.10434 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_625_0_load_97 | 182 | 0.15387 | 0.074524 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_625_0_load_185 | 185 | 0.32437 | 0.1571 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_625_0_load_197 | 186 | 0.14278 | 0.069151 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_625_0_load_110 | 188 | 0.073869 | 0.035776 | 0 | 0 |  | 1 | TRUE | wye
93 | MV_625_0_load_164 | 190 | 0.34644 | 0.16779 | 0 | 0 |  | 1 | TRUE | wye
94 | MV_625_0_load_175 | 191 | 0.40895 | 0.19806 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 115 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_625_0_line_0 |  | 0 | 1 | 0.038663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_625_0_line_1 |  | 0 | 2 | 0.078382 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
2 | MV_625_0_line_2 |  | 1 | 3 | 0.34365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_625_0_line_3 |  | 1 | 4 | 0.5625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_625_0_line_4 |  | 2 | 5 | 0.097363 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
5 | MV_625_0_line_5 |  | 3 | 9 | 0.1949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_625_0_line_6 |  | 3 | 10 | 0.056461 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_625_0_line_7 |  | 4 | 11 | 0.023537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_625_0_line_8 |  | 5 | 6 | 0.020279 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
9 | MV_625_0_line_9 |  | 6 | 7 | 0.019468 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_625_0_line_10 |  | 6 | 8 | 0.15941 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
11 | MV_625_0_line_11 |  | 8 | 54 | 0.09011 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
12 | MV_625_0_line_12 |  | 9 | 24 | 0.031347 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_625_0_line_13 |  | 9 | 21 | 0.29521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_625_0_line_14 |  | 12 | 13 | 0.055391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_625_0_line_15 |  | 12 | 14 | 0.63675 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_625_0_line_16 |  | 12 | 15 | 0.52222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_625_0_line_17 |  | 12 | 16 | 0.41389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_625_0_line_18 |  | 14 | 29 | 0.016811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_625_0_line_19 |  | 15 | 17 | 0.037072 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_625_0_line_20 |  | 16 | 35 | 0.032789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_625_0_line_21 |  | 16 | 30 | 0.27145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_625_0_line_22 |  | 18 | 19 | 0.02282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_625_0_line_23 |  | 18 | 20 | 0.25592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_625_0_line_24 |  | 19 | 36 | 0.039705 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_625_0_line_25 |  | 20 | 27 | 0.01011 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_625_0_line_26 |  | 20 | 21 | 0.32435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_625_0_line_27 |  | 21 | 22 | 0.017937 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_625_0_line_28 |  | 21 | 23 | 0.41091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_625_0_line_29 |  | 23 | 25 | 0.2668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_625_0_line_30 |  | 23 | 26 | 0.0578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_625_0_line_31 |  | 25 | 28 | 0.063898 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_625_0_line_32 |  | 28 | 40 | 0.026515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_625_0_line_33 |  | 30 | 31 | 0.030763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_625_0_line_34 |  | 30 | 32 | 0.16306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_625_0_line_35 |  | 30 | 33 | 0.42821 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_625_0_line_36 |  | 32 | 34 | 0.006978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_625_0_line_37 |  | 33 | 128 | 0.19844 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_625_0_line_38 |  | 33 | 129 | 0.002028 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_625_0_line_39 |  | 33 | 118 | 0.20423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_625_0_line_40 |  | 34 | 136 | 0.016157 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_625_0_line_41 |  | 35 | 139 | 0.046544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_625_0_line_42 |  | 36 | 187 | 0.19672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_625_0_line_43 |  | 37 | 38 | 0.30188 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_625_0_line_44 |  | 37 | 39 | 0.044883 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_625_0_line_45 |  | 38 | 47 | 0.007962 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_625_0_line_46 |  | 38 | 48 | 0.058481 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
47 | MV_625_0_line_47 |  | 40 | 189 | 0.61217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_625_0_line_48 |  | 41 | 42 | 0.2284 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_625_0_line_49 |  | 42 | 43 | 0.050298 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_625_0_line_50 |  | 43 | 78 | 0.36873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_625_0_line_51 |  | 43 | 73 | 0.16266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_625_0_line_52 |  | 44 | 45 | 0.0055253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_625_0_line_53 |  | 44 | 46 | 0.23392 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_625_0_line_54 |  | 45 | 157 | 0.01745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_625_0_line_55 |  | 46 | 79 | 0.4245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_625_0_line_56 |  | 46 | 80 | 0.025926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_625_0_line_57 |  | 47 | 49 | 0.052576 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
58 | MV_625_0_line_58 |  | 48 | 56 | 0.28459 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
59 | MV_625_0_line_59 |  | 49 | 94 | 0.031019 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
60 | MV_625_0_line_60 |  | 50 | 51 | 0.056062 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_625_0_line_61 |  | 50 | 52 | 0.057563 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_625_0_line_62 |  | 51 | 53 | 0.038826 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_625_0_line_63 |  | 51 | 54 | 0.084017 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
64 | MV_625_0_line_64 |  | 52 | 55 | 0.04078 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
65 | MV_625_0_line_65 |  | 55 | 56 | 0.042227 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
66 | MV_625_0_line_66 |  | 57 | 58 | 0.017963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_625_0_line_67 |  | 58 | 59 | 0.35015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_625_0_line_68 |  | 58 | 60 | 0.19963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_625_0_line_69 |  | 59 | 67 | 0.047703 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_625_0_line_70 |  | 59 | 64 | 0.19328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_625_0_line_71 |  | 60 | 68 | 0.021433 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_625_0_line_72 |  | 61 | 62 | 1.3214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_625_0_line_73 |  | 61 | 63 | 0.08137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_625_0_line_74 |  | 62 | 69 | 0.049696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_625_0_line_75 |  | 63 | 70 | 0.04234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_625_0_line_76 |  | 64 | 65 | 0.045269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_625_0_line_77 |  | 64 | 66 | 0.042753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_625_0_line_78 |  | 66 | 71 | 0.034322 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_625_0_line_79 |  | 69 | 181 | 0.45742 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_625_0_line_80 |  | 70 | 114 | 0.057803 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_625_0_line_81 |  | 71 | 186 | 0.1835 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_625_0_line_82 |  | 72 | 73 | 0.01941 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_625_0_line_83 |  | 73 | 74 | 0.33809 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_625_0_line_84 |  | 74 | 75 | 0.022446 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_625_0_line_85 |  | 74 | 76 | 0.11091 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_625_0_line_86 |  | 74 | 77 | 0.022422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_625_0_line_87 |  | 76 | 83 | 0.042473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_625_0_line_88 |  | 77 | 161 | 0.039091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_625_0_line_89 |  | 78 | 81 | 0.081286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_625_0_line_90 |  | 79 | 82 | 0.04913 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_625_0_line_91 |  | 82 | 145 | 0.039117 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_625_0_line_92 |  | 84 | 85 | 0.046855 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_625_0_line_93 |  | 84 | 86 | 0.061639 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
94 | MV_625_0_line_94 |  | 85 | 87 | 0.30098 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
95 | MV_625_0_line_95 |  | 86 | 88 | 0.017226 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
96 | MV_625_0_line_96 |  | 87 | 107 | 0.026649 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
97 | MV_625_0_line_97 |  | 87 | 98 | 0.086002 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_625_0_line_98 |  | 87 | 100 | 0.2684 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_625_0_line_99 |  | 88 | 89 | 0.040573 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_625_0_line_100 |  | 89 | 93 | 0.048793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_625_0_line_101 |  | 89 | 94 | 0.053558 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
102 | MV_625_0_line_102 |  | 90 | 91 | 0.036055 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_625_0_line_103 |  | 90 | 92 | 0.13649 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
104 | MV_625_0_line_104 |  | 91 | 140 | 0.0694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_625_0_line_105 |  | 92 | 95 | 0.022181 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_625_0_line_106 |  | 93 | 95 | 0.052521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_625_0_line_107 |  | 93 | 96 | 0.015364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_625_0_line_108 |  | 94 | 97 | 0.059473 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_625_0_line_109 |  | 97 | 141 | 0.017491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_625_0_line_110 |  | 98 | 99 | 0.043221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_625_0_line_111 |  | 100 | 101 | 0.32672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_625_0_line_112 |  | 100 | 102 | 0.050265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_625_0_line_113 |  | 101 | 106 | 0.041602 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_625_0_line_114 |  | 103 | 104 | 0.14331 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
115 | MV_625_0_line_115 |  | 103 | 105 | 0.086908 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
116 | MV_625_0_line_116 |  | 104 | 108 | 0.009265 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
117 | MV_625_0_line_117 |  | 105 | 107 | 0.096287 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
118 | MV_625_0_line_118 |  | 106 | 109 | 0.089805 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_625_0_line_119 |  | 108 | 130 | 0.007556 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
120 | MV_625_0_line_120 |  | 109 | 110 | 0.017223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_625_0_line_121 |  | 109 | 111 | 0.21581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_625_0_line_122 |  | 110 | 113 | 0.048997 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_625_0_line_123 |  | 110 | 114 | 0.038785 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_625_0_line_124 |  | 111 | 147 | 0.23405 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_625_0_line_125 |  | 111 | 146 | 0.04542 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
126 | MV_625_0_line_126 |  | 112 | 113 | 0.023043 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
127 | MV_625_0_line_127 |  | 115 | 116 | 0.026771 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
128 | MV_625_0_line_128 |  | 116 | 117 | 0.47938 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
129 | MV_625_0_line_129 |  | 116 | 118 | 0.16805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_625_0_line_130 |  | 117 | 119 | 0.51768 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
131 | MV_625_0_line_131 |  | 117 | 120 | 0.033287 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
132 | MV_625_0_line_132 |  | 118 | 127 | 0.042402 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_625_0_line_133 |  | 119 | 121 | 0.002225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_625_0_line_134 |  | 119 | 122 | 0.50986 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
135 | MV_625_0_line_135 |  | 120 | 132 | 0.005384 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
136 | MV_625_0_line_136 |  | 122 | 123 | 0.011829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_625_0_line_137 |  | 122 | 124 | 0.26809 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
138 | MV_625_0_line_138 |  | 124 | 125 | 0.30087 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
139 | MV_625_0_line_139 |  | 124 | 126 | 0.006893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_625_0_line_140 |  | 125 | 130 | 0.096962 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
141 | MV_625_0_line_141 |  | 125 | 131 | 0.030441 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_625_0_line_142 |  | 126 | 133 | 0.037255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_625_0_line_143 |  | 128 | 134 | 0.34704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_625_0_line_144 |  | 128 | 135 | 0.008069 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_625_0_line_145 |  | 132 | 176 | 0.19729 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
146 | MV_625_0_line_146 |  | 133 | 179 | 0.016836 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_625_0_line_147 |  | 134 | 191 | 0.03269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_625_0_line_148 |  | 136 | 137 | 0.25049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_625_0_line_149 |  | 137 | 138 | 0.026559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_625_0_line_150 |  | 139 | 183 | 0.17095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_625_0_line_151 |  | 140 | 188 | 0.070166 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_625_0_line_152 |  | 141 | 142 | 0.016352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_625_0_line_153 |  | 143 | 144 | 0.062281 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_625_0_line_154 |  | 144 | 145 | 0.4015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_625_0_line_155 |  | 147 | 150 | 0.01987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_625_0_line_156 |  | 147 | 148 | 0.20374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_625_0_line_157 |  | 148 | 149 | 0.031154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_625_0_line_158 |  | 151 | 152 | 0.005952 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_625_0_line_159 |  | 152 | 153 | 0.13769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_625_0_line_160 |  | 153 | 160 | 0.19785 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_625_0_line_161 |  | 153 | 161 | 0.038779 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_625_0_line_162 |  | 153 | 156 | 0.19152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_625_0_line_163 |  | 154 | 155 | 0.01423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_625_0_line_164 |  | 154 | 156 | 0.25119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_625_0_line_165 |  | 154 | 157 | 0.26007 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_625_0_line_166 |  | 156 | 158 | 0.21142 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
167 | MV_625_0_line_167 |  | 156 | 159 | 0.011236 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_625_0_line_168 |  | 157 | 163 | 0.40554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_625_0_line_169 |  | 158 | 172 | 0.028764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_625_0_line_170 |  | 158 | 168 | 0.2461 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
171 | MV_625_0_line_171 |  | 160 | 162 | 0.056486 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
172 | MV_625_0_line_172 |  | 163 | 164 | 0.16413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_625_0_line_173 |  | 163 | 165 | 0.015679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_625_0_line_174 |  | 164 | 166 | 0.14874 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_625_0_line_175 |  | 164 | 167 | 0.010373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_625_0_line_176 |  | 166 | 171 | 0.018092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_625_0_line_177 |  | 168 | 169 | 0.10642 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
178 | MV_625_0_line_178 |  | 168 | 170 | 0.10589 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
179 | MV_625_0_line_179 |  | 169 | 173 | 0.12614 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
180 | MV_625_0_line_180 |  | 173 | 174 | 0.009545 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
181 | MV_625_0_line_181 |  | 174 | 175 | 0.16099 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
182 | MV_625_0_line_182 |  | 175 | 176 | 0.016635 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
183 | MV_625_0_line_183 |  | 177 | 178 | 0.006254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
184 | MV_625_0_line_184 |  | 178 | 179 | 0.11149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
185 | MV_625_0_line_185 |  | 179 | 180 | 0.016476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
186 | MV_625_0_line_186 |  | 182 | 183 | 0.056463 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
187 | MV_625_0_line_187 |  | 183 | 184 | 0.11106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
188 | MV_625_0_line_188 |  | 184 | 185 | 0.04482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
189 | MV_625_0_line_189 |  | 186 | 187 | 0.032044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
190 | MV_625_0_line_190 |  | 189 | 190 | 0.092662 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_625_0_trafo_41 | 25 MVA 110/20 kV | 192 | 115 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2540481.2362 | 1154901.551
1 | 2540507.5751 | 1154929.9166
2 | 2540431.3817 | 1154841.0679
3 | 2540375.0874 | 1154950.3073
4 | 2540732.2051 | 1155106.8813
5 | 2540477.5387 | 1154783.8798
6 | 2540468.4161 | 1154765.7689
7 | 2540485.8026 | 1154757.0112
8 | 2540395.7879 | 1154623.8622
9 | 2540318.9317 | 1155077.1443
10 | 2540336.2509 | 1154909.3536
11 | 2540755.7923 | 1155107.6713
12 | 2540786.0772 | 1154341.3601
13 | 2540743.6765 | 1154377.1417
14 | 2540699.9575 | 1154505.4643
15 | 2541040.2748 | 1154700.0762
16 | 2540665.1321 | 1154070.029
17 | 2541057.5651 | 1154732.8687
18 | 2539842.7236 | 1155150.0653
19 | 2539837.3632 | 1155167.0392
20 | 2540010.9348 | 1155071.2856
21 | 2540148.9934 | 1154996.8244
22 | 2540165.3546 | 1154992.1478
23 | 2539936.9787 | 1155239.7153
24 | 2540326.169 | 1155107.6444
25 | 2540081.0999 | 1155294.4172
26 | 2539882.1976 | 1155250.5979
27 | 2540003.6922 | 1155064.2319
28 | 2540143.5311 | 1155283.0667
29 | 2540706.9159 | 1154520.2814
30 | 2540525.3085 | 1154065.8866
31 | 2540504.3782 | 1154043.2927
32 | 2540462.995 | 1154172.5054
33 | 2540227.4116 | 1153969.9567
34 | 2540456.328 | 1154171.7044
35 | 2540697.3234 | 1154063.7992
36 | 2539809.6429 | 1155195.4655
37 | 2539744.6501 | 1154910.2182
38 | 2539812.0819 | 1154615.9613
39 | 2539699.8668 | 1154913.2024
40 | 2540152.2714 | 1155307.3038
41 | 2540115.3363 | 1152538.7342
42 | 2539956.3062 | 1152702.6755
43 | 2539909.2707 | 1152720.7441
44 | 2539834.6033 | 1153145.2183
45 | 2539833.0215 | 1153150.5079
46 | 2540032.969 | 1153021.2375
47 | 2539809.2932 | 1154608.6631
48 | 2539864.8625 | 1154590.7784
49 | 2539838.314 | 1154568.7575
50 | 2540230.8699 | 1154648.4921
51 | 2540274.9594 | 1154613.8646
52 | 2540184.3774 | 1154682.4247
53 | 2540304.539 | 1154623.0534
54 | 2540336.6837 | 1154556.8652
55 | 2540168.6007 | 1154681.1699
56 | 2540143.6014 | 1154648.1788
57 | 2539152.131 | 1155178.5669
58 | 2539167.5636 | 1155182.3016
59 | 2539350.1061 | 1155048.4952
60 | 2539107.4448 | 1155074.3965
61 | 2539246.0984 | 1154863.4012
62 | 2538851.3093 | 1155300.0752
63 | 2539221.8613 | 1154810.6244
64 | 2539454.8046 | 1155126.9708
65 | 2539428.3692 | 1155090.2173
66 | 2539493.2583 | 1155110.3078
67 | 2539350.752 | 1155000.7962
68 | 2539110.1518 | 1155053.1353
69 | 2538887.8012 | 1155333.5952
70 | 2539237.0123 | 1154771.2876
71 | 2539518.6073 | 1155112.9972
72 | 2539773.788 | 1152746.3692
73 | 2539788.4043 | 1152759.1852
74 | 2539588.0215 | 1153031.4981
75 | 2539591.6662 | 1153009.3495
76 | 2539686.1347 | 1152979.785
77 | 2539571.4384 | 1153046.6396
78 | 2539735.3436 | 1152516.8862
79 | 2540228.3295 | 1152897.7142
80 | 2540049.7776 | 1153040.8805
81 | 2539685.1898 | 1152556.177
82 | 2540276.8978 | 1152890.3053
83 | 2539720.8984 | 1152968.7106
84 | 2539772.1867 | 1154509.1478
85 | 2539728.9503 | 1154526.6907
86 | 2539819.6934 | 1154469.8729
87 | 2539558.4517 | 1154278.6578
88 | 2539835.6211 | 1154463.9213
89 | 2539831.6545 | 1154494.5109
90 | 2539986.2496 | 1154318.0032
91 | 2540021.756 | 1154324.2644
92 | 2539895.6613 | 1154420.1016
93 | 2539874.5075 | 1154475.405
94 | 2539853.043 | 1154543.6122
95 | 2539873.6833 | 1154422.9516
96 | 2539889.7144 | 1154473.3184
97 | 2539909.28 | 1154524.262
98 | 2539540.887 | 1154362.8466
99 | 2539563.6327 | 1154399.5981
100 | 2539550.4112 | 1154546.9392
101 | 2539381.6486 | 1154636.5764
102 | 2539588.2993 | 1154560.2918
103 | 2539409.7859 | 1154241.7792
104 | 2539338.3324 | 1154145.4034
105 | 2539464.2779 | 1154309.0659
106 | 2539369.8913 | 1154663.7335
107 | 2539544.5828 | 1154255.9405
108 | 2539346.5592 | 1154141.0958
109 | 2539280.1634 | 1154667.462
110 | 2539272.5983 | 1154682.5021
111 | 2539224.8414 | 1154481.9653
112 | 2539336.5868 | 1154715.4795
113 | 2539315.5421 | 1154706.0922
114 | 2539257.5954 | 1154718.1677
115 | 2539965.0207 | 1154124.4107
116 | 2539970.6906 | 1154098.3512
117 | 2539839.0361 | 1153789.1673
118 | 2540092.8955 | 1154026.7155
119 | 2539597.2422 | 1154076.7143
120 | 2539830.0381 | 1153757.1512
121 | 2539595.4944 | 1154075.3311
122 | 2539446.8183 | 1153904.7016
123 | 2539438.5011 | 1153896.2697
124 | 2539314.2706 | 1153876.2785
125 | 2539301.5694 | 1154046.7545
126 | 2539310.8051 | 1153870.3201
127 | 2540123.054 | 1154044.6839
128 | 2540270.2882 | 1153874.0232
129 | 2540227.2936 | 1153971.9812
130 | 2539343.2683 | 1154134.292
131 | 2539272.4995 | 1154055.7864
132 | 2539828.2686 | 1153752.0662
133 | 2539306.2736 | 1153835.7707
134 | 2540206.6326 | 1153622.0092
135 | 2540266.901 | 1153866.6974
136 | 2540447.8722 | 1154185.4845
137 | 2540282.3365 | 1154183.0145
138 | 2540255.7052 | 1154183.535
139 | 2540734.5221 | 1154075.2139
140 | 2540090.0636 | 1154336.5249
141 | 2539925.2046 | 1154517.254
142 | 2539927.8342 | 1154533.0591
143 | 2540690.5834 | 1152871.1771
144 | 2540648.6981 | 1152824.9879
145 | 2540308.2763 | 1152913.6618
146 | 2539229.2785 | 1154436.7626
147 | 2539097.2321 | 1154637.5746
148 | 2539150.6438 | 1154528.9748
149 | 2539167.5613 | 1154546.8225
150 | 2539091.752 | 1154619.6925
151 | 2539635.0743 | 1153106.3658
152 | 2539638.4086 | 1153101.4297
153 | 2539588.6877 | 1153103.8527
154 | 2539742.0924 | 1153315.2493
155 | 2539737.5164 | 1153328.7246
156 | 2539621.8178 | 1153215.0576
157 | 2539828.3353 | 1153167.3167
158 | 2539673.9327 | 1153301.3699
159 | 2539619.8979 | 1153204.9715
160 | 2539554.9621 | 1153168.4932
161 | 2539568.4117 | 1153073.997
162 | 2539499.6979 | 1153156.8095
163 | 2539883.3163 | 1153465.9388
164 | 2539978.9265 | 1153456.7673
165 | 2539897.0698 | 1153459.4093
166 | 2539995.8433 | 1153546.4912
167 | 2539970.7966 | 1153463.2297
168 | 2539528.363 | 1153363.9997
169 | 2539492.6332 | 1153430.4334
170 | 2539455.1601 | 1153287.4841
171 | 2539986.6004 | 1153534.0859
172 | 2539671.5239 | 1153330.0333
173 | 2539604.3307 | 1153489.0479
174 | 2539612.5605 | 1153484.1737
175 | 2539686.7342 | 1153605.8613
176 | 2539681.113 | 1153620.659
177 | 2539368.7201 | 1153777.4312
178 | 2539362.5335 | 1153776.4041
179 | 2539297.1708 | 1153828.5921
180 | 2539280.9435 | 1153825.5099
181 | 2539218.7282 | 1155649.3813
182 | 2540878.0481 | 1154067.2331
183 | 2540850.8423 | 1154098.4472
184 | 2540954.6421 | 1154085.0971
185 | 2540944.025 | 1154042.2562
186 | 2539625.972 | 1155261.8105
187 | 2539654.4957 | 1155247.0494
188 | 2540156.7539 | 1154355.9791
189 | 2540364.4191 | 1155785.5194
190 | 2540440.8008 | 1155837.979
191 | 2540231.021 | 1153600.1659
192 | 2539965.0207 | 1154124.4107

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99172 | -0.17396 | 0.31021 | 0.15024
1 | 0.99152 | -0.17241 | 0 | 0
2 | 0.9921 | -0.16389 | 0 | 0
3 | 0.98994 | -0.15938 | 0 | 0
4 | 0.99132 | -0.17077 | 0 | 0
5 | 0.99232 | -0.16131 | 0 | 0
6 | 0.99234 | -0.16124 | 0.068118 | 0.032991
7 | 0.99233 | -0.16115 | 0.37386 | 0.18107
8 | 0.99259 | -0.14695 | 0.21722 | 0.1052
9 | 0.98911 | -0.15246 | 0 | 0
10 | 0.98992 | -0.15921 | 0.24722 | 0.11974
11 | 0.99132 | -0.17069 | 0.27779 | 0.13454
12 | 0.99554 | 0.034736 | 0 | 0
13 | 0.99551 | 0.034975 | 0.36116 | 0.17492
14 | 0.99521 | 0.037494 | 0 | 0
15 | 0.99528 | 0.037011 | 0 | 0
16 | 0.99614 | 0.029869 | 0 | 0
17 | 0.99525 | 0.036833 | 0.39398 | 0.19081
18 | 0.98677 | -0.13286 | 0 | 0
19 | 0.98672 | -0.13247 | 0.21717 | 0.10518
20 | 0.98726 | -0.13708 | 0 | 0
21 | 0.988 | -0.14334 | 0 | 0
22 | 0.98799 | -0.14327 | 0.33875 | 0.16406
23 | 0.98756 | -0.13993 | 0 | 0
24 | 0.98908 | -0.15262 | 0.41075 | 0.19894
25 | 0.98732 | -0.13794 | 0 | 0
26 | 0.98755 | -0.13986 | 0.11486 | 0.05563
27 | 0.98725 | -0.13711 | 0.26716 | 0.12939
28 | 0.98726 | -0.13744 | 0.36853 | 0.17849
29 | 0.9952 | 0.037575 | 0.40101 | 0.19422
30 | 0.99675 | 0.025072 | 0 | 0
31 | 0.99673 | 0.025221 | 0.4044 | 0.19586
32 | 0.99665 | 0.02588 | 0 | 0
33 | 0.99817 | 0.01362 | 0 | 0
34 | 0.99665 | 0.025915 | 0.38069 | 0.18438
35 | 0.99612 | 0.030081 | 0.11538 | 0.055879
36 | 0.98662 | -0.1332 | 0 | 0
37 | 0.99324 | -0.11792 | 0 | 0
38 | 0.99343 | -0.11675 | 0 | 0
39 | 0.99321 | -0.11809 | 0.31337 | 0.15177
40 | 0.98725 | -0.13735 | 0 | 0
41 | 0.99475 | -0.050412 | 0.22748 | 0.11018
42 | 0.99485 | -0.049775 | 0.40916 | 0.19816
43 | 0.9949 | -0.050159 | 0 | 0
44 | 0.99516 | -0.040148 | 0.1418 | 0.068675
45 | 0.99517 | -0.040214 | 0.16761 | 0.081177
46 | 0.99473 | -0.04333 | 0 | 0
47 | 0.99343 | -0.11672 | 0 | 0
48 | 0.99337 | -0.11701 | 0.26228 | 0.12703
49 | 0.99348 | -0.11647 | 0.10723 | 0.051935
50 | 0.99277 | -0.14606 | 0.074973 | 0.036311
51 | 0.99272 | -0.14628 | 0 | 0
52 | 0.99282 | -0.14582 | 0 | 0
53 | 0.99272 | -0.14623 | 0.11527 | 0.055826
54 | 0.99266 | -0.14661 | 0 | 0
55 | 0.99285 | -0.14565 | 0 | 0
56 | 0.99288 | -0.14548 | 0.12107 | 0.058637
57 | 0.98528 | -0.12799 | 0.20757 | 0.10053
58 | 0.98528 | -0.12804 | 0 | 0
59 | 0.98553 | -0.13017 | 0 | 0
60 | 0.9852 | -0.12725 | 0 | 0
61 | 0.99238 | -0.063475 | 0 | 0
62 | 0.99183 | -0.05971 | 0 | 0
63 | 0.99241 | -0.063619 | 0.1881 | 0.091101
64 | 0.98574 | -0.132 | 0 | 0
65 | 0.98573 | -0.13191 | 0.16822 | 0.081473
66 | 0.98579 | -0.13249 | 0 | 0
67 | 0.9855 | -0.13035 | 0.31282 | 0.1515
68 | 0.98518 | -0.12734 | 0.33383 | 0.16168
69 | 0.99181 | -0.059517 | 0.11063 | 0.053583
70 | 0.99244 | -0.063787 | 0 | 0
71 | 0.98584 | -0.13287 | 0.11814 | 0.057218
72 | 0.99508 | -0.051772 | 0.32222 | 0.15606
73 | 0.99509 | -0.051847 | 0 | 0
74 | 0.99591 | -0.046187 | 0 | 0
75 | 0.9959 | -0.04625 | 0.23354 | 0.11311
76 | 0.99583 | -0.046701 | 0 | 0
77 | 0.99596 | -0.046664 | 0 | 0
78 | 0.99476 | -0.048985 | 0 | 0
79 | 0.99442 | -0.040792 | 0 | 0
80 | 0.99472 | -0.043211 | 0.3802 | 0.18414
81 | 0.99473 | -0.048699 | 0.29681 | 0.14375
82 | 0.99436 | -0.041187 | 0.24566 | 0.11898
83 | 0.99581 | -0.046511 | 0.37279 | 0.18055
84 | 0.99382 | -0.10173 | 0.38812 | 0.18797
85 | 0.99387 | -0.10147 | 0 | 0
86 | 0.99368 | -0.10965 | 0.091409 | 0.044272
87 | 0.99458 | -0.060602 | 0.22139 | 0.10722
88 | 0.99366 | -0.10975 | 0 | 0
89 | 0.99362 | -0.10996 | 0 | 0
90 | 0.9935 | -0.10993 | 0 | 0
91 | 0.99349 | -0.10983 | 0.079972 | 0.038732
92 | 0.99357 | -0.10948 | 0.076024 | 0.03682
93 | 0.9936 | -0.10974 | 0 | 0
94 | 0.99351 | -0.11632 | 0.10394 | 0.05034
95 | 0.99357 | -0.10956 | 0 | 0
96 | 0.99359 | -0.10972 | 0.097628 | 0.047284
97 | 0.99349 | -0.11647 | 0.078333 | 0.037938
98 | 0.99457 | -0.060683 | 0 | 0
99 | 0.99457 | -0.060648 | 0.069255 | 0.033542
100 | 0.9936 | -0.068366 | 0 | 0
101 | 0.9929 | -0.062946 | 0 | 0
102 | 0.99359 | -0.068237 | 0.21599 | 0.10461
103 | 0.99505 | -0.042612 | 0 | 0
104 | 0.99527 | -0.041516 | 0 | 0
105 | 0.99492 | -0.043268 | 0.2054 | 0.099478
106 | 0.99281 | -0.062244 | 0.077355 | 0.037465
107 | 0.99462 | -0.060405 | 0 | 0
108 | 0.99529 | -0.041445 | 0.37284 | 0.18057
109 | 0.99254 | -0.064444 | 0 | 0
110 | 0.99251 | -0.064242 | 0 | 0
111 | 0.99242 | -0.063496 | 0 | 0
112 | 0.99246 | -0.064581 | 0.16514 | 0.079982
113 | 0.99246 | -0.064534 | 0.32183 | 0.15587
114 | 0.99248 | -0.064013 | 0.17146 | 0.083041
115 | 1 | 0 | -22.08 | -9.8774
116 | 0.9999 | -0.00050502 | 0 | 0
117 | 0.99849 | -0.0080313 | 0 | 0
118 | 0.99911 | 0.0059478 | 0 | 0
119 | 0.99751 | -0.013334 | 0 | 0
120 | 0.99845 | -0.0081981 | 0.36631 | 0.17741
121 | 0.99751 | -0.013324 | 0.37868 | 0.1834
122 | 0.99657 | -0.018211 | 0 | 0
123 | 0.99657 | -0.01813 | 0.57333 | 0.27768
124 | 0.99611 | -0.020592 | 0 | 0
125 | 0.99561 | -0.023056 | 0 | 0
126 | 0.9961 | -0.020537 | 0.092756 | 0.044924
127 | 0.9991 | 0.0059993 | 0.104 | 0.050368
128 | 0.99798 | 0.015214 | 0 | 0
129 | 0.99817 | 0.013627 | 0.29142 | 0.14114
130 | 0.9953 | -0.041384 | 0 | 0
131 | 0.9956 | -0.023142 | 0.23227 | 0.11249
132 | 0.99845 | -0.0082238 | 0 | 0
133 | 0.99607 | -0.020282 | 0 | 0
134 | 0.9978 | 0.01681 | 0 | 0
135 | 0.99798 | 0.015245 | 0.32152 | 0.15572
136 | 0.99665 | 0.025924 | 0 | 0
137 | 0.99662 | 0.026104 | 0 | 0
138 | 0.99662 | 0.026129 | 0.078953 | 0.038239
139 | 0.99609 | 0.030321 | 0 | 0
140 | 0.99348 | -0.10971 | 0.084463 | 0.040907
141 | 0.99349 | -0.11644 | 0 | 0
142 | 0.99348 | -0.11642 | 0.11632 | 0.056334
143 | 0.99414 | -0.039671 | 0.33418 | 0.16185
144 | 0.99417 | -0.03992 | 0 | 0
145 | 0.99434 | -0.041383 | 0 | 0
146 | 0.9924 | -0.063614 | 0.21089 | 0.10214
147 | 0.99235 | -0.062986 | 0 | 0
148 | 0.99231 | -0.062678 | 0 | 0
149 | 0.99231 | -0.062626 | 0.141 | 0.06829
150 | 0.99235 | -0.062966 | 0.084866 | 0.041102
151 | 0.99611 | -0.047936 | 0.24739 | 0.11982
152 | 0.99611 | -0.047954 | 0 | 0
153 | 0.99615 | -0.048349 | 0 | 0
154 | 0.99592 | -0.046572 | 0 | 0
155 | 0.99591 | -0.046502 | 0.40576 | 0.19652
156 | 0.99674 | -0.053594 | 0 | 0
157 | 0.9952 | -0.040456 | 0 | 0
158 | 0.99733 | -0.047081 | 0 | 0
159 | 0.99674 | -0.053584 | 0.073735 | 0.035711
160 | 0.99609 | -0.047766 | 0 | 0
161 | 0.99606 | -0.047495 | 0.068063 | 0.032964
162 | 0.99606 | -0.047943 | 0.25737 | 0.12465
163 | 0.99473 | -0.036341 | 0 | 0
164 | 0.99456 | -0.034808 | 0 | 0
165 | 0.99472 | -0.036322 | 0.1047 | 0.050709
166 | 0.99447 | -0.034002 | 0 | 0
167 | 0.99455 | -0.034764 | 0.34597 | 0.16756
168 | 0.99754 | -0.046135 | 0 | 0
169 | 0.99763 | -0.045692 | 0.089834 | 0.043509
170 | 0.99748 | -0.04647 | 0.2606 | 0.12622
171 | 0.99446 | -0.033902 | 0.45937 | 0.22248
172 | 0.99733 | -0.047053 | 0.083448 | 0.040416
173 | 0.99786 | -0.032349 | 0.3882 | 0.18801
174 | 0.99787 | -0.032306 | 0 | 0
175 | 0.99803 | -0.031572 | 0 | 0
176 | 0.99804 | -0.031494 | 0.25139 | 0.12175
177 | 0.99602 | -0.019764 | 0.28972 | 0.14032
178 | 0.99602 | -0.019786 | 0 | 0
179 | 0.99606 | -0.020165 | 0 | 0
180 | 0.99605 | -0.020106 | 0.30102 | 0.14579
181 | 0.99162 | -0.060738 | 0.21543 | 0.10434
182 | 0.99598 | 0.031332 | 0.15387 | 0.074524
183 | 0.99599 | 0.031229 | 0 | 0
184 | 0.99594 | 0.031647 | 0 | 0
185 | 0.99592 | 0.031821 | 0.32437 | 0.1571
186 | 0.98625 | -0.12994 | 0.14278 | 0.069151
187 | 0.9863 | -0.1304 | 0 | 0
188 | 0.99347 | -0.10965 | 0.073869 | 0.035776
189 | 0.98697 | -0.13504 | 0 | 0
190 | 0.98691 | -0.13544 | 0.34644 | 0.16779
191 | 0.99778 | 0.01697 | 0.40895 | 0.19806
192 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 3.8902 | 1.7712 | -3.8894 | -1.7719 | 0.00079913 | -0.00067067 | 0.12442 | 0.12443 | 0.12443 | 0.99172 | -0.17396 | 0.99152 | -0.17241 | 56.5611
1 | -4.2004 | -1.9214 | 4.2017 | 1.9228 | 0.0013008 | 0.0013909 | 0.13445 | 0.13445 | 0.13445 | 0.99172 | -0.17396 | 0.9921 | -0.16389 | 38.4154
2 | 3.6116 | 1.6511 | -3.6054 | -1.6573 | 0.0061375 | -0.0062331 | 0.11561 | 0.11571 | 0.11571 | 0.99152 | -0.17241 | 0.98994 | -0.15938 | 52.5966
3 | 0.27786 | 0.12081 | -0.2778 | -0.13399 | 5.9475e-05 | -0.013183 | 0.0088211 | 0.0089813 | 0.0089813 | 0.99152 | -0.17241 | 0.99132 | -0.17077 | 4.0824
4 | -4.2017 | -1.9228 | 4.2026 | 1.9202 | 0.00084987 | -0.0026707 | 0.13445 | 0.13441 | 0.13445 | 0.9921 | -0.16389 | 0.99232 | -0.16131 | 37.1416
5 | 3.3582 | 1.5389 | -3.3552 | -1.5425 | 0.0030207 | -0.0036605 | 0.10772 | 0.10778 | 0.10778 | 0.98994 | -0.15938 | 0.98911 | -0.15246 | 48.9888
6 | 0.24723 | 0.11842 | -0.24722 | -0.11974 | 4.8265e-06 | -0.0013196 | 0.0079937 | 0.0080104 | 0.0080104 | 0.98994 | -0.15938 | 0.98992 | -0.15921 | 3.6411
7 | 0.2778 | 0.13399 | -0.27779 | -0.13454 | 2.5366e-06 | -0.00055151 | 0.0089813 | 0.0089883 | 0.0089883 | 0.99132 | -0.17077 | 0.99132 | -0.17069 | 4.0856
8 | -4.2026 | -1.9202 | 4.2026 | 1.9177 | 5.6592e-05 | -0.0024775 | 0.13441 | 0.13438 | 0.13441 | 0.99232 | -0.16131 | 0.99234 | -0.16124 | 10.5339
9 | 0.37387 | 0.18061 | -0.37386 | -0.18107 | 3.7935e-06 | -0.00045658 | 0.012079 | 0.012084 | 0.012084 | 0.99234 | -0.16124 | 0.99233 | -0.16115 | 5.4929
10 | -4.6446 | -2.1313 | 4.6452 | 2.1325 | 0.00062883 | 0.0012569 | 0.14866 | 0.14865 | 0.14866 | 0.99234 | -0.16124 | 0.99259 | -0.14695 | 11.524
11 | -4.8625 | -2.2377 | 4.8628 | 2.2268 | 0.00033709 | -0.010967 | 0.15567 | 0.15554 | 0.15567 | 0.99259 | -0.14695 | 0.99266 | -0.14661 | 12.2
12 | 0.41076 | 0.19891 | -0.41075 | -0.19894 | 9.9094e-06 | -3.0404e-05 | 0.01332 | 0.01332 | 0.01332 | 0.98911 | -0.15246 | 0.98908 | -0.15262 | 6.343
13 | 2.9444 | 1.3436 | -2.9409 | -1.3495 | 0.0035195 | -0.005844 | 0.094459 | 0.094542 | 0.094542 | 0.98911 | -0.15246 | 0.988 | -0.14334 | 42.9737
14 | 0.36117 | 0.17361 | -0.36116 | -0.17492 | 9.9986e-06 | -0.0013077 | 0.01162 | 0.011636 | 0.011636 | 0.99554 | 0.034736 | 0.99551 | 0.034975 | 5.2893
15 | 0.40115 | 0.1788 | -0.40101 | -0.19382 | 0.00013984 | -0.015021 | 0.012735 | 0.012919 | 0.012919 | 0.99554 | 0.034736 | 0.99521 | 0.037494 | 5.8724
16 | 0.3941 | 0.17846 | -0.39399 | -0.19078 | 0.00011103 | -0.012321 | 0.012545 | 0.012697 | 0.012697 | 0.99554 | 0.034736 | 0.99528 | 0.037011 | 5.7713
17 | -1.1564 | -0.53087 | 1.1572 | 0.52129 | 0.00074984 | -0.0095777 | 0.036897 | 0.03678 | 0.036897 | 0.99554 | 0.034736 | 0.99614 | 0.029869 | 16.7715
18 | 0.40101 | 0.19382 | -0.40101 | -0.19422 | 3.7474e-06 | -0.00039643 | 0.012919 | 0.012924 | 0.012924 | 0.99521 | 0.037494 | 0.9952 | 0.037575 | 5.8747
19 | 0.39399 | 0.19078 | -0.39398 | -0.19081 | 1.0648e-05 | -3.7168e-05 | 0.012697 | 0.012697 | 0.012697 | 0.99528 | 0.037011 | 0.99525 | 0.036833 | 6.0463
20 | 0.59373 | 0.27658 | -0.59371 | -0.27735 | 1.5778e-05 | -0.00077214 | 0.018981 | 0.01899 | 0.01899 | 0.99614 | 0.029869 | 0.99612 | 0.030081 | 8.632
21 | -1.7509 | -0.79786 | 1.752 | 0.79176 | 0.0011251 | -0.0061014 | 0.05576 | 0.055683 | 0.05576 | 0.99614 | 0.029869 | 0.99675 | 0.025072 | 25.3453
22 | 1.5022 | 0.70076 | -1.5021 | -0.70126 | 7.1648e-05 | -0.00050925 | 0.048492 | 0.048499 | 0.048499 | 0.98677 | -0.13286 | 0.98672 | -0.13247 | 22.045
23 | -1.5022 | -0.70076 | 1.503 | 0.69504 | 0.00080217 | -0.0057146 | 0.048492 | 0.048419 | 0.048492 | 0.98677 | -0.13286 | 0.98726 | -0.13708 | 22.042
24 | 1.285 | 0.59609 | -1.2848 | -0.59606 | 0.00012149 | 2.9952e-05 | 0.041441 | 0.041441 | 0.041441 | 0.98672 | -0.13247 | 0.98662 | -0.1332 | 19.7339
25 | 0.26716 | 0.12938 | -0.26716 | -0.12939 | 1.357e-06 | -1.0914e-05 | 0.0086795 | 0.0086797 | 0.0086797 | 0.98726 | -0.13708 | 0.98725 | -0.13711 | 4.1332
26 | -1.7702 | -0.82442 | 1.7716 | 0.81728 | 0.0014094 | -0.0071357 | 0.057097 | 0.057005 | 0.057097 | 0.98726 | -0.13708 | 0.988 | -0.14334 | 25.9534
27 | 0.33875 | 0.16365 | -0.33875 | -0.16406 | 2.8948e-06 | -0.00041718 | 0.010992 | 0.010998 | 0.010998 | 0.988 | -0.14334 | 0.98799 | -0.14327 | 4.9989
28 | 0.83057 | 0.36855 | -0.83019 | -0.37801 | 0.00038834 | -0.0094575 | 0.02655 | 0.026664 | 0.026664 | 0.988 | -0.14334 | 0.98756 | -0.13993 | 12.1202
29 | 0.71532 | 0.32372 | -0.71513 | -0.32988 | 0.00018823 | -0.0061552 | 0.022951 | 0.023027 | 0.023027 | 0.98756 | -0.13993 | 0.98732 | -0.13794 | 10.4667
30 | 0.11486 | 0.054285 | -0.11486 | -0.05563 | 1.069e-06 | -0.0013456 | 0.0037137 | 0.0037306 | 0.0037306 | 0.98756 | -0.13993 | 0.98755 | -0.13986 | 1.6957
31 | 0.71513 | 0.32988 | -0.71509 | -0.33135 | 4.5266e-05 | -0.0014737 | 0.023027 | 0.023045 | 0.023045 | 0.98732 | -0.13794 | 0.98726 | -0.13744 | 10.475
32 | 0.34656 | 0.15286 | -0.34656 | -0.15348 | 4.345e-06 | -0.00061575 | 0.011076 | 0.011083 | 0.011083 | 0.98726 | -0.13744 | 0.98725 | -0.13735 | 5.0376
33 | 0.40441 | 0.19513 | -0.4044 | -0.19586 | 6.9504e-06 | -0.00072766 | 0.013005 | 0.013014 | 0.013014 | 0.99675 | 0.025072 | 0.99673 | 0.025221 | 5.9153
34 | 0.4597 | 0.21164 | -0.45965 | -0.2155 | 4.6915e-05 | -0.0038538 | 0.014657 | 0.014704 | 0.014704 | 0.99675 | 0.025072 | 0.99665 | 0.02588 | 6.6837
35 | -2.6161 | -1.1985 | 2.6201 | 1.1895 | 0.0039647 | -0.008996 | 0.083341 | 0.083218 | 0.083341 | 0.99675 | 0.025072 | 0.99817 | 0.01362 | 37.8821
36 | 0.45965 | 0.2155 | -0.45965 | -0.21566 | 2.0144e-06 | -0.0001649 | 0.014704 | 0.014706 | 0.014706 | 0.99665 | 0.02588 | 0.99665 | 0.025915 | 6.6846
37 | 0.7307 | 0.33991 | -0.73056 | -0.34459 | 0.00014427 | -0.004677 | 0.023307 | 0.023365 | 0.023365 | 0.99817 | 0.01362 | 0.99798 | 0.015214 | 10.6204
38 | 0.29142 | 0.14109 | -0.29142 | -0.14114 | 2.3743e-07 | -4.8173e-05 | 0.009364 | 0.0093646 | 0.0093646 | 0.99817 | 0.01362 | 0.99817 | 0.013627 | 4.2566
39 | -3.6422 | -1.6705 | 3.6459 | 1.6668 | 0.0036596 | -0.0037773 | 0.11589 | 0.11583 | 0.11589 | 0.99817 | 0.01362 | 0.99911 | 0.0059478 | 52.6756
40 | 0.078955 | 0.031286 | -0.078955 | -0.031669 | 1.3074e-07 | -0.00038314 | 0.0024599 | 0.002464 | 0.002464 | 0.99665 | 0.025915 | 0.99665 | 0.025924 | 1.12
41 | 0.47833 | 0.22147 | -0.47832 | -0.22257 | 1.4512e-05 | -0.0010983 | 0.015276 | 0.015289 | 0.015289 | 0.99612 | 0.030081 | 0.99609 | 0.030321 | 6.9497
42 | 1.2848 | 0.59606 | -1.2844 | -0.60049 | 0.00045164 | -0.0044367 | 0.041441 | 0.041498 | 0.041498 | 0.98662 | -0.1332 | 0.9863 | -0.1304 | 18.8625
43 | -0.31338 | -0.15173 | 0.31344 | 0.1514 | 5.5055e-05 | -0.00032112 | 0.010119 | 0.010115 | 0.010119 | 0.99324 | -0.11792 | 0.99343 | -0.11675 | 4.8188
44 | 0.31338 | 0.15173 | -0.31337 | -0.15177 | 8.1894e-06 | -4.7728e-05 | 0.010119 | 0.01012 | 0.01012 | 0.99324 | -0.11792 | 0.99321 | -0.11809 | 4.8191
45 | -5.7526 | -2.6168 | 5.7526 | 2.6158 | 4.1484e-05 | -0.00096407 | 0.18364 | 0.18363 | 0.18364 | 0.99343 | -0.11675 | 0.99343 | -0.11672 | 14.3922
46 | 5.4391 | 2.4654 | -5.4389 | -2.4725 | 0.00027222 | -0.0070989 | 0.17353 | 0.17362 | 0.17362 | 0.99343 | -0.11675 | 0.99337 | -0.11701 | 13.6065
47 | 0.34656 | 0.15348 | -0.34646 | -0.16769 | 0.00010194 | -0.014212 | 0.011083 | 0.011258 | 0.011258 | 0.98725 | -0.13735 | 0.98697 | -0.13504 | 5.1172
48 | -0.22748 | -0.11018 | 0.22751 | 0.10992 | 2.1885e-05 | -0.00025613 | 0.007335 | 0.0073316 | 0.007335 | 0.99475 | -0.050412 | 0.99485 | -0.049775 | 3.4929
49 | -0.63666 | -0.30808 | 0.63669 | 0.3069 | 2.8262e-05 | -0.0011803 | 0.020523 | 0.020508 | 0.020523 | 0.99485 | -0.049775 | 0.9949 | -0.050159 | 9.3288
50 | 0.29686 | 0.13313 | -0.29682 | -0.14183 | 4.4357e-05 | -0.0086998 | 0.0094402 | 0.0095465 | 0.0095465 | 0.9949 | -0.050159 | 0.99476 | -0.048985 | 4.3393
51 | -0.93356 | -0.44004 | 0.93375 | 0.43625 | 0.00019443 | -0.0037872 | 0.029946 | 0.029899 | 0.029946 | 0.9949 | -0.050159 | 0.99509 | -0.051847 | 13.6118
52 | -1.1025 | -0.51203 | 1.1026 | 0.5119 | 9.172e-06 | -0.00012793 | 0.035263 | 0.035262 | 0.035263 | 0.99516 | -0.040148 | 0.99517 | -0.040214 | 16.0287
53 | 0.96075 | 0.44336 | -0.96036 | -0.44339 | 0.00039269 | -3.0473e-05 | 0.030694 | 0.030697 | 0.030697 | 0.99516 | -0.040148 | 0.99473 | -0.04333 | 14.6176
54 | -1.2702 | -0.59308 | 1.2702 | 0.59268 | 3.8514e-05 | -0.0004012 | 0.040663 | 0.040658 | 0.040663 | 0.99517 | -0.040214 | 0.9952 | -0.040456 | 18.4832
55 | 0.58015 | 0.25986 | -0.57995 | -0.26983 | 0.00019412 | -0.0099681 | 0.018448 | 0.018569 | 0.018569 | 0.99473 | -0.04333 | 0.99442 | -0.040792 | 8.4404
56 | 0.38021 | 0.18353 | -0.3802 | -0.18414 | 5.1988e-06 | -0.00061095 | 0.012252 | 0.01226 | 0.01226 | 0.99473 | -0.04333 | 0.99472 | -0.043211 | 5.5726
57 | -5.7526 | -2.6158 | 5.7529 | 2.6095 | 0.0002738 | -0.0063666 | 0.18363 | 0.18355 | 0.18363 | 0.99343 | -0.11672 | 0.99348 | -0.11647 | 14.3912
58 | 5.1766 | 2.3455 | -5.1752 | -2.3425 | 0.0013856 | 0.0029501 | 0.16515 | 0.16516 | 0.16516 | 0.99337 | -0.11701 | 0.99288 | -0.14548 | 12.8033
59 | -5.8601 | -2.6614 | 5.8603 | 2.6576 | 0.00016757 | -0.003753 | 0.18701 | 0.18697 | 0.18701 | 0.99348 | -0.11647 | 0.99351 | -0.11632 | 14.6563
60 | 4.9786 | 2.2646 | -4.9784 | -2.2715 | 0.0002192 | -0.0068197 | 0.15904 | 0.15912 | 0.15912 | 0.99277 | -0.14606 | 0.99272 | -0.14628 | 12.4705
61 | -5.0536 | -2.301 | 5.0538 | 2.294 | 0.00023173 | -0.0069992 | 0.16146 | 0.16138 | 0.16146 | 0.99277 | -0.14606 | 0.99282 | -0.14582 | 12.6537
62 | 0.11527 | 0.054913 | -0.11527 | -0.055826 | 7.1672e-07 | -0.00091335 | 0.0037128 | 0.0037243 | 0.0037243 | 0.99272 | -0.14628 | 0.99272 | -0.14623 | 1.6929
63 | 4.8631 | 2.2166 | -4.8628 | -2.2268 | 0.00031377 | -0.010227 | 0.15541 | 0.15554 | 0.15554 | 0.99272 | -0.14628 | 0.99266 | -0.14661 | 12.1894
64 | -5.0538 | -2.294 | 5.054 | 2.289 | 0.00016402 | -0.0049591 | 0.16138 | 0.16131 | 0.16138 | 0.99282 | -0.14582 | 0.99285 | -0.14565 | 12.647
65 | -5.054 | -2.289 | 5.0541 | 2.2839 | 0.00016971 | -0.0051354 | 0.16131 | 0.16125 | 0.16131 | 0.99285 | -0.14565 | 0.99288 | -0.14548 | 12.6422
66 | -0.20757 | -0.10053 | 0.20757 | 0.10012 | 1.0941e-06 | -0.00041603 | 0.0067574 | 0.0067521 | 0.0067574 | 0.98528 | -0.12799 | 0.98528 | -0.12804 | 3.0715
67 | -0.54144 | -0.25716 | 0.54159 | 0.24908 | 0.00014334 | -0.0080753 | 0.017562 | 0.017461 | 0.017562 | 0.98528 | -0.12804 | 0.98553 | -0.13017 | 7.9827
68 | 0.33387 | 0.15704 | -0.33384 | -0.16166 | 3.1311e-05 | -0.0046175 | 0.01081 | 0.010868 | 0.010868 | 0.98528 | -0.12804 | 0.9852 | -0.12725 | 4.9402
69 | 0.31282 | 0.15145 | -0.31282 | -0.1515 | 8.8095e-06 | -4.9792e-05 | 0.010181 | 0.010181 | 0.010181 | 0.98553 | -0.13017 | 0.9855 | -0.13035 | 4.8482
70 | -0.85441 | -0.40054 | 0.85461 | 0.39611 | 0.00019674 | -0.0044247 | 0.027641 | 0.027585 | 0.027641 | 0.98553 | -0.13017 | 0.98574 | -0.132 | 12.5639
71 | 0.33384 | 0.16166 | -0.33383 | -0.16168 | 4.5109e-06 | -2.2009e-05 | 0.010868 | 0.010869 | 0.010869 | 0.9852 | -0.12725 | 0.98518 | -0.12734 | 5.1756
72 | 0.3263 | 0.12524 | -0.32611 | -0.15624 | 0.00018851 | -0.030997 | 0.010167 | 0.010525 | 0.010525 | 0.99238 | -0.063475 | 0.99183 | -0.05971 | 4.7839
73 | -0.3263 | -0.12524 | 0.32631 | 0.12333 | 1.1207e-05 | -0.00191 | 0.010167 | 0.010147 | 0.010167 | 0.99238 | -0.063475 | 0.99241 | -0.063619 | 4.6213
74 | 0.32611 | 0.15624 | -0.3261 | -0.15741 | 7.359e-06 | -0.001165 | 0.010525 | 0.010539 | 0.010539 | 0.99183 | -0.05971 | 0.99181 | -0.059517 | 4.7906
75 | -0.51441 | -0.21444 | 0.51442 | 0.21344 | 1.4845e-05 | -0.00099125 | 0.016211 | 0.0162 | 0.016211 | 0.99241 | -0.063619 | 0.99244 | -0.063787 | 7.3688
76 | 0.16822 | 0.080423 | -0.16822 | -0.081473 | 1.8063e-06 | -0.0010497 | 0.0054605 | 0.0054738 | 0.0054738 | 0.98574 | -0.132 | 0.98573 | -0.13191 | 2.4881
77 | -1.0228 | -0.47654 | 1.0229 | 0.47556 | 6.2303e-05 | -0.00097345 | 0.033045 | 0.033033 | 0.033045 | 0.98574 | -0.132 | 0.98579 | -0.13249 | 15.0205
78 | -1.0229 | -0.47556 | 1.0229 | 0.47478 | 4.9983e-05 | -0.00078157 | 0.033033 | 0.033023 | 0.033033 | 0.98579 | -0.13249 | 0.98584 | -0.13287 | 15.015
79 | 0.21547 | 0.10382 | -0.21543 | -0.10434 | 3.9534e-05 | -0.0005123 | 0.0069615 | 0.0069683 | 0.0069683 | 0.99181 | -0.059517 | 0.99162 | -0.060738 | 3.3182
80 | -0.51442 | -0.21344 | 0.51444 | 0.21209 | 2.0233e-05 | -0.0013534 | 0.0162 | 0.016185 | 0.0162 | 0.99244 | -0.063787 | 0.99248 | -0.064013 | 7.3637
81 | -1.1411 | -0.532 | 1.1415 | 0.53206 | 0.00044433 | 6.532e-05 | 0.036866 | 0.036864 | 0.036866 | 0.98584 | -0.13287 | 0.98625 | -0.12994 | 17.5554
82 | -0.32222 | -0.15606 | 0.32222 | 0.1556 | 2.7938e-06 | -0.00045806 | 0.010386 | 0.010381 | 0.010386 | 0.99508 | -0.051772 | 0.99509 | -0.051847 | 4.7211
83 | -1.256 | -0.59185 | 1.257 | 0.59206 | 0.00097716 | 0.00021207 | 0.040279 | 0.040274 | 0.040279 | 0.99509 | -0.051847 | 0.99591 | -0.046187 | 19.1803
84 | 0.23354 | 0.11308 | -0.23354 | -0.11311 | 2.2625e-06 | -2.516e-05 | 0.0075214 | 0.0075217 | 0.0075217 | 0.99591 | -0.046187 | 0.9959 | -0.04625 | 3.5818
85 | 0.37283 | 0.17943 | -0.3728 | -0.17955 | 2.8427e-05 | -0.0001135 | 0.011993 | 0.011995 | 0.011995 | 0.99591 | -0.046187 | 0.99583 | -0.046701 | 5.7119
86 | -1.8633 | -0.88458 | 1.8634 | 0.88408 | 0.00010699 | -0.00049927 | 0.059788 | 0.059781 | 0.059788 | 0.99591 | -0.046187 | 0.99596 | -0.046664 | 27.1762
87 | 0.3728 | 0.17955 | -0.37279 | -0.18055 | 8.1669e-06 | -0.0010032 | 0.011995 | 0.012008 | 0.012008 | 0.99583 | -0.046701 | 0.99581 | -0.046511 | 5.458
88 | -1.8634 | -0.88408 | 1.8636 | 0.88321 | 0.00018647 | -0.00087059 | 0.059781 | 0.05977 | 0.059781 | 0.99596 | -0.046664 | 0.99606 | -0.047495 | 27.1732
89 | 0.29682 | 0.14183 | -0.29681 | -0.14375 | 9.9147e-06 | -0.0019175 | 0.0095465 | 0.0095706 | 0.0095706 | 0.99476 | -0.048985 | 0.99473 | -0.048699 | 4.3503
90 | 0.57995 | 0.26983 | -0.57992 | -0.26987 | 3.0183e-05 | -3.9089e-05 | 0.018569 | 0.01857 | 0.01857 | 0.99442 | -0.040792 | 0.99436 | -0.041187 | 8.8426
91 | 0.33426 | 0.15089 | -0.33425 | -0.15093 | 7.9008e-06 | -4.1223e-05 | 0.010647 | 0.010647 | 0.010647 | 0.99436 | -0.041187 | 0.99434 | -0.041383 | 5.0702
92 | -7.0517 | -3.2207 | 7.052 | 3.2151 | 0.00036696 | -0.0056091 | 0.22518 | 0.22511 | 0.22518 | 0.99382 | -0.10173 | 0.99387 | -0.10147 | 17.6475
93 | 6.6636 | 3.0327 | -6.6631 | -3.0315 | 0.00049759 | 0.0011698 | 0.21266 | 0.21266 | 0.21266 | 0.99382 | -0.10173 | 0.99368 | -0.10965 | 16.4854
94 | -7.052 | -3.2151 | 7.0548 | 3.2215 | 0.0027224 | 0.0064983 | 0.22511 | 0.2251 | 0.22511 | 0.99387 | -0.10147 | 0.99458 | -0.060602 | 17.4505
95 | 6.5716 | 2.9872 | -6.5715 | -2.9893 | 0.00011706 | -0.0020715 | 0.20971 | 0.20974 | 0.20974 | 0.99368 | -0.10965 | 0.99366 | -0.10975 | 16.4371
96 | -9.2522 | -4.2193 | 9.2525 | 4.2162 | 0.00035862 | -0.0031108 | 0.29515 | 0.29511 | 0.29515 | 0.99458 | -0.060602 | 0.99462 | -0.060405 | 23.1307
97 | 0.069256 | 0.03242 | -0.069255 | -0.032521 | 7.5525e-07 | -0.00010109 | 0.0022195 | 0.0022207 | 0.0022207 | 0.99458 | -0.060602 | 0.99457 | -0.060683 | 1.0575
98 | 1.9067 | 0.85813 | -1.905 | -0.85734 | 0.0017615 | 0.00078668 | 0.060689 | 0.060693 | 0.060693 | 0.99458 | -0.060602 | 0.9936 | -0.068366 | 28.9015
99 | 6.5715 | 2.9893 | -6.5713 | -2.9942 | 0.00027583 | -0.0048786 | 0.20974 | 0.2098 | 0.2098 | 0.99366 | -0.10975 | 0.99362 | -0.10996 | 16.4418
100 | 0.412 | 0.19196 | -0.41199 | -0.19311 | 1.1371e-05 | -0.0011468 | 0.013205 | 0.013219 | 0.013219 | 0.99362 | -0.10996 | 0.9936 | -0.10974 | 6.0088
101 | 6.1593 | 2.8022 | -6.1589 | -2.8014 | 0.00036949 | 0.00084741 | 0.19659 | 0.1966 | 0.1966 | 0.99362 | -0.10996 | 0.99351 | -0.11632 | 15.2399
102 | 0.23831 | 0.11128 | -0.23831 | -0.11213 | 2.8149e-06 | -0.00084885 | 0.0076421 | 0.0076526 | 0.0076526 | 0.9935 | -0.10993 | 0.99349 | -0.10983 | 3.4785
103 | -0.23831 | -0.11128 | 0.23832 | 0.11113 | 1.4199e-05 | -0.00015195 | 0.0076421 | 0.0076401 | 0.0076421 | 0.9935 | -0.10993 | 0.99357 | -0.10948 | 3.6391
104 | 0.15834 | 0.073396 | -0.15833 | -0.07503 | 2.3919e-06 | -0.0016348 | 0.0050709 | 0.0050911 | 0.0050911 | 0.99349 | -0.10983 | 0.99348 | -0.10971 | 2.3141
105 | -0.31435 | -0.14795 | 0.31435 | 0.14743 | 3.0153e-06 | -0.00052192 | 0.010094 | 0.010088 | 0.010094 | 0.99357 | -0.10948 | 0.99357 | -0.10956 | 4.5883
106 | 0.31436 | 0.14619 | -0.31435 | -0.14743 | 7.1243e-06 | -0.0012358 | 0.010073 | 0.010088 | 0.010088 | 0.9936 | -0.10974 | 0.99357 | -0.10956 | 4.5853
107 | 0.097629 | 0.046921 | -0.097628 | -0.047284 | 2.0344e-07 | -0.0003621 | 0.003147 | 0.0031516 | 0.0031516 | 0.9936 | -0.10974 | 0.99359 | -0.10972 | 1.4326
108 | 0.19465 | 0.093408 | -0.19465 | -0.093475 | 4.1707e-06 | -6.7467e-05 | 0.0062733 | 0.0062742 | 0.0062742 | 0.99351 | -0.11632 | 0.99349 | -0.11647 | 2.9877
109 | 0.11632 | 0.055537 | -0.11632 | -0.055949 | 3.2798e-07 | -0.00041209 | 0.0037453 | 0.0037504 | 0.0037504 | 0.99349 | -0.11647 | 0.99349 | -0.11644 | 1.7047
110 | 0.069255 | 0.032521 | -0.069255 | -0.033542 | 2.8619e-07 | -0.0010207 | 0.0022207 | 0.0022335 | 0.0022335 | 0.99457 | -0.060683 | 0.99457 | -0.060648 | 1.0152
111 | 1.689 | 0.75392 | -1.6877 | -0.76124 | 0.0012617 | -0.0073215 | 0.053738 | 0.053829 | 0.053829 | 0.9936 | -0.068366 | 0.9929 | -0.062946 | 24.4679
112 | 0.21599 | 0.10343 | -0.21599 | -0.10461 | 3.2554e-06 | -0.0011839 | 0.0069577 | 0.0069726 | 0.0069726 | 0.9936 | -0.068366 | 0.99359 | -0.068237 | 3.1694
113 | 1.6877 | 0.76124 | -1.6876 | -0.76217 | 0.00016096 | -0.0009314 | 0.053829 | 0.053841 | 0.053841 | 0.9929 | -0.062946 | 0.99281 | -0.062244 | 24.4732
114 | -9.4606 | -4.3093 | 9.4626 | 4.2926 | 0.0020125 | -0.016701 | 0.30159 | 0.30138 | 0.30159 | 0.99505 | -0.042612 | 0.99527 | -0.041516 | 23.636
115 | 9.4606 | 4.3093 | -9.4594 | -4.3195 | 0.0012219 | -0.010124 | 0.30159 | 0.30173 | 0.30173 | 0.99505 | -0.042612 | 0.99492 | -0.043268 | 23.6462
116 | -9.4626 | -4.2926 | 9.4628 | 4.2915 | 0.00013001 | -0.0010801 | 0.30138 | 0.30137 | 0.30138 | 0.99527 | -0.041516 | 0.99529 | -0.041445 | 23.6192
117 | 9.254 | 4.22 | -9.2525 | -4.2162 | 0.0014968 | 0.0037616 | 0.2951 | 0.29511 | 0.29511 | 0.99492 | -0.043268 | 0.99462 | -0.060405 | 22.8766
118 | 1.6102 | 0.72471 | -1.6098 | -0.72455 | 0.0004218 | 0.00015856 | 0.051343 | 0.051344 | 0.051344 | 0.99281 | -0.062244 | 0.99254 | -0.064444 | 24.4496
119 | -9.8356 | -4.4721 | 9.8357 | 4.4712 | 0.00011464 | -0.00087604 | 0.31338 | 0.31337 | 0.31338 | 0.99529 | -0.041445 | 0.9953 | -0.041384 | 24.5595
120 | 1.173 | 0.52961 | -1.1729 | -0.53001 | 3.2219e-05 | -0.00039553 | 0.037431 | 0.037436 | 0.037436 | 0.99254 | -0.064444 | 0.99251 | -0.064242 | 17.0164
121 | 0.43684 | 0.19494 | -0.43679 | -0.19999 | 5.6012e-05 | -0.0050589 | 0.013913 | 0.013974 | 0.013974 | 0.99254 | -0.064444 | 0.99242 | -0.063496 | 6.3517
122 | 0.48699 | 0.23578 | -0.48697 | -0.23582 | 2.1621e-05 | -4.4074e-05 | 0.015737 | 0.015738 | 0.015738 | 0.99251 | -0.064242 | 0.99246 | -0.064534 | 7.4942
123 | 0.68593 | 0.29423 | -0.6859 | -0.29513 | 2.4412e-05 | -0.00090494 | 0.021708 | 0.021719 | 0.021719 | 0.99251 | -0.064242 | 0.99248 | -0.064013 | 9.8722
124 | 0.22589 | 0.097906 | -0.22587 | -0.1034 | 1.6169e-05 | -0.0054986 | 0.0071613 | 0.0072265 | 0.0072265 | 0.99242 | -0.063496 | 0.99235 | -0.062986 | 3.2848
125 | 0.2109 | 0.10209 | -0.21089 | -0.10214 | 3.7594e-06 | -5.1047e-05 | 0.0068155 | 0.0068162 | 0.0068162 | 0.99242 | -0.063496 | 0.9924 | -0.063614 | 3.2458
126 | -0.16514 | -0.079982 | 0.16514 | 0.079956 | 1.1695e-06 | -2.6364e-05 | 0.0053372 | 0.0053369 | 0.0053372 | 0.99246 | -0.064581 | 0.99246 | -0.064534 | 2.5415
127 | 22.0661 | 9.8669 | -22.064 | -9.8691 | 0.0020139 | -0.0022298 | 0.69777 | 0.69781 | 0.69781 | 1 | 0 | 0.9999 | -0.00050502 | 54.6876
128 | 18.311 | 8.156 | -18.2861 | -8.2022 | 0.024835 | -0.046159 | 0.57871 | 0.57942 | 0.57942 | 0.9999 | -0.00050502 | 0.99849 | -0.0080313 | 45.4092
129 | 3.7531 | 1.7131 | -3.7499 | -1.7161 | 0.0031839 | -0.003064 | 0.11911 | 0.11915 | 0.11915 | 0.9999 | -0.00050502 | 0.99911 | 0.0059478 | 54.1607
130 | 11.7361 | 5.1931 | -11.7251 | -5.2517 | 0.011034 | -0.058581 | 0.37104 | 0.3718 | 0.3718 | 0.99849 | -0.0080313 | 0.99751 | -0.013334 | 29.138
131 | 6.55 | 3.0091 | -6.5498 | -3.0131 | 0.0002234 | -0.0040444 | 0.2084 | 0.20845 | 0.20845 | 0.99849 | -0.0080313 | 0.99845 | -0.0081981 | 16.3359
132 | 0.104 | 0.049358 | -0.104 | -0.050368 | 6.286e-07 | -0.0010104 | 0.0033261 | 0.0033387 | 0.0033387 | 0.99911 | 0.0059478 | 0.9991 | 0.0059993 | 1.5176
133 | 0.37868 | 0.18335 | -0.37868 | -0.1834 | 4.4039e-07 | -5.2729e-05 | 0.012176 | 0.012176 | 0.012176 | 0.99751 | -0.013334 | 0.99751 | -0.013324 | 5.5347
134 | 11.3464 | 5.0684 | -11.3362 | -5.1263 | 0.010209 | -0.057943 | 0.35963 | 0.36039 | 0.36039 | 0.99751 | -0.013334 | 0.99657 | -0.018211 | 28.2435
135 | 6.1835 | 2.8357 | -6.1835 | -2.8363 | 3.2179e-05 | -0.00065636 | 0.19668 | 0.19669 | 0.19669 | 0.99845 | -0.0081981 | 0.99845 | -0.0082238 | 15.4145
136 | 0.57334 | 0.2774 | -0.57333 | -0.27768 | 5.3763e-06 | -0.0002789 | 0.01845 | 0.018453 | 0.018453 | 0.99657 | -0.018211 | 0.99657 | -0.01813 | 8.3878
137 | 10.7629 | 4.8489 | -10.758 | -4.8796 | 0.0048487 | -0.030713 | 0.34194 | 0.34234 | 0.34234 | 0.99657 | -0.018211 | 0.99611 | -0.020592 | 26.8294
138 | 10.0745 | 4.5532 | -10.0697 | -4.588 | 0.0047785 | -0.034806 | 0.3204 | 0.32084 | 0.32084 | 0.99611 | -0.020592 | 0.99561 | -0.023056 | 25.1446
139 | 0.68354 | 0.32642 | -0.68354 | -0.32658 | 4.4348e-06 | -0.00016198 | 0.021952 | 0.021954 | 0.021954 | 0.99611 | -0.020592 | 0.9961 | -0.020537 | 9.9791
140 | 9.8374 | 4.4755 | -9.8357 | -4.4712 | 0.0016996 | 0.0043047 | 0.31336 | 0.31337 | 0.31337 | 0.99561 | -0.023056 | 0.9953 | -0.041384 | 24.2921
141 | 0.23228 | 0.11246 | -0.23227 | -0.11249 | 3.0368e-06 | -3.412e-05 | 0.0074826 | 0.0074831 | 0.0074831 | 0.99561 | -0.023056 | 0.9956 | -0.023142 | 3.5634
142 | 0.59078 | 0.28166 | -0.59076 | -0.28254 | 1.7903e-05 | -0.00087725 | 0.018967 | 0.018978 | 0.018978 | 0.9961 | -0.020537 | 0.99607 | -0.020282 | 8.6265
143 | 0.40904 | 0.18906 | -0.40896 | -0.19729 | 7.9326e-05 | -0.0082276 | 0.013035 | 0.013136 | 0.013136 | 0.99798 | 0.015214 | 0.9978 | 0.01681 | 5.9711
144 | 0.32152 | 0.15553 | -0.32152 | -0.15572 | 1.15e-06 | -0.00019154 | 0.010331 | 0.010334 | 0.010334 | 0.99798 | 0.015214 | 0.99798 | 0.015245 | 4.6971
145 | 6.1835 | 2.8363 | -6.1821 | -2.8332 | 0.0013624 | 0.0031202 | 0.19669 | 0.1967 | 0.1967 | 0.99845 | -0.0082238 | 0.99804 | -0.031494 | 15.2477
146 | 0.59076 | 0.28254 | -0.59075 | -0.28293 | 8.0978e-06 | -0.00039643 | 0.018978 | 0.018983 | 0.018983 | 0.99607 | -0.020282 | 0.99606 | -0.020165 | 8.6288
147 | 0.40896 | 0.19729 | -0.40895 | -0.19806 | 7.5366e-06 | -0.00077483 | 0.013136 | 0.013146 | 0.013146 | 0.9978 | 0.01681 | 0.99778 | 0.01697 | 5.9756
148 | 0.078955 | 0.031669 | -0.078953 | -0.037609 | 2.0855e-06 | -0.0059399 | 0.002464 | 0.0025331 | 0.0025331 | 0.99665 | 0.025924 | 0.99662 | 0.026104 | 1.1514
149 | 0.078953 | 0.037609 | -0.078953 | -0.038239 | 2.2822e-07 | -0.00062978 | 0.0025331 | 0.002541 | 0.002541 | 0.99662 | 0.026104 | 0.99662 | 0.026129 | 1.155
150 | 0.47832 | 0.22257 | -0.47827 | -0.2266 | 5.3522e-05 | -0.0040335 | 0.015289 | 0.015339 | 0.015339 | 0.99609 | 0.030321 | 0.99599 | 0.031229 | 6.9723
151 | 0.073869 | 0.034123 | -0.073869 | -0.035776 | 5.2817e-07 | -0.0016534 | 0.0023644 | 0.0023849 | 0.0023849 | 0.99348 | -0.10971 | 0.99347 | -0.10965 | 1.0841
152 | 0.11632 | 0.055949 | -0.11632 | -0.056334 | 3.0746e-07 | -0.00038527 | 0.0037504 | 0.0037553 | 0.0037553 | 0.99349 | -0.11644 | 0.99348 | -0.11642 | 1.707
153 | -0.33418 | -0.16185 | 0.33419 | 0.16039 | 9.6494e-06 | -0.0014668 | 0.010782 | 0.010764 | 0.010782 | 0.99414 | -0.039671 | 0.99417 | -0.03992 | 4.901
154 | -0.33419 | -0.16039 | 0.33425 | 0.15093 | 6.1422e-05 | -0.0094581 | 0.010764 | 0.010647 | 0.010764 | 0.99417 | -0.03992 | 0.99434 | -0.041383 | 4.8926
155 | 0.084866 | 0.040635 | -0.084866 | -0.041102 | 1.9916e-07 | -0.00046712 | 0.0027372 | 0.0027431 | 0.0027431 | 0.99235 | -0.062986 | 0.99235 | -0.062966 | 1.2468
156 | 0.14101 | 0.06277 | -0.141 | -0.067558 | 5.5539e-06 | -0.0047885 | 0.00449 | 0.0045484 | 0.0045484 | 0.99235 | -0.062986 | 0.99231 | -0.062678 | 2.0675
157 | 0.141 | 0.067558 | -0.141 | -0.06829 | 8.6219e-07 | -0.00073218 | 0.0045484 | 0.0045577 | 0.0045577 | 0.99231 | -0.062678 | 0.99231 | -0.062626 | 2.0717
158 | -0.24739 | -0.11982 | 0.2474 | 0.11968 | 5.0411e-07 | -0.00014086 | 0.0079662 | 0.0079644 | 0.0079662 | 0.99611 | -0.047936 | 0.99611 | -0.047954 | 3.621
159 | -0.2474 | -0.11968 | 0.24741 | 0.11642 | 1.16e-05 | -0.0032585 | 0.0079644 | 0.0079237 | 0.0079644 | 0.99611 | -0.047954 | 0.99615 | -0.048349 | 3.6202
160 | 0.25739 | 0.11991 | -0.25738 | -0.12459 | 1.8011e-05 | -0.004682 | 0.0082287 | 0.008287 | 0.008287 | 0.99615 | -0.048349 | 0.99609 | -0.047766 | 3.7668
161 | 1.9319 | 0.91532 | -1.9317 | -0.91618 | 0.00019872 | -0.00085974 | 0.06195 | 0.061961 | 0.061961 | 0.99615 | -0.048349 | 0.99606 | -0.047495 | 28.1642
162 | -2.4367 | -1.1516 | 2.4382 | 1.1476 | 0.0015585 | -0.0040781 | 0.078102 | 0.078046 | 0.078102 | 0.99615 | -0.048349 | 0.99674 | -0.053594 | 35.501
163 | 0.40577 | 0.19618 | -0.40576 | -0.19652 | 3.2433e-06 | -0.00033602 | 0.013064 | 0.013068 | 0.013068 | 0.99592 | -0.046572 | 0.99591 | -0.046502 | 5.9402
164 | -2.5884 | -1.2061 | 2.5906 | 1.2009 | 0.0022954 | -0.0052727 | 0.082771 | 0.082699 | 0.082771 | 0.99592 | -0.046572 | 0.99674 | -0.053594 | 37.6233
165 | 2.1826 | 1.01 | -2.1809 | -1.0156 | 0.0016889 | -0.0056534 | 0.069709 | 0.069784 | 0.069784 | 0.99592 | -0.046572 | 0.9952 | -0.040456 | 31.72
166 | -5.1026 | -2.3839 | 5.1053 | 2.3786 | 0.0027154 | -0.0052368 | 0.16311 | 0.16303 | 0.16311 | 0.99674 | -0.053594 | 0.99733 | -0.047081 | 45.0589
167 | 0.073735 | 0.035445 | -0.073735 | -0.035711 | 8.4332e-08 | -0.00026651 | 0.0023694 | 0.0023728 | 0.0023728 | 0.99674 | -0.053594 | 0.99674 | -0.053584 | 1.0785
168 | 0.9107 | 0.42293 | -0.91023 | -0.43238 | 0.00046114 | -0.0094487 | 0.029126 | 0.029244 | 0.029244 | 0.9952 | -0.040456 | 0.99473 | -0.036341 | 13.2928
169 | 0.083448 | 0.039733 | -0.083448 | -0.040416 | 2.757e-07 | -0.00068303 | 0.0026752 | 0.0026838 | 0.0026838 | 0.99733 | -0.047081 | 0.99733 | -0.047053 | 1.2199
170 | -5.1888 | -2.4184 | 5.1898 | 2.3882 | 0.0010416 | -0.03018 | 0.1657 | 0.16533 | 0.1657 | 0.99733 | -0.047081 | 0.99754 | -0.046135 | 12.9859
171 | 0.25738 | 0.12459 | -0.25737 | -0.12465 | 6.9121e-06 | -6.2575e-05 | 0.008287 | 0.0082878 | 0.0082878 | 0.99609 | -0.047766 | 0.99606 | -0.047943 | 3.9466
172 | 0.80553 | 0.38204 | -0.80539 | -0.38587 | 0.00014695 | -0.0038333 | 0.025873 | 0.025921 | 0.025921 | 0.99473 | -0.036341 | 0.99456 | -0.034808 | 11.7824
173 | 0.1047 | 0.050339 | -0.1047 | -0.050709 | 2.3825e-07 | -0.00037035 | 0.0033714 | 0.0033761 | 0.0033761 | 0.99473 | -0.036341 | 0.99472 | -0.036322 | 1.5346
174 | 0.45942 | 0.21856 | -0.45937 | -0.22206 | 4.3428e-05 | -0.0034995 | 0.014767 | 0.014811 | 0.014811 | 0.99456 | -0.034808 | 0.99447 | -0.034002 | 6.7322
175 | 0.34597 | 0.16732 | -0.34597 | -0.16756 | 1.7235e-06 | -0.00024447 | 0.011155 | 0.011158 | 0.011158 | 0.99456 | -0.034808 | 0.99455 | -0.034764 | 5.0717
176 | 0.45937 | 0.22206 | -0.45937 | -0.22248 | 5.3002e-06 | -0.00042563 | 0.014811 | 0.014816 | 0.014816 | 0.99447 | -0.034002 | 0.99446 | -0.033902 | 6.7347
177 | -5.4504 | -2.5143 | 5.4509 | 2.5013 | 0.00049565 | -0.01303 | 0.1737 | 0.17354 | 0.1737 | 0.99754 | -0.046135 | 0.99763 | -0.045692 | 13.6131
178 | 0.26061 | 0.1261 | -0.2606 | -0.12622 | 1.3246e-05 | -0.00011749 | 0.0083783 | 0.0083799 | 0.0083799 | 0.99754 | -0.046135 | 0.99748 | -0.04647 | 3.9904
179 | -5.5408 | -2.5448 | 5.5415 | 2.5463 | 0.00070086 | 0.0015375 | 0.17643 | 0.17643 | 0.17643 | 0.99763 | -0.045692 | 0.99786 | -0.032349 | 13.6767
180 | -5.9297 | -2.7343 | 5.9297 | 2.7332 | 5.2619e-05 | -0.0011647 | 0.1889 | 0.18889 | 0.1889 | 0.99786 | -0.032349 | 0.99787 | -0.032306 | 14.8042
181 | -5.9297 | -2.7332 | 5.9306 | 2.7135 | 0.0008863 | -0.019649 | 0.18889 | 0.18864 | 0.18889 | 0.99787 | -0.032306 | 0.99803 | -0.031572 | 14.803
182 | -5.9306 | -2.7135 | 5.9307 | 2.7115 | 9.1449e-05 | -0.0020307 | 0.18864 | 0.18862 | 0.18864 | 0.99803 | -0.031572 | 0.99804 | -0.031494 | 14.784
183 | -0.28972 | -0.14032 | 0.28972 | 0.14017 | 7.2664e-07 | -0.00014792 | 0.00933 | 0.0093282 | 0.00933 | 0.99602 | -0.019764 | 0.99602 | -0.019786 | 4.2409
184 | -0.28972 | -0.14017 | 0.28974 | 0.13753 | 1.2905e-05 | -0.0026371 | 0.0093282 | 0.0092951 | 0.0093282 | 0.99602 | -0.019786 | 0.99606 | -0.020165 | 4.2401
185 | 0.30102 | 0.1454 | -0.30102 | -0.14579 | 2.0657e-06 | -0.00038967 | 0.0096884 | 0.0096933 | 0.0096933 | 0.99606 | -0.020165 | 0.99605 | -0.020106 | 4.4061
186 | -0.15387 | -0.074524 | 0.15387 | 0.073187 | 1.8447e-06 | -0.0013368 | 0.0049554 | 0.0049386 | 0.0049554 | 0.99598 | 0.031332 | 0.99599 | 0.031229 | 2.2524
187 | 0.32439 | 0.15341 | -0.32438 | -0.15604 | 1.6088e-05 | -0.0026255 | 0.010401 | 0.010433 | 0.010433 | 0.99599 | 0.031229 | 0.99594 | 0.031647 | 4.7424
188 | 0.32438 | 0.15604 | -0.32437 | -0.1571 | 6.5216e-06 | -0.0010595 | 0.010433 | 0.010447 | 0.010447 | 0.99594 | 0.031647 | 0.99592 | 0.031821 | 4.7485
189 | -1.2843 | -0.60122 | 1.2844 | 0.60049 | 7.3683e-05 | -0.00072237 | 0.041507 | 0.041498 | 0.041507 | 0.98625 | -0.12994 | 0.9863 | -0.1304 | 18.8667
190 | 0.34646 | 0.16769 | -0.34644 | -0.16779 | 2.0927e-05 | -9.4642e-05 | 0.011258 | 0.011259 | 0.011259 | 0.98697 | -0.13504 | 0.98691 | -0.13544 | 5.3616

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 22.3817 | 10.0235

## res_load
| p_mw | q_mvar
0 | 0.31021 | 0.15024
1 | 0.068118 | 0.032991
2 | 0.37386 | 0.18107
3 | 0.21722 | 0.1052
4 | 0.24722 | 0.11974
5 | 0.27779 | 0.13454
6 | 0.36116 | 0.17492
7 | 0.39398 | 0.19081
8 | 0.21717 | 0.10518
9 | 0.33875 | 0.16406
10 | 0.41075 | 0.19894
11 | 0.11486 | 0.05563
12 | 0.26716 | 0.12939
13 | 0.36853 | 0.17849
14 | 0.40101 | 0.19422
15 | 0.4044 | 0.19586
16 | 0.38069 | 0.18438
17 | 0.11538 | 0.055879
18 | 0.31337 | 0.15177
19 | 0.22748 | 0.11018
20 | 0.40916 | 0.19816
21 | 0.1418 | 0.068675
22 | 0.16761 | 0.081177
23 | 0.26228 | 0.12703
24 | 0.10723 | 0.051935
25 | 0.074973 | 0.036311
26 | 0.11527 | 0.055826
27 | 0.12107 | 0.058637
28 | 0.20757 | 0.10053
29 | 0.1881 | 0.091101
30 | 0.16822 | 0.081473
31 | 0.31282 | 0.1515
32 | 0.33383 | 0.16168
33 | 0.11063 | 0.053583
34 | 0.11814 | 0.057218
35 | 0.32222 | 0.15606
36 | 0.23354 | 0.11311
37 | 0.3802 | 0.18414
38 | 0.29681 | 0.14375
39 | 0.24566 | 0.11898
40 | 0.37279 | 0.18055
41 | 0.38812 | 0.18797
42 | 0.091409 | 0.044272
43 | 0.22139 | 0.10722
44 | 0.079972 | 0.038732
45 | 0.076024 | 0.03682
46 | 0.10394 | 0.05034
47 | 0.097628 | 0.047284
48 | 0.078333 | 0.037938
49 | 0.069255 | 0.033542
50 | 0.21599 | 0.10461
51 | 0.2054 | 0.099478
52 | 0.077355 | 0.037465
53 | 0.37284 | 0.18057
54 | 0.16514 | 0.079982
55 | 0.32183 | 0.15587
56 | 0.17146 | 0.083041
57 | 0.30169 | 0.14611
58 | 0.36631 | 0.17741
59 | 0.37868 | 0.1834
60 | 0.57333 | 0.27768
61 | 0.092756 | 0.044924
62 | 0.104 | 0.050368
63 | 0.29142 | 0.14114
64 | 0.23227 | 0.11249
65 | 0.32152 | 0.15572
66 | 0.078953 | 0.038239
67 | 0.084463 | 0.040907
68 | 0.11632 | 0.056334
69 | 0.33418 | 0.16185
70 | 0.21089 | 0.10214
71 | 0.141 | 0.06829
72 | 0.084866 | 0.041102
73 | 0.24739 | 0.11982
74 | 0.40576 | 0.19652
75 | 0.073735 | 0.035711
76 | 0.068063 | 0.032964
77 | 0.25737 | 0.12465
78 | 0.1047 | 0.050709
79 | 0.34597 | 0.16756
80 | 0.089834 | 0.043509
81 | 0.2606 | 0.12622
82 | 0.45937 | 0.22248
83 | 0.083448 | 0.040416
84 | 0.3882 | 0.18801
85 | 0.25139 | 0.12175
86 | 0.28972 | 0.14032
87 | 0.30102 | 0.14579
88 | 0.21543 | 0.10434
89 | 0.15387 | 0.074524
90 | 0.32437 | 0.1571
91 | 0.14278 | 0.069151
92 | 0.073869 | 0.035776
93 | 0.34644 | 0.16779
94 | 0.40895 | 0.19806

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1