## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_644_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_644_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_644_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_644_0_node_153 | 20 | n |  | TRUE
4 | bus_MV_644_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_644_0_node_109 | 20 | n |  | TRUE
6 | bus_MV_644_0_node_3 | 20 | n |  | TRUE
7 | bus_MV_644_0_node_22 | 20 | n |  | TRUE
8 | bus_MV_644_0_node_163 | 20 | n |  | TRUE
9 | bus_MV_644_0_node_137 | 20 | n |  | TRUE
10 | bus_MV_644_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_644_0_node_64 | 20 | n |  | TRUE
12 | bus_MV_644_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_644_0_node_63 | 20 | n |  | TRUE
14 | bus_MV_644_0_node_61 | 20 | n |  | TRUE
15 | bus_MV_644_0_node_106 | 20 | n |  | TRUE
16 | bus_MV_644_0_node_107 | 20 | n |  | TRUE
17 | bus_MV_644_0_node_105 | 20 | n |  | TRUE
18 | bus_MV_644_0_node_112 | 20 | n |  | TRUE
19 | bus_MV_644_0_node_108 | 20 | n |  | TRUE
20 | bus_MV_644_0_node_111 | 20 | n |  | TRUE
21 | bus_MV_644_0_node_110 | 20 | n |  | TRUE
22 | bus_MV_644_0_node_122 | 20 | n |  | TRUE
23 | bus_MV_644_0_node_121 | 20 | n |  | TRUE
24 | bus_MV_644_0_node_48 | 20 | n |  | TRUE
25 | bus_MV_644_0_node_138 | 20 | n |  | TRUE
26 | bus_MV_644_0_node_66 | 20 | n |  | TRUE
27 | bus_MV_644_0_node_141 | 20 | n |  | TRUE
28 | bus_MV_644_0_node_65 | 20 | n |  | TRUE
29 | bus_MV_644_0_node_68 | 20 | n |  | TRUE
30 | bus_MV_644_0_node_160 | 20 | n |  | TRUE
31 | bus_MV_644_0_node_10 | 20 | n |  | TRUE
32 | bus_MV_644_0_node_69 | 20 | n |  | TRUE
33 | bus_MV_644_0_node_9 | 20 | n |  | TRUE
34 | bus_MV_644_0_node_12 | 20 | n |  | TRUE
35 | bus_MV_644_0_node_8 | 20 | n |  | TRUE
36 | bus_MV_644_0_node_11 | 20 | n |  | TRUE
37 | bus_MV_644_0_node_19 | 20 | n |  | TRUE
38 | bus_MV_644_0_node_21 | 20 | n |  | TRUE
39 | bus_MV_644_0_node_119 | 20 | n |  | TRUE
40 | bus_MV_644_0_node_17 | 20 | n |  | TRUE
41 | bus_MV_644_0_node_116 | 20 | n |  | TRUE
42 | bus_MV_644_0_node_115 | 20 | n |  | TRUE
43 | bus_MV_644_0_node_120 | 20 | n |  | TRUE
44 | bus_MV_644_0_node_18 | 20 | n |  | TRUE
45 | bus_MV_644_0_node_20 | 20 | n |  | TRUE
46 | bus_MV_644_0_node_57 | 20 | n |  | TRUE
47 | bus_MV_644_0_node_13 | 20 | n |  | TRUE
48 | bus_MV_644_0_node_14 | 20 | n |  | TRUE
49 | bus_MV_644_0_node_58 | 20 | n |  | TRUE
50 | bus_MV_644_0_node_56 | 20 | n |  | TRUE
51 | bus_MV_644_0_node_15 | 20 | n |  | TRUE
52 | bus_MV_644_0_node_140 | 20 | n |  | TRUE
53 | bus_MV_644_0_node_114 | 20 | n |  | TRUE
54 | bus_MV_644_0_node_117 | 20 | n |  | TRUE
55 | bus_MV_644_0_node_113 | 20 | n |  | TRUE
56 | bus_MV_644_0_node_118 | 20 | n |  | TRUE
57 | bus_MV_644_0_node_139 | 20 | n |  | TRUE
58 | bus_MV_644_0_node_23 | 20 | n |  | TRUE
59 | bus_MV_644_0_node_24 | 20 | n |  | TRUE
60 | bus_MV_644_0_node_25 | 20 | n |  | TRUE
61 | bus_MV_644_0_node_26 | 20 | n |  | TRUE
62 | bus_MV_644_0_node_155 | 20 | n |  | TRUE
63 | bus_MV_644_0_node_154 | 20 | n |  | TRUE
64 | bus_MV_644_0_node_27 | 20 | n |  | TRUE
65 | bus_MV_644_0_node_28 | 20 | n |  | TRUE
66 | bus_MV_644_0_node_31 | 20 | n |  | TRUE
67 | bus_MV_644_0_node_29 | 20 | n |  | TRUE
68 | bus_MV_644_0_node_126 | 20 | n |  | TRUE
69 | bus_MV_644_0_node_30 | 20 | n |  | TRUE
70 | bus_MV_644_0_node_125 | 20 | n |  | TRUE
71 | bus_MV_644_0_node_32 | 20 | n |  | TRUE
72 | bus_MV_644_0_node_134 | 20 | n |  | TRUE
73 | bus_MV_644_0_node_42 | 20 | n |  | TRUE
74 | bus_MV_644_0_node_127 | 20 | n |  | TRUE
75 | bus_MV_644_0_node_124 | 20 | n |  | TRUE
76 | bus_MV_644_0_node_133 | 20 | n |  | TRUE
77 | bus_MV_644_0_node_43 | 20 | n |  | TRUE
78 | bus_MV_644_0_node_128 | 20 | n |  | TRUE
79 | bus_MV_644_0_node_33 | 20 | n |  | TRUE
80 | bus_MV_644_0_node_34 | 20 | n |  | TRUE
81 | bus_MV_644_0_node_36 | 20 | n |  | TRUE
82 | bus_MV_644_0_node_35 | 20 | n |  | TRUE
83 | bus_MV_644_0_node_67 | 20 | n |  | TRUE
84 | bus_MV_644_0_node_37 | 20 | n |  | TRUE
85 | bus_MV_644_0_node_38 | 20 | n |  | TRUE
86 | bus_MV_644_0_node_39 | 20 | n |  | TRUE
87 | bus_MV_644_0_node_41 | 20 | n |  | TRUE
88 | bus_MV_644_0_node_55 | 20 | n |  | TRUE
89 | bus_MV_644_0_node_161 | 20 | n |  | TRUE
90 | bus_MV_644_0_node_40 | 20 | n |  | TRUE
91 | bus_MV_644_0_node_162 | 20 | n |  | TRUE
92 | bus_MV_644_0_node_54 | 20 | n |  | TRUE
93 | bus_MV_644_0_node_44 | 20 | n |  | TRUE
94 | bus_MV_644_0_node_45 | 20 | n |  | TRUE
95 | bus_MV_644_0_node_47 | 20 | n |  | TRUE
96 | bus_MV_644_0_node_46 | 20 | n |  | TRUE
97 | bus_MV_644_0_node_49 | 20 | n |  | TRUE
98 | bus_MV_644_0_node_159 | 20 | n |  | TRUE
99 | bus_MV_644_0_node_152 | 20 | n |  | TRUE
100 | bus_MV_644_0_node_53 | 20 | n |  | TRUE
101 | bus_MV_644_0_node_136 | 20 | n |  | TRUE
102 | bus_MV_644_0_node_50 | 20 | n |  | TRUE
103 | bus_MV_644_0_node_51 | 20 | n |  | TRUE
104 | bus_MV_644_0_node_52 | 20 | n |  | TRUE
105 | bus_MV_644_0_node_59 | 20 | n |  | TRUE
106 | bus_MV_644_0_node_60 | 20 | n |  | TRUE
107 | bus_MV_644_0_node_62 | 20 | n |  | TRUE
108 | bus_MV_644_0_node_70 | 20 | n |  | TRUE
109 | bus_MV_644_0_node_71 | 20 | n |  | TRUE
110 | bus_MV_644_0_node_72 | 20 | n |  | TRUE
111 | bus_MV_644_0_node_73 | 20 | n |  | TRUE
112 | bus_MV_644_0_node_148 | 20 | n |  | TRUE
113 | bus_MV_644_0_node_76 | 20 | n |  | TRUE
114 | bus_MV_644_0_node_74 | 20 | n |  | TRUE
115 | bus_MV_644_0_node_75 | 20 | n |  | TRUE
116 | bus_MV_644_0_node_87 | 20 | n |  | TRUE
117 | bus_MV_644_0_node_143 | 20 | n |  | TRUE
118 | bus_MV_644_0_node_147 | 20 | n |  | TRUE
119 | bus_MV_644_0_node_150 | 20 | n |  | TRUE
120 | bus_MV_644_0_node_79 | 20 | n |  | TRUE
121 | bus_MV_644_0_node_101 | 20 | n |  | TRUE
122 | bus_MV_644_0_node_100 | 20 | n |  | TRUE
123 | bus_MV_644_0_node_77 | 20 | n |  | TRUE
124 | bus_MV_644_0_node_142 | 20 | n |  | TRUE
125 | bus_MV_644_0_node_86 | 20 | n |  | TRUE
126 | bus_MV_644_0_node_144 | 20 | n |  | TRUE
127 | bus_MV_644_0_node_96 | 20 | n |  | TRUE
128 | bus_MV_644_0_node_164 | 20 | n |  | TRUE
129 | bus_MV_644_0_node_103 | 20 | n |  | TRUE
130 | bus_MV_644_0_node_149 | 20 | n |  | TRUE
131 | bus_MV_644_0_node_81 | 20 | n |  | TRUE
132 | bus_MV_644_0_node_82 | 20 | n |  | TRUE
133 | bus_MV_644_0_node_83 | 20 | n |  | TRUE
134 | bus_MV_644_0_node_84 | 20 | n |  | TRUE
135 | bus_MV_644_0_node_88 | 20 | n |  | TRUE
136 | bus_MV_644_0_node_85 | 20 | n |  | TRUE
137 | bus_MV_644_0_node_98 | 20 | n |  | TRUE
138 | bus_MV_644_0_node_146 | 20 | n |  | TRUE
139 | bus_MV_644_0_node_97 | 20 | n |  | TRUE
140 | bus_MV_644_0_node_151 | 20 | n |  | TRUE
141 | bus_MV_644_0_node_145 | 20 | n |  | TRUE
142 | bus_MV_644_0_node_99 | 20 | n |  | TRUE
143 | bus_MV_644_0_node_104 | 20 | n |  | TRUE
144 | bus_MV_644_0_node_89 | 20 | n |  | TRUE
145 | bus_MV_644_0_node_91 | 20 | n |  | TRUE
146 | bus_MV_644_0_node_157 | 20 | n |  | TRUE
147 | bus_MV_644_0_node_90 | 20 | n |  | TRUE
148 | bus_MV_644_0_node_93 | 20 | n |  | TRUE
149 | bus_MV_644_0_node_92 | 20 | n |  | TRUE
150 | bus_MV_644_0_node_158 | 20 | n |  | TRUE
151 | bus_MV_644_0_node_156 | 20 | n |  | TRUE
152 | bus_MV_644_0_node_94 | 20 | n |  | TRUE
153 | bus_MV_644_0_node_95 | 20 | n |  | TRUE
154 | bus_MV_644_0_node_102 | 20 | n |  | TRUE
155 | bus_MV_644_0_node_123 | 20 | n |  | TRUE
156 | bus_MV_644_0_node_165 | 20 | n |  | TRUE
157 | bus_MV_644_0_node_132 | 20 | n |  | TRUE
158 | bus_MV_644_0_node_130 | 20 | n |  | TRUE
159 | bus_MV_644_0_node_129 | 20 | n |  | TRUE
160 | bus_MV_644_0_node_135 | 20 | n |  | TRUE
161 | bus_HV_644_0_node_33 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_644_0_load_0 | 0 | 0.40329 | 0.19532 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_644_0_load_153 | 3 | 0.41426 | 0.20064 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_644_0_load_22 | 7 | 0.36277 | 0.1757 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_644_0_load_163 | 8 | 0.32764 | 0.15868 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_644_0_load_137 | 9 | 0.078998 | 0.038261 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_644_0_load_63 | 13 | 0.3818 | 0.18491 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_644_0_load_61 | 14 | 0.10683 | 0.051742 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_644_0_load_105 | 17 | 0.11372 | 0.055077 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_644_0_load_111 | 20 | 0.17014 | 0.082401 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_644_0_load_110 | 21 | 0.076922 | 0.037255 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_644_0_load_121 | 23 | 0.080463 | 0.03897 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_644_0_load_138 | 25 | 0.39325 | 0.19046 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_644_0_load_141 | 27 | 0.072674 | 0.035198 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_644_0_load_68 | 29 | 0.28185 | 0.1365 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_644_0_load_160 | 30 | 0.16276 | 0.078828 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_644_0_load_69 | 32 | 0.34675 | 0.16794 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_644_0_load_12 | 34 | 0.31198 | 0.1511 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_644_0_load_8 | 35 | 0.34566 | 0.16741 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_644_0_load_21 | 38 | 0.26858 | 0.13008 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_644_0_load_119 | 39 | 0.28972 | 0.14032 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_644_0_load_120 | 43 | 0.11784 | 0.057071 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_644_0_load_20 | 45 | 0.22734 | 0.11011 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_644_0_load_56 | 50 | 0.32288 | 0.15638 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_644_0_load_15 | 51 | 0.38265 | 0.18533 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_644_0_load_140 | 52 | 0.074253 | 0.035962 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_644_0_load_113 | 55 | 0.57335 | 0.27768 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_644_0_load_118 | 56 | 0.11483 | 0.055616 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_644_0_load_139 | 57 | 1.1464 | 0.55523 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_644_0_load_23 | 58 | 0.27376 | 0.13259 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_644_0_load_155 | 62 | 0.25975 | 0.1258 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_644_0_load_27 | 64 | 0.27578 | 0.13357 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_644_0_load_126 | 68 | 0.14967 | 0.072487 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_644_0_load_134 | 72 | 0.10021 | 0.048534 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_644_0_load_42 | 73 | 0.41201 | 0.19955 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_644_0_load_127 | 74 | 0.12525 | 0.060661 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_644_0_load_124 | 75 | 1.3411 | 0.64954 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_644_0_load_133 | 76 | 0.42044 | 0.20363 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_644_0_load_128 | 78 | 0.25476 | 0.12339 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_644_0_load_33 | 79 | 0.33473 | 0.16212 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_644_0_load_67 | 83 | 0.36281 | 0.17572 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_644_0_load_37 | 84 | 0.23565 | 0.11413 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_644_0_load_55 | 88 | 0.087315 | 0.042289 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_644_0_load_161 | 89 | 0.32502 | 0.15742 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_644_0_load_162 | 91 | 0.4021 | 0.19475 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_644_0_load_54 | 92 | 0.21058 | 0.10199 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_644_0_load_45 | 94 | 0.37841 | 0.18327 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_644_0_load_159 | 98 | 0.38415 | 0.18605 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_644_0_load_152 | 99 | 0.27622 | 0.13378 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_644_0_load_50 | 102 | 0.34817 | 0.16862 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_644_0_load_59 | 105 | 0.29067 | 0.14078 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_644_0_load_70 | 108 | 0.22519 | 0.10906 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_644_0_load_148 | 112 | 0.072327 | 0.035029 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_644_0_load_76 | 113 | 0.23522 | 0.11392 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_644_0_load_147 | 118 | 0.07948 | 0.038494 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_644_0_load_150 | 119 | 0.30973 | 0.15001 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_644_0_load_100 | 122 | 0.32952 | 0.15959 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_644_0_load_142 | 124 | 0.073449 | 0.035573 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_644_0_load_144 | 126 | 0.20854 | 0.101 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_644_0_load_164 | 128 | 0.40834 | 0.19777 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_644_0_load_149 | 130 | 0.2287 | 0.11076 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_644_0_load_81 | 131 | 0.3889 | 0.18835 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_644_0_load_146 | 138 | 0.10203 | 0.049416 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_644_0_load_97 | 139 | 0.29501 | 0.14288 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_644_0_load_151 | 140 | 0.33384 | 0.16168 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_644_0_load_145 | 141 | 0.099542 | 0.048211 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_644_0_load_99 | 142 | 0.27628 | 0.13381 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_644_0_load_89 | 144 | 0.25462 | 0.12332 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_644_0_load_157 | 146 | 0.38783 | 0.18784 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_644_0_load_158 | 150 | 0.32844 | 0.15907 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_644_0_load_156 | 151 | 0.41317 | 0.20011 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_644_0_load_94 | 152 | 0.30792 | 0.14913 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_644_0_load_102 | 154 | 0.27378 | 0.1326 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_644_0_load_123 | 155 | 0.41097 | 0.19904 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_644_0_load_165 | 156 | 0.10462 | 0.050669 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_644_0_load_129 | 159 | 0.083609 | 0.040494 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_644_0_load_135 | 160 | 0.24743 | 0.11984 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_644_0_line_0 |  | 0 | 1 | 0.008199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_644_0_line_1 |  | 1 | 2 | 0.12052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_644_0_line_2 |  | 2 | 3 | 0.008658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_644_0_line_3 |  | 2 | 4 | 0.21163 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
4 | MV_644_0_line_4 |  | 2 | 5 | 0.45217 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
5 | MV_644_0_line_5 |  | 4 | 9 | 0.021219 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
6 | MV_644_0_line_6 |  | 4 | 6 | 0.2002 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
7 | MV_644_0_line_7 |  | 5 | 22 | 0.040256 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_644_0_line_8 |  | 5 | 23 | 0.045923 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
9 | MV_644_0_line_9 |  | 6 | 7 | 0.005914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_644_0_line_10 |  | 6 | 8 | 0.083943 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
11 | MV_644_0_line_11 |  | 8 | 24 | 0.050692 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
12 | MV_644_0_line_12 |  | 9 | 25 | 0.050552 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
13 | MV_644_0_line_13 |  | 10 | 11 | 0.10792 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_644_0_line_14 |  | 10 | 12 | 0.14379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_644_0_line_15 |  | 10 | 13 | 0.005273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_644_0_line_16 |  | 11 | 26 | 0.16154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_644_0_line_17 |  | 11 | 27 | 0.057649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_644_0_line_18 |  | 12 | 14 | 0.013636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_644_0_line_19 |  | 15 | 16 | 0.13561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_644_0_line_20 |  | 15 | 17 | 0.019075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_644_0_line_21 |  | 16 | 18 | 0.11171 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_644_0_line_22 |  | 16 | 19 | 0.11046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_644_0_line_23 |  | 16 | 20 | 0.055909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_644_0_line_24 |  | 18 | 57 | 0.036753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_644_0_line_25 |  | 19 | 21 | 0.005107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_644_0_line_26 |  | 21 | 36 | 0.1019 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_644_0_line_27 |  | 21 | 35 | 0.03437 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_644_0_line_28 |  | 22 | 155 | 0.007668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_644_0_line_29 |  | 23 | 60 | 0.010359 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
30 | MV_644_0_line_30 |  | 24 | 98 | 0.004123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_644_0_line_31 |  | 24 | 96 | 0.044007 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
32 | MV_644_0_line_32 |  | 25 | 82 | 0.002462 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_644_0_line_33 |  | 26 | 30 | 0.019204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_644_0_line_34 |  | 26 | 28 | 0.10222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_644_0_line_35 |  | 27 | 107 | 0.062831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_644_0_line_36 |  | 28 | 29 | 0.028369 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_644_0_line_37 |  | 31 | 32 | 0.003869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_644_0_line_38 |  | 31 | 33 | 0.1794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_644_0_line_39 |  | 32 | 34 | 0.12692 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_644_0_line_40 |  | 33 | 35 | 0.07385 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_644_0_line_41 |  | 34 | 47 | 0.004063 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
42 | MV_644_0_line_42 |  | 36 | 37 | 0.077842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_644_0_line_43 |  | 36 | 38 | 0.043072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_644_0_line_44 |  | 37 | 39 | 0.052378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_644_0_line_45 |  | 40 | 41 | 0.059654 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_644_0_line_46 |  | 40 | 42 | 0.079804 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_644_0_line_47 |  | 40 | 43 | 0.034896 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_644_0_line_48 |  | 41 | 52 | 0.0070371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_644_0_line_49 |  | 41 | 53 | 0.24096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_644_0_line_50 |  | 42 | 56 | 0.0065902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_644_0_line_51 |  | 44 | 45 | 0.007672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_644_0_line_52 |  | 44 | 46 | 0.21081 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_644_0_line_53 |  | 46 | 49 | 0.095913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_644_0_line_54 |  | 46 | 50 | 0.033815 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
55 | MV_644_0_line_55 |  | 46 | 47 | 0.15295 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
56 | MV_644_0_line_56 |  | 47 | 48 | 0.2085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_644_0_line_57 |  | 48 | 51 | 0.055736 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_644_0_line_58 |  | 49 | 105 | 0.006767 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_644_0_line_59 |  | 50 | 88 | 0.087441 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
60 | MV_644_0_line_60 |  | 53 | 54 | 0.17563 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_644_0_line_61 |  | 53 | 55 | 0.048833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_644_0_line_62 |  | 54 | 156 | 0.055127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_644_0_line_63 |  | 55 | 57 | 0.088473 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_644_0_line_64 |  | 58 | 59 | 0.014023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_644_0_line_65 |  | 59 | 60 | 0.12264 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
66 | MV_644_0_line_66 |  | 59 | 61 | 0.09983 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
67 | MV_644_0_line_67 |  | 61 | 62 | 0.007034 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
68 | MV_644_0_line_68 |  | 62 | 63 | 0.027918 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
69 | MV_644_0_line_69 |  | 63 | 148 | 0.024732 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
70 | MV_644_0_line_70 |  | 64 | 65 | 0.041475 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_644_0_line_71 |  | 65 | 66 | 0.20163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_644_0_line_72 |  | 66 | 73 | 0.013081 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
73 | MV_644_0_line_73 |  | 66 | 69 | 0.11455 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
74 | MV_644_0_line_74 |  | 67 | 68 | 0.02509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_644_0_line_75 |  | 67 | 69 | 0.14753 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_644_0_line_76 |  | 67 | 70 | 0.006502 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_644_0_line_77 |  | 69 | 71 | 0.35874 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_644_0_line_78 |  | 69 | 72 | 0.089826 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_644_0_line_79 |  | 70 | 75 | 0.049209 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_644_0_line_80 |  | 71 | 74 | 0.029573 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_644_0_line_81 |  | 72 | 76 | 0.05447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_644_0_line_82 |  | 73 | 77 | 0.021374 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_644_0_line_83 |  | 74 | 78 | 0.00096059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_644_0_line_84 |  | 75 | 104 | 0.037013 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
85 | MV_644_0_line_85 |  | 77 | 93 | 0.065918 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
86 | MV_644_0_line_86 |  | 79 | 80 | 0.002081 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
87 | MV_644_0_line_87 |  | 80 | 81 | 0.09945 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
88 | MV_644_0_line_88 |  | 81 | 83 | 0.055639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_644_0_line_89 |  | 81 | 82 | 0.01266 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
90 | MV_644_0_line_90 |  | 84 | 85 | 0.008143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_644_0_line_91 |  | 85 | 86 | 0.13031 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
92 | MV_644_0_line_92 |  | 85 | 87 | 0.059261 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_644_0_line_93 |  | 86 | 89 | 0.16581 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
94 | MV_644_0_line_94 |  | 87 | 92 | 0.014051 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_644_0_line_95 |  | 88 | 92 | 0.02563 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
96 | MV_644_0_line_96 |  | 89 | 93 | 0.030052 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
97 | MV_644_0_line_97 |  | 89 | 90 | 0.038246 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_644_0_line_98 |  | 90 | 91 | 0.077871 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_644_0_line_99 |  | 94 | 95 | 0.042278 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_644_0_line_100 |  | 94 | 96 | 0.020145 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
101 | MV_644_0_line_101 |  | 95 | 97 | 0.24746 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
102 | MV_644_0_line_102 |  | 97 | 99 | 0.0663 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
103 | MV_644_0_line_103 |  | 99 | 100 | 0.034518 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
104 | MV_644_0_line_104 |  | 99 | 101 | 0.022417 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_644_0_line_105 |  | 100 | 103 | 0.038234 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
106 | MV_644_0_line_106 |  | 101 | 160 | 0.008894 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_644_0_line_107 |  | 102 | 103 | 0.063416 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_644_0_line_108 |  | 103 | 104 | 0.058158 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
109 | MV_644_0_line_109 |  | 105 | 106 | 0.057906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_644_0_line_110 |  | 106 | 107 | 0.022885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_644_0_line_111 |  | 108 | 109 | 0.041411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_644_0_line_112 |  | 109 | 110 | 0.10645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_644_0_line_113 |  | 110 | 111 | 0.034629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_644_0_line_114 |  | 110 | 112 | 0.036275 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_644_0_line_115 |  | 111 | 113 | 0.03799 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_644_0_line_116 |  | 112 | 121 | 0.10364 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_644_0_line_117 |  | 112 | 122 | 0.077936 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_644_0_line_118 |  | 113 | 123 | 0.004938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_644_0_line_119 |  | 114 | 115 | 0.11447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_644_0_line_120 |  | 114 | 116 | 0.058049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_644_0_line_121 |  | 114 | 117 | 0.040876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_644_0_line_122 |  | 114 | 118 | 0.012154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_644_0_line_123 |  | 115 | 119 | 0.005606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_644_0_line_124 |  | 115 | 120 | 0.077813 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
125 | MV_644_0_line_125 |  | 116 | 124 | 0.017698 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_644_0_line_126 |  | 116 | 125 | 0.1073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_644_0_line_127 |  | 117 | 126 | 0.014742 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_644_0_line_128 |  | 118 | 127 | 0.020893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_644_0_line_129 |  | 120 | 128 | 0.008178 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_644_0_line_130 |  | 120 | 123 | 0.11663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_644_0_line_131 |  | 121 | 130 | 0.0062667 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
132 | MV_644_0_line_132 |  | 125 | 140 | 0.014647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_644_0_line_133 |  | 125 | 132 | 0.051103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_644_0_line_134 |  | 127 | 153 | 0.017773 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_644_0_line_135 |  | 128 | 129 | 0.080667 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_644_0_line_136 |  | 129 | 154 | 0.03763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_644_0_line_137 |  | 131 | 132 | 0.007941 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_644_0_line_138 |  | 131 | 133 | 0.010897 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
139 | MV_644_0_line_139 |  | 132 | 134 | 0.13349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_644_0_line_140 |  | 133 | 135 | 0.022408 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
141 | MV_644_0_line_141 |  | 134 | 136 | 0.21811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_644_0_line_142 |  | 134 | 137 | 0.12928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_644_0_line_143 |  | 135 | 141 | 0.021725 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
144 | MV_644_0_line_144 |  | 136 | 138 | 0.044619 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_644_0_line_145 |  | 136 | 139 | 0.063676 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_644_0_line_146 |  | 137 | 142 | 0.00915 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_644_0_line_147 |  | 141 | 143 | 0.04927 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
148 | MV_644_0_line_148 |  | 143 | 150 | 0.15133 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
149 | MV_644_0_line_149 |  | 144 | 145 | 0.024315 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
150 | MV_644_0_line_150 |  | 144 | 146 | 0.065714 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
151 | MV_644_0_line_151 |  | 144 | 147 | 0.064366 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
152 | MV_644_0_line_152 |  | 145 | 148 | 0.064336 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
153 | MV_644_0_line_153 |  | 147 | 149 | 0.12352 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
154 | MV_644_0_line_154 |  | 148 | 151 | 0.034609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_644_0_line_155 |  | 149 | 150 | 0.078412 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
156 | MV_644_0_line_156 |  | 152 | 153 | 0.027168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_644_0_line_157 |  | 155 | 157 | 0.036914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_644_0_line_158 |  | 157 | 158 | 0.12706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_644_0_line_159 |  | 158 | 159 | 0.019045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_644_0_trafo_33 | 25 MVA 110/20 kV | 161 | 79 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2499537.3476 | 1115616.9948
1 | 2499536.9817 | 1115625.1837
2 | 2499536.18 | 1115725.2265
3 | 2499527.6604 | 1115723.7114
4 | 2499678.0923 | 1115654.0722
5 | 2499442.4917 | 1115972.1597
6 | 2499641.0257 | 1115830.9422
7 | 2499635.236 | 1115829.6596
8 | 2499724.8924 | 1115834.5098
9 | 2499699.0861 | 1115657.1549
10 | 2499886.6746 | 1115564.6955
11 | 2499961.6189 | 1115580.4773
12 | 2499886.1677 | 1115472.0236
13 | 2499891.9541 | 1115565.0084
14 | 2499892.4916 | 1115484.1044
15 | 2499414.5205 | 1115497.9268
16 | 2499383.9178 | 1115422.3547
17 | 2499433.5363 | 1115499.4226
18 | 2499301.0966 | 1115347.4294
19 | 2499454.3965 | 1115421.5607
20 | 2499359.3442 | 1115381.4802
21 | 2499457.2203 | 1115419.4226
22 | 2499457.6321 | 1116009.187
23 | 2499487.9271 | 1115966.8589
24 | 2499764.1047 | 1115866.6359
25 | 2499749.1017 | 1115664.5021
26 | 2500065.2127 | 1115570.0815
27 | 2499976.0184 | 1115527.5305
28 | 2500043.6086 | 1115635.2235
29 | 2500047.9485 | 1115663.2583
30 | 2500075.7438 | 1115561.0687
31 | 2499692.218 | 1115466.0535
32 | 2499696.0577 | 1115466.6124
33 | 2499552.6593 | 1115452.2817
34 | 2499766.3264 | 1115360.9153
35 | 2499479.0816 | 1115445.9437
36 | 2499497.9087 | 1115326.0002
37 | 2499479.9075 | 1115277.7021
38 | 2499501.5359 | 1115283.0908
39 | 2499505.6095 | 1115232.0637
40 | 2499380.5552 | 1115050.7549
41 | 2499339.0875 | 1115062.6741
42 | 2499357.4128 | 1115007.3457
43 | 2499406.0795 | 1115074.5509
44 | 2499754.2214 | 1115204.5955
45 | 2499747.5923 | 1115201.6256
46 | 2499918.5024 | 1115336.704
47 | 2499766.893 | 1115356.8923
48 | 2499698.0174 | 1115236.9136
49 | 2499955.0089 | 1115418.4962
50 | 2499941.1714 | 1115311.6493
51 | 2499642.8455 | 1115229.001
52 | 2499333.8159 | 1115058.0124
53 | 2499361.4988 | 1115236.2104
54 | 2499477.9413 | 1115140.3374
55 | 2499397.8052 | 1115268.8673
56 | 2499363.5718 | 1115007.5656
57 | 2499325.6842 | 1115320.112
58 | 2499552.7744 | 1116054.8357
59 | 2499540.0553 | 1116049.1766
60 | 2499498.259 | 1115966.1073
61 | 2499571.2855 | 1116092.6188
62 | 2499578.3186 | 1116092.0684
63 | 2499606.1877 | 1116089.3599
64 | 2500368.0431 | 1115606.0222
65 | 2500326.8821 | 1115611.1143
66 | 2500186.8561 | 1115651.5362
67 | 2500061.2465 | 1115726.8341
68 | 2500069.1134 | 1115750.6462
69 | 2500186.046 | 1115665.6139
70 | 2500055.2178 | 1115729.313
71 | 2500107.7426 | 1115767.0916
72 | 2500103.6292 | 1115701.1574
73 | 2500175.3243 | 1115645.3003
74 | 2500081.5092 | 1115778.3832
75 | 2500009.6039 | 1115747.7759
76 | 2500053.1449 | 1115721.6094
77 | 2500172.254 | 1115624.4379
78 | 2500080.6001 | 1115778.6935
79 | 2499747.6189 | 1115746.9561
80 | 2499747.9014 | 1115744.8946
81 | 2499758.8582 | 1115665.6301
82 | 2499748.7792 | 1115666.9423
83 | 2499814.0397 | 1115673.9104
84 | 2500096.8374 | 1115333.1332
85 | 2500103.8518 | 1115329.0593
86 | 2500205.1539 | 1115377.4851
87 | 2500053.9589 | 1115297.4855
88 | 2500028.611 | 1115312.0395
89 | 2500172.2348 | 1115539.9964
90 | 2500154.2787 | 1115506.2271
91 | 2500213.5652 | 1115455.7399
92 | 2500041.9657 | 1115290.1638
93 | 2500169.7483 | 1115569.9451
94 | 2499808.9673 | 1115894.9329
95 | 2499826.0695 | 1115933.5073
96 | 2499793.2603 | 1115882.3184
97 | 2499909.2772 | 1115881.0199
98 | 2499761.9623 | 1115870.1625
99 | 2499925.6508 | 1115816.7978
100 | 2499934.2877 | 1115783.4118
101 | 2499948.0554 | 1115816.038
102 | 2499897.4549 | 1115704.6605
103 | 2499926.6037 | 1115760.9804
104 | 2499975.2874 | 1115761.6426
105 | 2499958.4799 | 1115424.3091
106 | 2499978.8245 | 1115455.8037
107 | 2499962.1387 | 1115468.5652
108 | 2500141.9956 | 1116089.1835
109 | 2500120.2079 | 1116124.4318
110 | 2500054.7445 | 1116095.0498
111 | 2500027.236 | 1116106.5002
112 | 2500046.192 | 1116059.7971
113 | 2499990.1705 | 1116114.829
114 | 2500037.6843 | 1116317.7043
115 | 2500052.4784 | 1116213.5058
116 | 2500030.0127 | 1116361.8253
117 | 2500048.4037 | 1116357.0741
118 | 2500048.8267 | 1116312.8506
119 | 2500057.1762 | 1116210.4263
120 | 2499974.9452 | 1116206.9161
121 | 2500117.4498 | 1115984.5453
122 | 2499971.5907 | 1116037.243
123 | 2499991.2463 | 1116119.6476
124 | 2500026.0433 | 1116344.5784
125 | 2499974.3782 | 1116420.5259
126 | 2500062.7535 | 1116353.6946
127 | 2500067.9813 | 1116304.5068
128 | 2499966.9778 | 1116208.8601
129 | 2499888.9449 | 1116188.4155
130 | 2500121.6509 | 1115979.8953
131 | 2499960.8462 | 1116377.7895
132 | 2499968.8003 | 1116377.3911
133 | 2499950.0936 | 1116379.3905
134 | 2499922.9494 | 1116484.6164
135 | 2499936.6194 | 1116382.1595
136 | 2499792.1249 | 1116492.3084
137 | 2499942.5275 | 1116573.5705
138 | 2499778.5905 | 1116534.8254
139 | 2499848.7566 | 1116463.1971
140 | 2499971.2406 | 1116434.8312
141 | 2499915.641 | 1116376.512
142 | 2499940.6682 | 1116582.5291
143 | 2499868.0647 | 1116363.7041
144 | 2499703.0906 | 1116080.681
145 | 2499678.813 | 1116082.9848
146 | 2499708.0887 | 1116015.1571
147 | 2499708.4861 | 1116144.8207
148 | 2499623.2292 | 1116096.7819
149 | 2499723.2291 | 1116224.1261
150 | 2499729.775 | 1116302.2444
151 | 2499625.8558 | 1116131.2822
152 | 2500109.1055 | 1116286.2608
153 | 2500084.4408 | 1116297.8086
154 | 2499900.3041 | 1116152.5384
155 | 2499462.6627 | 1116014.9848
156 | 2499515.9227 | 1115128.7105
157 | 2499435.7993 | 1116040.1136
158 | 2499453.4474 | 1116116.5128
159 | 2499445.1264 | 1116100.9633
160 | 2499956.4134 | 1115812.9312
161 | 2499747.6189 | 1115746.9561

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99903 | -0.0036134 | 0.40329 | 0.19532
1 | 0.99903 | -0.003653 | 0 | 0
2 | 0.9991 | -0.004223 | 0 | 0
3 | 0.99909 | -0.0041801 | 0.41426 | 0.20064
4 | 0.99936 | -0.0029711 | 0 | 0
5 | 0.9986 | -0.0065344 | 0 | 0
6 | 0.99893 | -0.0048305 | 0 | 0
7 | 0.99893 | -0.0048048 | 0.36277 | 0.1757
8 | 0.99858 | -0.024953 | 0.32764 | 0.15868
9 | 0.99943 | -0.0026443 | 0.078998 | 0.038261
10 | 0.99523 | -0.081706 | 0 | 0
11 | 0.9953 | -0.082307 | 0 | 0
12 | 0.99521 | -0.081539 | 0 | 0
13 | 0.99523 | -0.081681 | 0.3818 | 0.18491
14 | 0.99521 | -0.081521 | 0.10683 | 0.051742
15 | 0.99212 | -0.10659 | 0 | 0
16 | 0.99214 | -0.10676 | 0 | 0
17 | 0.99212 | -0.10657 | 0.11372 | 0.055077
18 | 0.99183 | -0.104 | 0 | 0
19 | 0.99248 | -0.10981 | 0 | 0
20 | 0.99213 | -0.10665 | 0.17014 | 0.082401
21 | 0.99249 | -0.10995 | 0.076922 | 0.037255
22 | 0.99857 | -0.0063085 | 0 | 0
23 | 0.99855 | -0.0067436 | 0.080463 | 0.03897
24 | 0.99837 | -0.036799 | 0 | 0
25 | 0.9996 | -0.0018621 | 0.39325 | 0.19046
26 | 0.99521 | -0.081489 | 0 | 0
27 | 0.99537 | -0.082905 | 0.072674 | 0.035198
28 | 0.99517 | -0.081149 | 0 | 0
29 | 0.99515 | -0.081247 | 0.28185 | 0.1365
30 | 0.9952 | -0.081452 | 0.16276 | 0.078828
31 | 0.99396 | -0.11228 | 0 | 0
32 | 0.99398 | -0.11243 | 0.34675 | 0.16794
33 | 0.99319 | -0.10529 | 0 | 0
34 | 0.9949 | -0.10621 | 0.31198 | 0.1511
35 | 0.9927 | -0.10857 | 0.34566 | 0.16741
36 | 0.99238 | -0.11069 | 0 | 0
37 | 0.99236 | -0.11043 | 0 | 0
38 | 0.99237 | -0.11055 | 0.26858 | 0.13008
39 | 0.99234 | -0.11024 | 0.28972 | 0.14032
40 | 0.99143 | -0.10315 | 0 | 0
41 | 0.99144 | -0.10331 | 0 | 0
42 | 0.99141 | -0.10305 | 0 | 0
43 | 0.99142 | -0.1031 | 0.11784 | 0.057071
44 | 0.99563 | -0.08657 | 0 | 0
45 | 0.99562 | -0.086549 | 0.22734 | 0.11011
46 | 0.99572 | -0.085981 | 0 | 0
47 | 0.99491 | -0.10612 | 0 | 0
48 | 0.99481 | -0.10518 | 0 | 0
49 | 0.99556 | -0.084598 | 0 | 0
50 | 0.99575 | -0.085846 | 0.32288 | 0.15638
51 | 0.99477 | -0.10545 | 0.38265 | 0.18533
52 | 0.99144 | -0.1033 | 0.074253 | 0.035962
53 | 0.99154 | -0.1041 | 0 | 0
54 | 0.99151 | -0.10391 | 0 | 0
55 | 0.99156 | -0.10429 | 0.57335 | 0.27768
56 | 0.99141 | -0.10304 | 0.11483 | 0.055616
57 | 0.99173 | -0.10309 | 1.1464 | 0.55523
58 | 0.99842 | -0.0072863 | 0.27376 | 0.13259
59 | 0.99842 | -0.0073322 | 0 | 0
60 | 0.99854 | -0.00679 | 0 | 0
61 | 0.99832 | -0.0077472 | 0 | 0
62 | 0.99832 | -0.0077761 | 0.25975 | 0.1258
63 | 0.99829 | -0.0078861 | 0 | 0
64 | 0.99668 | -0.047406 | 0.27578 | 0.13357
65 | 0.99671 | -0.047266 | 0 | 0
66 | 0.99678 | -0.047905 | 0 | 0
67 | 0.99715 | -0.046309 | 0 | 0
68 | 0.99715 | -0.046264 | 0.14967 | 0.072487
69 | 0.99693 | -0.047255 | 0 | 0
70 | 0.99716 | -0.046266 | 0 | 0
71 | 0.99676 | -0.045728 | 0 | 0
72 | 0.99687 | -0.046705 | 0.10021 | 0.048534
73 | 0.99676 | -0.047975 | 0.41201 | 0.19955
74 | 0.99674 | -0.045593 | 0.12525 | 0.060661
75 | 0.99724 | -0.045941 | 1.3411 | 0.64954
76 | 0.99684 | -0.046432 | 0.42044 | 0.20363
77 | 0.99673 | -0.048086 | 0 | 0
78 | 0.99674 | -0.04559 | 0.25476 | 0.12339
79 | 1 | 0 | -21.4271 | -9.8941
80 | 0.99999 | -3.3375e-05 | 0 | 0
81 | 0.99965 | -0.0016243 | 0 | 0
82 | 0.9996 | -0.0018234 | 0 | 0
83 | 0.99962 | -0.0013849 | 0.36281 | 0.17572
84 | 0.99604 | -0.074908 | 0.23565 | 0.11413
85 | 0.99605 | -0.074931 | 0 | 0
86 | 0.99619 | -0.074327 | 0 | 0
87 | 0.99598 | -0.075192 | 0 | 0
88 | 0.99594 | -0.075362 | 0.087315 | 0.042289
89 | 0.99658 | -0.052746 | 0.32502 | 0.15742
90 | 0.99655 | -0.052934 | 0 | 0
91 | 0.99648 | -0.053315 | 0.4021 | 0.19475
92 | 0.99597 | -0.075253 | 0.21058 | 0.10199
93 | 0.99665 | -0.048423 | 0 | 0
94 | 0.9982 | -0.04174 | 0.37841 | 0.18327
95 | 0.99812 | -0.042094 | 0 | 0
96 | 0.99828 | -0.037178 | 0 | 0
97 | 0.99766 | -0.044133 | 0 | 0
98 | 0.99837 | -0.03678 | 0.38415 | 0.18605
99 | 0.99753 | -0.04467 | 0.27622 | 0.13378
100 | 0.99747 | -0.044937 | 0 | 0
101 | 0.99752 | -0.044738 | 0 | 0
102 | 0.99736 | -0.045501 | 0.34817 | 0.16862
103 | 0.9974 | -0.045232 | 0 | 0
104 | 0.9973 | -0.045666 | 0 | 0
105 | 0.99555 | -0.0845 | 0.29067 | 0.14078
106 | 0.99548 | -0.083861 | 0 | 0
107 | 0.99545 | -0.083607 | 0 | 0
108 | 0.99594 | -0.016943 | 0.22519 | 0.10906
109 | 0.99595 | -0.017054 | 0 | 0
110 | 0.99598 | -0.017328 | 0 | 0
111 | 0.99602 | -0.017674 | 0 | 0
112 | 0.99595 | -0.017053 | 0.072327 | 0.035029
113 | 0.99608 | -0.01726 | 0.23522 | 0.11392
114 | 0.99682 | -0.019853 | 0 | 0
115 | 0.99652 | -0.017062 | 0 | 0
116 | 0.99702 | -0.021665 | 0 | 0
117 | 0.99681 | -0.019753 | 0 | 0
118 | 0.99682 | -0.019798 | 0.07948 | 0.038494
119 | 0.99652 | -0.017041 | 0.30973 | 0.15001
120 | 0.99625 | -0.018806 | 0 | 0
121 | 0.99591 | -0.017343 | 0 | 0
122 | 0.9959 | -0.017366 | 0.32952 | 0.15959
123 | 0.99609 | -0.017323 | 0 | 0
124 | 0.99702 | -0.02165 | 0.073449 | 0.035573
125 | 0.9974 | -0.025091 | 0 | 0
126 | 0.99681 | -0.019716 | 0.20854 | 0.101
127 | 0.99681 | -0.019722 | 0 | 0
128 | 0.99624 | -0.018739 | 0.40834 | 0.19777
129 | 0.9962 | -0.019014 | 0 | 0
130 | 0.9959 | -0.01736 | 0.2287 | 0.11076
131 | 0.99764 | -0.02726 | 0.3889 | 0.18835
132 | 0.9976 | -0.026919 | 0 | 0
133 | 0.99766 | -0.026997 | 0 | 0
134 | 0.99748 | -0.025934 | 0 | 0
135 | 0.99768 | -0.026937 | 0 | 0
136 | 0.99737 | -0.024944 | 0 | 0
137 | 0.99744 | -0.025519 | 0 | 0
138 | 0.99737 | -0.024891 | 0.10203 | 0.049416
139 | 0.99734 | -0.025173 | 0.29501 | 0.14288
140 | 0.99739 | -0.025032 | 0.33384 | 0.16168
141 | 0.99769 | -0.026878 | 0.099542 | 0.048211
142 | 0.99744 | -0.025489 | 0.27628 | 0.13381
143 | 0.99772 | -0.026739 | 0 | 0
144 | 0.99819 | -0.0083035 | 0.25462 | 0.12332
145 | 0.99821 | -0.0082163 | 0 | 0
146 | 0.99814 | -0.0086128 | 0.38783 | 0.18784
147 | 0.99809 | -0.013905 | 0 | 0
148 | 0.99827 | -0.0079829 | 0 | 0
149 | 0.998 | -0.014294 | 0 | 0
150 | 0.99794 | -0.014534 | 0.32844 | 0.15907
151 | 0.99825 | -0.0078121 | 0.41317 | 0.20011
152 | 0.99679 | -0.019557 | 0.30792 | 0.14913
153 | 0.9968 | -0.019657 | 0 | 0
154 | 0.99619 | -0.018891 | 0.27378 | 0.1326
155 | 0.99857 | -0.0062652 | 0.41097 | 0.19904
156 | 0.99151 | -0.10384 | 0.10462 | 0.050669
157 | 0.99857 | -0.0062374 | 0 | 0
158 | 0.99855 | -0.0061259 | 0 | 0
159 | 0.99855 | -0.0061071 | 0.083609 | 0.040494
160 | 0.99752 | -0.044711 | 0.24743 | 0.11984
161 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.40329 | -0.19532 | 0.40329 | 0.19513 | 1.8347e-06 | -0.00019484 | 0.012948 | 0.012946 | 0.012948 | 0.99903 | -0.0036134 | 0.99903 | -0.003653 | 5.8855
1 | -0.40329 | -0.19513 | 0.40332 | 0.19226 | 2.689e-05 | -0.0028643 | 0.012946 | 0.01291 | 0.012946 | 0.99903 | -0.003653 | 0.9991 | -0.004223 | 5.8844
2 | 0.41427 | 0.20043 | -0.41426 | -0.20064 | 2.0441e-06 | -0.00020574 | 0.013297 | 0.0133 | 0.0133 | 0.9991 | -0.004223 | 0.99909 | -0.0041801 | 6.0453
3 | -7.5695 | -3.475 | 7.5714 | 3.4496 | 0.0018912 | -0.025489 | 0.24066 | 0.24034 | 0.24066 | 0.9991 | -0.004223 | 0.99936 | -0.0029711 | 18.8603
4 | 6.7519 | 3.0823 | -6.7487 | -3.1372 | 0.0032232 | -0.054876 | 0.21446 | 0.21514 | 0.21514 | 0.9991 | -0.004223 | 0.9986 | -0.0065344 | 16.8606
5 | -20.5649 | -9.4968 | 20.5663 | 9.4949 | 0.0014035 | -0.0018729 | 0.65432 | 0.65429 | 0.65432 | 0.99936 | -0.0029711 | 0.99943 | -0.0026443 | 51.2793
6 | 12.9935 | 6.0472 | -12.9882 | -6.0694 | 0.0053051 | -0.022127 | 0.41399 | 0.4143 | 0.4143 | 0.99936 | -0.0029711 | 0.99893 | -0.0048305 | 32.4684
7 | 0.49459 | 0.23404 | -0.49458 | -0.23499 | 1.3456e-05 | -0.00095445 | 0.015818 | 0.015829 | 0.015829 | 0.9986 | -0.0065344 | 0.99857 | -0.0063085 | 7.1952
8 | 6.2541 | 2.9032 | -6.2538 | -2.9088 | 0.00028199 | -0.0055956 | 0.19932 | 0.19939 | 0.19939 | 0.9986 | -0.0065344 | 0.99855 | -0.0067436 | 15.6265
9 | 0.36277 | 0.17556 | -0.36277 | -0.1757 | 1.0711e-06 | -0.00014058 | 0.011647 | 0.011648 | 0.011648 | 0.99893 | -0.0048305 | 0.99893 | -0.0048048 | 5.2947
10 | 12.6254 | 5.8938 | -12.623 | -5.8875 | 0.0024293 | 0.0063011 | 0.40265 | 0.40265 | 0.40265 | 0.99893 | -0.0048305 | 0.99858 | -0.024953 | 31.2135
11 | 12.2954 | 5.7288 | -12.294 | -5.7252 | 0.0013914 | 0.0036018 | 0.39213 | 0.39213 | 0.39213 | 0.99858 | -0.024953 | 0.99837 | -0.036799 | 30.3979
12 | -20.6453 | -9.5332 | 20.6487 | 9.5287 | 0.0033691 | -0.0044492 | 0.65683 | 0.65675 | 0.65683 | 0.99943 | -0.0026443 | 0.9996 | -0.0018621 | 51.4754
13 | -0.48863 | -0.23281 | 0.48867 | 0.23027 | 3.5438e-05 | -0.0025417 | 0.0157 | 0.015668 | 0.0157 | 0.99523 | -0.081706 | 0.9953 | -0.082307 | 7.1362
14 | 0.10684 | 0.04802 | -0.10683 | -0.05142 | 2.2427e-06 | -0.0033999 | 0.0033975 | 0.0034391 | 0.0034391 | 0.99523 | -0.081706 | 0.99521 | -0.081539 | 1.5632
15 | 0.3818 | 0.18479 | -0.3818 | -0.18491 | 1.0657e-06 | -0.00012438 | 0.012303 | 0.012305 | 0.012305 | 0.99523 | -0.081706 | 0.99523 | -0.081681 | 5.5931
16 | 0.44467 | 0.20863 | -0.44462 | -0.21243 | 4.3913e-05 | -0.0038074 | 0.014246 | 0.014293 | 0.014293 | 0.9953 | -0.082307 | 0.99521 | -0.081489 | 6.497
17 | -0.93334 | -0.43889 | 0.93341 | 0.43755 | 6.8831e-05 | -0.0013432 | 0.029914 | 0.029897 | 0.029914 | 0.9953 | -0.082307 | 0.99537 | -0.082905 | 13.5973
18 | 0.10683 | 0.05142 | -0.10683 | -0.051742 | 2.1556e-07 | -0.0003224 | 0.0034391 | 0.0034432 | 0.0034432 | 0.99521 | -0.081539 | 0.99521 | -0.081521 | 1.5651
19 | -0.11372 | -0.054629 | 0.11372 | 0.051443 | 2.4133e-06 | -0.0031863 | 0.0036709 | 0.0036317 | 0.0036709 | 0.99212 | -0.10659 | 0.99214 | -0.10676 | 1.6686
20 | 0.11372 | 0.054629 | -0.11372 | -0.055077 | 3.4367e-07 | -0.00044817 | 0.0036709 | 0.0036766 | 0.0036766 | 0.99212 | -0.10659 | 0.99212 | -0.10657 | 1.6712
21 | 2.1324 | 1.0124 | -2.1317 | -1.0148 | 0.00070387 | -0.0024159 | 0.068684 | 0.068716 | 0.068716 | 0.99214 | -0.10676 | 0.99183 | -0.104 | 31.2347
22 | -2.4163 | -1.1449 | 2.4172 | 1.1426 | 0.00089218 | -0.0023323 | 0.077799 | 0.077766 | 0.077799 | 0.99214 | -0.10676 | 0.99248 | -0.10981 | 35.363
23 | 0.17014 | 0.081088 | -0.17014 | -0.082401 | 2.2514e-06 | -0.0013133 | 0.0054839 | 0.0055005 | 0.0055005 | 0.99214 | -0.10676 | 0.99213 | -0.10665 | 2.5002
24 | 2.1317 | 1.0148 | -2.1315 | -1.0156 | 0.00023172 | -0.00079442 | 0.068716 | 0.068727 | 0.068727 | 0.99183 | -0.104 | 0.99173 | -0.10309 | 31.2396
25 | -2.4172 | -1.1426 | 2.4172 | 1.1425 | 4.1231e-05 | -0.00010788 | 0.077766 | 0.077765 | 0.077766 | 0.99248 | -0.10981 | 0.99249 | -0.10995 | 35.3483
26 | 0.55838 | 0.26624 | -0.55832 | -0.26633 | 5.8779e-05 | -8.2997e-05 | 0.017993 | 0.017994 | 0.017994 | 0.99249 | -0.10995 | 0.99238 | -0.11069 | 8.5686
27 | -3.0525 | -1.446 | 3.0531 | 1.4463 | 0.00059104 | 0.00032978 | 0.098243 | 0.098243 | 0.098243 | 0.99249 | -0.10995 | 0.9927 | -0.10857 | 46.7824
28 | 0.49458 | 0.23499 | -0.49458 | -0.23518 | 2.5654e-06 | -0.0001818 | 0.015829 | 0.015832 | 0.015832 | 0.99857 | -0.0063085 | 0.99857 | -0.0062652 | 7.1963
29 | 6.1734 | 2.8698 | -6.1733 | -2.8711 | 6.1999e-05 | -0.0012631 | 0.19681 | 0.19683 | 0.19683 | 0.99855 | -0.0067436 | 0.99854 | -0.00679 | 15.4252
30 | 0.38415 | 0.18595 | -0.38415 | -0.18605 | 8.3834e-07 | -9.7871e-05 | 0.012341 | 0.012342 | 0.012342 | 0.99837 | -0.036799 | 0.99837 | -0.03678 | 5.6099
31 | 11.9098 | 5.5393 | -11.9088 | -5.5442 | 0.00098089 | -0.0049592 | 0.37979 | 0.37986 | 0.37986 | 0.99837 | -0.036799 | 0.99828 | -0.037178 | 29.7697
32 | -21.0419 | -9.7192 | 21.0421 | 9.719 | 0.00017043 | -0.00021317 | 0.66937 | 0.66936 | 0.66937 | 0.9996 | -0.0018621 | 0.9996 | -0.0018234 | 52.4581
33 | 0.16276 | 0.078374 | -0.16276 | -0.078828 | 7.047e-07 | -0.00045392 | 0.00524 | 0.0052457 | 0.0052457 | 0.99521 | -0.081489 | 0.9952 | -0.081452 | 2.3844
34 | 0.28186 | 0.13406 | -0.28185 | -0.13647 | 1.1223e-05 | -0.0024138 | 0.0090535 | 0.0090838 | 0.0090838 | 0.99521 | -0.081489 | 0.99517 | -0.081149 | 4.129
35 | -1.0061 | -0.47275 | 1.0062 | 0.47129 | 8.7131e-05 | -0.0014606 | 0.032239 | 0.032221 | 0.032239 | 0.99537 | -0.082905 | 0.99545 | -0.083607 | 14.6541
36 | 0.28185 | 0.13647 | -0.28185 | -0.1365 | 4.1709e-06 | -3.0927e-05 | 0.0090838 | 0.0090843 | 0.0090843 | 0.99517 | -0.081149 | 0.99515 | -0.081247 | 4.3258
37 | -3.4032 | -1.6113 | 3.4033 | 1.6112 | 6.1769e-05 | -7.2944e-05 | 0.10936 | 0.10936 | 0.10936 | 0.99396 | -0.11228 | 0.99398 | -0.11243 | 49.7078
38 | 3.4032 | 1.6113 | -3.4004 | -1.6146 | 0.0028656 | -0.0033786 | 0.10936 | 0.10941 | 0.10941 | 0.99396 | -0.11228 | 0.99319 | -0.10529 | 49.7317
39 | -3.75 | -1.7791 | 3.7533 | 1.781 | 0.003286 | 0.0019084 | 0.12054 | 0.12054 | 0.12054 | 0.99398 | -0.11243 | 0.9949 | -0.10621 | 57.4023
40 | 3.4004 | 1.6146 | -3.3988 | -1.6137 | 0.0015751 | 0.00089966 | 0.10941 | 0.10941 | 0.10941 | 0.99319 | -0.10529 | 0.9927 | -0.10857 | 52.1004
41 | -4.0653 | -1.9321 | 4.0653 | 1.932 | 3.3472e-05 | -0.00011365 | 0.1306 | 0.1306 | 0.1306 | 0.9949 | -0.10621 | 0.99491 | -0.10612 | 36.0776
42 | 0.28973 | 0.13726 | -0.28972 | -0.13909 | 9.0603e-06 | -0.0018276 | 0.0093259 | 0.0093488 | 0.0093488 | 0.99238 | -0.11069 | 0.99236 | -0.11043 | 4.2495
43 | 0.26859 | 0.12907 | -0.26858 | -0.13008 | 4.3269e-06 | -0.0010115 | 0.0086682 | 0.008681 | 0.008681 | 0.99238 | -0.11069 | 0.99237 | -0.11055 | 3.9459
44 | 0.28972 | 0.13909 | -0.28972 | -0.14032 | 6.1216e-06 | -0.0012297 | 0.0093488 | 0.0093644 | 0.0093644 | 0.99236 | -0.11043 | 0.99234 | -0.11024 | 4.2565
45 | -0.23267 | -0.10984 | 0.23268 | 0.10844 | 4.4594e-06 | -0.0013987 | 0.0074917 | 0.0074744 | 0.0074917 | 0.99143 | -0.10315 | 0.99144 | -0.10331 | 3.4053
46 | 0.11483 | 0.053589 | -0.11483 | -0.055461 | 1.4596e-06 | -0.0018724 | 0.0036898 | 0.0037132 | 0.0037132 | 0.99143 | -0.10315 | 0.99141 | -0.10305 | 1.6878
47 | 0.11784 | 0.056252 | -0.11784 | -0.057071 | 6.7524e-07 | -0.00081875 | 0.003802 | 0.0038123 | 0.0038123 | 0.99143 | -0.10315 | 0.99142 | -0.1031 | 1.7329
48 | 0.074253 | 0.035797 | -0.074253 | -0.035962 | 5.4165e-08 | -0.00016514 | 0.0024001 | 0.0024022 | 0.0024022 | 0.99144 | -0.10331 | 0.99144 | -0.1033 | 1.0919
49 | -0.30693 | -0.14424 | 0.30696 | 0.13859 | 3.1145e-05 | -0.0056465 | 0.0098744 | 0.0098055 | 0.0098744 | 0.99144 | -0.10331 | 0.99154 | -0.1041 | 4.4883
50 | 0.11483 | 0.055461 | -0.11483 | -0.055616 | 1.2136e-07 | -0.00015462 | 0.0037132 | 0.0037152 | 0.0037152 | 0.99141 | -0.10305 | 0.99141 | -0.10304 | 1.6887
51 | 0.22734 | 0.10992 | -0.22734 | -0.11011 | 5.4922e-07 | -0.00018142 | 0.0073216 | 0.0073239 | 0.0073239 | 0.99563 | -0.08657 | 0.99562 | -0.086549 | 3.3291
52 | -0.22734 | -0.10992 | 0.22736 | 0.10969 | 2.0126e-05 | -0.00023689 | 0.0073216 | 0.0073185 | 0.0073216 | 0.99563 | -0.08657 | 0.99572 | -0.085981 | 3.4865
53 | 1.2972 | 0.60783 | -1.297 | -0.61003 | 0.00022101 | -0.0022046 | 0.041531 | 0.041559 | 0.041559 | 0.99572 | -0.085981 | 0.99556 | -0.084598 | 18.8906
54 | -5.9755 | -2.833 | 5.9756 | 2.8289 | 0.00019198 | -0.0041051 | 0.19172 | 0.19167 | 0.19172 | 0.99572 | -0.085981 | 0.99575 | -0.085846 | 15.0252
55 | 4.4509 | 2.1155 | -4.448 | -2.1124 | 0.0028661 | 0.0030878 | 0.14287 | 0.14287 | 0.14287 | 0.99572 | -0.085981 | 0.99491 | -0.10612 | 40.8213
56 | 0.38271 | 0.18035 | -0.38266 | -0.18527 | 4.2154e-05 | -0.0049147 | 0.012276 | 0.012337 | 0.012337 | 0.99491 | -0.10612 | 0.99481 | -0.10518 | 5.6078
57 | 0.38266 | 0.18527 | -0.38265 | -0.18533 | 1.5116e-05 | -5.6379e-05 | 0.012337 | 0.012338 | 0.012338 | 0.99481 | -0.10518 | 0.99477 | -0.10545 | 5.8752
58 | 1.297 | 0.61003 | -1.297 | -0.61019 | 1.5604e-05 | -0.00015551 | 0.041559 | 0.041561 | 0.041561 | 0.99556 | -0.084598 | 0.99555 | -0.0845 | 18.8915
59 | -6.2985 | -2.9852 | 6.2992 | 2.9867 | 0.0006373 | 0.001474 | 0.20207 | 0.20207 | 0.20207 | 0.99575 | -0.085846 | 0.99594 | -0.075362 | 15.6643
60 | 0.10462 | 0.045253 | -0.10462 | -0.049375 | 2.6202e-06 | -0.0041218 | 0.0033187 | 0.0033681 | 0.0033681 | 0.99154 | -0.1041 | 0.99151 | -0.10391 | 1.531
61 | -0.41158 | -0.18385 | 0.41159 | 0.1827 | 1.1217e-05 | -0.001143 | 0.013124 | 0.01311 | 0.013124 | 0.99154 | -0.1041 | 0.99156 | -0.10429 | 5.9654
62 | 0.10462 | 0.049375 | -0.10462 | -0.050669 | 8.3888e-07 | -0.0012937 | 0.0033681 | 0.0033844 | 0.0033844 | 0.99151 | -0.10391 | 0.99151 | -0.10384 | 1.5384
63 | -0.98494 | -0.46039 | 0.9851 | 0.46038 | 0.00015792 | -4.9449e-06 | 0.031653 | 0.031651 | 0.031653 | 0.99156 | -0.10429 | 0.99173 | -0.10309 | 15.0726
64 | -0.27376 | -0.13259 | 0.27376 | 0.13225 | 1.4473e-06 | -0.00033333 | 0.0087947 | 0.0087905 | 0.0087947 | 0.99842 | -0.0072863 | 0.99842 | -0.0073322 | 3.9976
65 | -6.1726 | -2.886 | 6.1733 | 2.8711 | 0.00073472 | -0.01495 | 0.19701 | 0.19683 | 0.19701 | 0.99842 | -0.0073322 | 0.99854 | -0.00679 | 15.4399
66 | 5.8988 | 2.7538 | -5.8983 | -2.766 | 0.00054688 | -0.012196 | 0.18822 | 0.18838 | 0.18838 | 0.99842 | -0.0073322 | 0.99832 | -0.0077472 | 14.7631
67 | 5.8983 | 2.766 | -5.8982 | -2.7668 | 3.8567e-05 | -0.00085924 | 0.18838 | 0.18839 | 0.18839 | 0.99832 | -0.0077472 | 0.99832 | -0.0077761 | 14.7639
68 | 5.6385 | 2.641 | -5.6384 | -2.6444 | 0.00013985 | -0.0034176 | 0.18004 | 0.18009 | 0.18009 | 0.99832 | -0.0077761 | 0.99829 | -0.0078861 | 14.1133
69 | 5.6384 | 2.6444 | -5.6382 | -2.6475 | 0.00012395 | -0.0030275 | 0.18009 | 0.18012 | 0.18012 | 0.99829 | -0.0078861 | 0.99827 | -0.0079829 | 14.1163
70 | -0.27578 | -0.13357 | 0.27579 | 0.13352 | 5.8203e-06 | -4.5541e-05 | 0.0088752 | 0.0088746 | 0.0088752 | 0.99668 | -0.047406 | 0.99671 | -0.047266 | 4.2263
71 | -0.27579 | -0.13352 | 0.27581 | 0.12875 | 2.1057e-05 | -0.0047766 | 0.0088746 | 0.0088151 | 0.0088746 | 0.99671 | -0.047266 | 0.99678 | -0.047905 | 4.0339
72 | 7.9762 | 3.761 | -7.976 | -3.7625 | 0.00013183 | -0.001559 | 0.25539 | 0.25541 | 0.25541 | 0.99678 | -0.047905 | 0.99676 | -0.047975 | 20.0164
73 | -8.252 | -3.8897 | 8.2532 | 3.8761 | 0.0012346 | -0.013609 | 0.2642 | 0.26403 | 0.2642 | 0.99678 | -0.047905 | 0.99693 | -0.047255 | 20.7056
74 | 0.14967 | 0.071892 | -0.14967 | -0.072487 | 7.7513e-07 | -0.00059542 | 0.0048068 | 0.0048143 | 0.0048143 | 0.99715 | -0.046309 | 0.99715 | -0.046264 | 2.1883
75 | 9.156 | 4.2824 | -9.154 | -4.2997 | 0.0019533 | -0.01733 | 0.29262 | 0.29285 | 0.29285 | 0.99715 | -0.046309 | 0.99693 | -0.047255 | 22.9507
76 | -9.3056 | -4.3543 | 9.3057 | 4.3535 | 8.8865e-05 | -0.00076239 | 0.29743 | 0.29742 | 0.29743 | 0.99715 | -0.046309 | 0.99716 | -0.046266 | 23.3096
77 | 0.38009 | 0.17484 | -0.38002 | -0.18333 | 7.0891e-05 | -0.0084902 | 0.012115 | 0.01222 | 0.01222 | 0.99693 | -0.047255 | 0.99676 | -0.045728 | 5.5544
78 | 0.5207 | 0.24875 | -0.52066 | -0.25087 | 3.3536e-05 | -0.0021215 | 0.01671 | 0.016736 | 0.016736 | 0.99693 | -0.047255 | 0.99687 | -0.046705 | 7.6074
79 | -9.3057 | -4.3535 | 9.3064 | 4.3477 | 0.00067237 | -0.0057706 | 0.29742 | 0.29735 | 0.29742 | 0.99716 | -0.046266 | 0.99724 | -0.045941 | 23.3088
80 | 0.38002 | 0.18333 | -0.38001 | -0.18403 | 5.8994e-06 | -0.00069977 | 0.01222 | 0.012228 | 0.012228 | 0.99676 | -0.045728 | 0.99674 | -0.045593 | 5.5584
81 | 0.42045 | 0.20234 | -0.42044 | -0.20363 | 1.3292e-05 | -0.0012884 | 0.013512 | 0.013528 | 0.013528 | 0.99687 | -0.046705 | 0.99684 | -0.046432 | 6.1492
82 | 7.564 | 3.563 | -7.5638 | -3.5655 | 0.00019366 | -0.0025594 | 0.24215 | 0.24218 | 0.24218 | 0.99676 | -0.047975 | 0.99673 | -0.048086 | 18.9799
83 | 0.25476 | 0.12336 | -0.25476 | -0.12339 | 8.6274e-08 | -2.2761e-05 | 0.008198 | 0.0081982 | 0.0081982 | 0.99674 | -0.045593 | 0.99674 | -0.04559 | 3.7265
84 | -10.6475 | -4.9973 | 10.6482 | 4.993 | 0.0006628 | -0.0042526 | 0.34048 | 0.34042 | 0.34048 | 0.99724 | -0.045941 | 0.9973 | -0.045666 | 26.6832
85 | 7.5638 | 3.5655 | -7.5632 | -3.5734 | 0.0005976 | -0.0078923 | 0.24218 | 0.24229 | 0.24229 | 0.99673 | -0.048086 | 0.99665 | -0.048423 | 18.9879
86 | 21.4131 | 9.8836 | -21.4129 | -9.8838 | 0.00014902 | -0.00017759 | 0.68081 | 0.68081 | 0.68081 | 1 | 0 | 0.99999 | -3.3375e-05 | 53.3554
87 | 21.4129 | 9.8838 | -21.4058 | -9.8923 | 0.0071234 | -0.0084815 | 0.68081 | 0.68097 | 0.68097 | 0.99999 | -3.3375e-05 | 0.99965 | -0.0016243 | 53.3672
88 | 0.36282 | 0.17439 | -0.36281 | -0.17572 | 1.0052e-05 | -0.0013245 | 0.011625 | 0.011641 | 0.011641 | 0.99965 | -0.0016243 | 0.99962 | -0.0013849 | 5.2916
89 | 21.043 | 9.7179 | -21.0421 | -9.719 | 0.00087631 | -0.0010962 | 0.66934 | 0.66936 | 0.66936 | 0.99965 | -0.0016243 | 0.9996 | -0.0018234 | 52.4578
90 | -0.23565 | -0.11413 | 0.23565 | 0.11394 | 6.2581e-07 | -0.0001927 | 0.0075885 | 0.0075861 | 0.0075885 | 0.99604 | -0.074908 | 0.99605 | -0.074931 | 3.4493
91 | -6.8334 | -3.233 | 6.8343 | 3.2173 | 0.00096554 | -0.015705 | 0.21909 | 0.21889 | 0.21909 | 0.99605 | -0.074931 | 0.99619 | -0.074327 | 17.1703
92 | 6.5977 | 3.119 | -6.5973 | -3.1262 | 0.00040976 | -0.007157 | 0.21151 | 0.2116 | 0.2116 | 0.99605 | -0.074931 | 0.99598 | -0.075192 | 16.5829
93 | -6.8343 | -3.2173 | 6.8358 | 3.2206 | 0.0014181 | 0.0033582 | 0.21889 | 0.21889 | 0.21889 | 0.99619 | -0.074327 | 0.99658 | -0.052746 | 16.9683
94 | 6.5973 | 3.1262 | -6.5972 | -3.1279 | 9.7212e-05 | -0.0016968 | 0.2116 | 0.21162 | 0.21162 | 0.99598 | -0.075192 | 0.99597 | -0.075253 | 16.5846
95 | -6.3865 | -3.029 | 6.3866 | 3.0259 | 0.00016618 | -0.0031012 | 0.20488 | 0.20484 | 0.20488 | 0.99594 | -0.075362 | 0.99597 | -0.075253 | 16.0563
96 | -7.5629 | -3.5727 | 7.5632 | 3.5734 | 0.00031489 | 0.00076426 | 0.24229 | 0.24229 | 0.24229 | 0.99658 | -0.052746 | 0.99665 | -0.048423 | 18.7819
97 | 0.40214 | 0.19463 | -0.40212 | -0.19467 | 1.1413e-05 | -3.8197e-05 | 0.012941 | 0.012942 | 0.012942 | 0.99658 | -0.052746 | 0.99655 | -0.052934 | 6.1627
98 | 0.40212 | 0.19467 | -0.4021 | -0.19475 | 2.324e-05 | -7.7759e-05 | 0.012942 | 0.012943 | 0.012943 | 0.99655 | -0.052934 | 0.99648 | -0.053315 | 6.1633
99 | 11.5299 | 5.3596 | -11.529 | -5.3644 | 0.00088331 | -0.0047959 | 0.3677 | 0.36777 | 0.36777 | 0.9982 | -0.04174 | 0.99812 | -0.042094 | 28.822
100 | -11.9083 | -5.5429 | 11.9088 | 5.5442 | 0.00051888 | 0.0013398 | 0.37986 | 0.37986 | 0.37986 | 0.9982 | -0.04174 | 0.99828 | -0.037178 | 29.4466
101 | 11.529 | 5.3644 | -11.5238 | -5.3925 | 0.0051764 | -0.028051 | 0.36777 | 0.36815 | 0.36815 | 0.99812 | -0.042094 | 0.99766 | -0.044133 | 28.8517
102 | 11.5238 | 5.3925 | -11.5225 | -5.4 | 0.0013887 | -0.0075095 | 0.36815 | 0.36825 | 0.36825 | 0.99766 | -0.044133 | 0.99753 | -0.04467 | 28.8596
103 | 10.9988 | 5.1466 | -10.9981 | -5.1505 | 0.00065869 | -0.0039451 | 0.35142 | 0.35147 | 0.35147 | 0.99753 | -0.04467 | 0.99747 | -0.044937 | 27.5445
104 | 0.24744 | 0.1196 | -0.24743 | -0.11963 | 2.5265e-06 | -2.5047e-05 | 0.0079532 | 0.0079535 | 0.0079535 | 0.99753 | -0.04467 | 0.99752 | -0.044738 | 3.7874
105 | 10.9981 | 5.1505 | -10.9974 | -5.1549 | 0.00072983 | -0.0043691 | 0.35147 | 0.35153 | 0.35153 | 0.99747 | -0.044937 | 0.9974 | -0.045232 | 27.5491
106 | 0.24743 | 0.11963 | -0.24743 | -0.11984 | 7.5134e-07 | -0.00021108 | 0.0079535 | 0.0079562 | 0.0079562 | 0.99752 | -0.044738 | 0.99752 | -0.044711 | 3.6165
107 | -0.34817 | -0.16862 | 0.34818 | 0.16856 | 1.4164e-05 | -6.6438e-05 | 0.011197 | 0.011196 | 0.011197 | 0.99736 | -0.045501 | 0.9974 | -0.045232 | 5.3319
108 | 10.6492 | 4.9863 | -10.6482 | -4.993 | 0.001041 | -0.0066835 | 0.34033 | 0.34042 | 0.34042 | 0.9974 | -0.045232 | 0.9973 | -0.045666 | 26.6788
109 | 1.0063 | 0.46941 | -1.0062 | -0.47076 | 8.018e-05 | -0.0013464 | 0.032197 | 0.032214 | 0.032214 | 0.99555 | -0.0845 | 0.99548 | -0.083861 | 14.6427
110 | 1.0062 | 0.47076 | -1.0062 | -0.47129 | 3.1711e-05 | -0.00053205 | 0.032214 | 0.032221 | 0.032221 | 0.99548 | -0.083861 | 0.99545 | -0.083607 | 14.6457
111 | -0.22519 | -0.10906 | 0.22519 | 0.10808 | 2.9028e-06 | -0.00097987 | 0.0072524 | 0.0072401 | 0.0072524 | 0.99594 | -0.016943 | 0.99595 | -0.017054 | 3.2965
112 | -0.22519 | -0.10808 | 0.2252 | 0.10557 | 7.4167e-06 | -0.0025189 | 0.0072401 | 0.0072087 | 0.0072401 | 0.99595 | -0.017054 | 0.99598 | -0.017328 | 3.2909
113 | -0.85579 | -0.40989 | 0.85582 | 0.40908 | 3.4954e-05 | -0.00080983 | 0.027503 | 0.027492 | 0.027503 | 0.99598 | -0.017328 | 0.99602 | -0.017674 | 12.5012
114 | 0.63059 | 0.30433 | -0.63057 | -0.30518 | 1.9956e-05 | -0.00085322 | 0.020294 | 0.020305 | 0.020305 | 0.99598 | -0.017328 | 0.99595 | -0.017053 | 9.2295
115 | -0.85582 | -0.40908 | 0.85588 | 0.40907 | 5.1158e-05 | -1.2951e-05 | 0.027492 | 0.027492 | 0.027492 | 0.99602 | -0.017674 | 0.99608 | -0.01726 | 13.0916
116 | 0.22871 | 0.11064 | -0.2287 | -0.11076 | 1.0016e-05 | -0.00011644 | 0.0073641 | 0.0073656 | 0.0073656 | 0.99595 | -0.017053 | 0.99591 | -0.017343 | 3.5074
117 | 0.32953 | 0.15951 | -0.32952 | -0.15959 | 1.5638e-05 | -8.2489e-05 | 0.010612 | 0.010613 | 0.010613 | 0.99595 | -0.017053 | 0.9959 | -0.017366 | 5.0537
118 | -1.0911 | -0.52299 | 1.0911 | 0.52288 | 8.1056e-06 | -0.00011457 | 0.035066 | 0.035065 | 0.035066 | 0.99608 | -0.01726 | 0.99609 | -0.017323 | 15.9391
119 | 2.0843 | 0.99692 | -2.0836 | -0.99943 | 0.0006845 | -0.0025119 | 0.06691 | 0.066944 | 0.066944 | 0.99682 | -0.019853 | 0.99652 | -0.017062 | 30.4289
120 | -2.6803 | -1.2824 | 2.6808 | 1.2812 | 0.00057365 | -0.0012073 | 0.086046 | 0.086028 | 0.086046 | 0.99682 | -0.019853 | 0.99702 | -0.021665 | 39.1117
121 | 0.20854 | 0.09968 | -0.20854 | -0.10065 | 2.4494e-06 | -0.00096904 | 0.0066936 | 0.0067058 | 0.0067058 | 0.99682 | -0.019853 | 0.99681 | -0.019753 | 3.0481
122 | 0.38741 | 0.18578 | -0.38741 | -0.18607 | 2.5127e-06 | -0.00028759 | 0.012443 | 0.012446 | 0.012446 | 0.99682 | -0.019853 | 0.99682 | -0.019798 | 5.6573
123 | 0.30973 | 0.14988 | -0.30973 | -0.15001 | 7.4369e-07 | -0.0001327 | 0.0099676 | 0.0099693 | 0.0099693 | 0.99652 | -0.017062 | 0.99652 | -0.017041 | 4.5315
124 | 1.7739 | 0.84956 | -1.7734 | -0.84937 | 0.00045007 | 0.00018968 | 0.056976 | 0.056977 | 0.056977 | 0.99652 | -0.017062 | 0.99625 | -0.018806 | 27.1319
125 | 0.073449 | 0.035153 | -0.073449 | -0.035573 | 1.3162e-07 | -0.00042 | 0.0023576 | 0.0023629 | 0.0023629 | 0.99702 | -0.021665 | 0.99702 | -0.02165 | 1.0741
126 | -2.7543 | -1.3163 | 2.7554 | 1.3141 | 0.0011186 | -0.0022158 | 0.088386 | 0.088354 | 0.088386 | 0.99702 | -0.021665 | 0.9974 | -0.025091 | 40.1755
127 | 0.20854 | 0.10065 | -0.20854 | -0.101 | 8.856e-07 | -0.00034949 | 0.0067058 | 0.0067102 | 0.0067102 | 0.99681 | -0.019753 | 0.99681 | -0.019716 | 3.0501
128 | 0.30793 | 0.14757 | -0.30792 | -0.14807 | 2.7292e-06 | -0.00049486 | 0.0098887 | 0.0098949 | 0.0098949 | 0.99682 | -0.019798 | 0.99681 | -0.019722 | 4.4977
129 | 0.68214 | 0.3292 | -0.68214 | -0.32939 | 5.2594e-06 | -0.00019224 | 0.021947 | 0.02195 | 0.02195 | 0.99625 | -0.018806 | 0.99624 | -0.018739 | 9.9771
130 | 1.0913 | 0.52017 | -1.0911 | -0.52288 | 0.00019124 | -0.0027066 | 0.03503 | 0.035065 | 0.035065 | 0.99625 | -0.018806 | 0.99609 | -0.017323 | 15.9385
131 | 0.2287 | 0.11076 | -0.2287 | -0.11076 | 6.0576e-07 | -7.0407e-06 | 0.0073656 | 0.0073657 | 0.0073657 | 0.99591 | -0.017343 | 0.9959 | -0.01736 | 3.5075
132 | 0.33384 | 0.16134 | -0.33384 | -0.16168 | 2.2528e-06 | -0.00034722 | 0.010731 | 0.010736 | 0.010736 | 0.9974 | -0.025091 | 0.99739 | -0.025032 | 4.8799
133 | -3.0892 | -1.4754 | 3.0899 | 1.4744 | 0.00066971 | -0.0010154 | 0.099086 | 0.099071 | 0.099086 | 0.9974 | -0.025091 | 0.9976 | -0.026919 | 45.0389
134 | 0.30792 | 0.14807 | -0.30792 | -0.14849 | 2.3243e-06 | -0.00042094 | 0.0098949 | 0.0099002 | 0.0099002 | 0.99681 | -0.019722 | 0.9968 | -0.019657 | 4.5001
135 | 0.27379 | 0.13162 | -0.27378 | -0.13171 | 1.1138e-05 | -8.8598e-05 | 0.0088026 | 0.0088038 | 0.0088038 | 0.99624 | -0.018739 | 0.9962 | -0.019014 | 4.1923
136 | 0.27378 | 0.13171 | -0.27378 | -0.1326 | 3.8986e-06 | -0.00089048 | 0.0088038 | 0.008815 | 0.008815 | 0.9962 | -0.019014 | 0.99619 | -0.018891 | 4.0068
137 | 3.7635 | 1.7877 | -3.7634 | -1.7878 | 0.0001541 | -0.00014299 | 0.12056 | 0.12056 | 0.12056 | 0.99764 | -0.02726 | 0.9976 | -0.026919 | 54.8022
138 | -4.1524 | -1.976 | 4.1525 | 1.9757 | 9.319e-05 | -0.00030436 | 0.13307 | 0.13306 | 0.13307 | 0.99764 | -0.02726 | 0.99766 | -0.026997 | 36.7585
139 | 0.67348 | 0.31338 | -0.6734 | -0.31653 | 8.2489e-05 | -0.0031471 | 0.021495 | 0.021534 | 0.021534 | 0.9976 | -0.026919 | 0.99748 | -0.025934 | 9.7882
140 | -4.1525 | -1.9757 | 4.1526 | 1.9729 | 6.128e-05 | -0.0027683 | 0.13306 | 0.13303 | 0.13306 | 0.99766 | -0.026997 | 0.99768 | -0.026937 | 10.428
141 | 0.3971 | 0.186 | -0.39706 | -0.19117 | 4.7131e-05 | -0.0051669 | 0.012691 | 0.012755 | 0.012755 | 0.99748 | -0.025934 | 0.99737 | -0.024944 | 5.7977
142 | 0.2763 | 0.13053 | -0.27628 | -0.13359 | 1.3556e-05 | -0.003067 | 0.0088435 | 0.0088819 | 0.0088819 | 0.99748 | -0.025934 | 0.99744 | -0.025519 | 4.0372
143 | -4.1526 | -1.9729 | 4.1527 | 1.9703 | 5.9382e-05 | -0.002684 | 0.13303 | 0.13299 | 0.13303 | 0.99768 | -0.026937 | 0.99769 | -0.026878 | 10.4253
144 | 0.10203 | 0.048357 | -0.10203 | -0.049416 | 6.3876e-07 | -0.0010595 | 0.0032681 | 0.0032813 | 0.0032813 | 0.99737 | -0.024944 | 0.99737 | -0.024891 | 1.4915
145 | 0.29502 | 0.14281 | -0.29501 | -0.14288 | 1.0212e-05 | -6.9219e-05 | 0.0094869 | 0.0094878 | 0.0094878 | 0.99737 | -0.024944 | 0.99734 | -0.025173 | 4.518
146 | 0.27628 | 0.13359 | -0.27628 | -0.13381 | 9.6393e-07 | -0.00021706 | 0.0088819 | 0.0088846 | 0.0088846 | 0.99744 | -0.025519 | 0.99744 | -0.025489 | 4.0385
147 | -4.2522 | -2.0185 | 4.2523 | 2.0124 | 0.00014112 | -0.0060836 | 0.13619 | 0.13612 | 0.13619 | 0.99769 | -0.026878 | 0.99772 | -0.026739 | 10.6734
148 | -4.2523 | -2.0124 | 4.2528 | 2.0133 | 0.00050046 | 0.00092922 | 0.13612 | 0.13611 | 0.13612 | 0.99772 | -0.026739 | 0.99794 | -0.014534 | 10.5516
149 | -5.2247 | -2.4591 | 5.2248 | 2.4561 | 0.00010474 | -0.0029856 | 0.167 | 0.16696 | 0.167 | 0.99819 | -0.0083035 | 0.99821 | -0.0082163 | 13.0874
150 | 0.38785 | 0.18777 | -0.38783 | -0.18784 | 1.8184e-05 | -6.6773e-05 | 0.012462 | 0.012463 | 0.012463 | 0.99819 | -0.0083035 | 0.99814 | -0.0086128 | 5.9347
151 | 4.5822 | 2.148 | -4.5819 | -2.1475 | 0.0002461 | 0.00048449 | 0.14635 | 0.14636 | 0.14636 | 0.99819 | -0.0083035 | 0.99809 | -0.013905 | 11.3454
152 | -5.2248 | -2.4561 | 5.2251 | 2.4482 | 0.00027691 | -0.0079004 | 0.16696 | 0.16686 | 0.16696 | 0.99821 | -0.0082163 | 0.99827 | -0.0079829 | 13.0845
153 | 4.5819 | 2.1475 | -4.5815 | -2.1627 | 0.00040932 | -0.015231 | 0.14636 | 0.14655 | 0.14655 | 0.99809 | -0.013905 | 0.998 | -0.014294 | 11.4848
154 | 0.41318 | 0.19929 | -0.41317 | -0.20011 | 8.1368e-06 | -0.00082104 | 0.013265 | 0.013276 | 0.013276 | 0.99827 | -0.0079829 | 0.99825 | -0.0078121 | 6.0345
155 | 4.5815 | 2.1627 | -4.5813 | -2.1724 | 0.00026039 | -0.009667 | 0.14655 | 0.14667 | 0.14667 | 0.998 | -0.014294 | 0.99794 | -0.014534 | 11.4943
156 | -0.30792 | -0.14913 | 0.30792 | 0.14849 | 3.5578e-06 | -0.00064346 | 0.0099083 | 0.0099002 | 0.0099083 | 0.99679 | -0.019557 | 0.9968 | -0.019657 | 4.5038
157 | 0.083611 | 0.036137 | -0.08361 | -0.037016 | 3.4301e-07 | -0.00087874 | 0.0026332 | 0.0026434 | 0.0026434 | 0.99857 | -0.0062652 | 0.99857 | -0.0062374 | 1.2015
158 | 0.08361 | 0.037016 | -0.083609 | -0.04004 | 1.2014e-06 | -0.0030246 | 0.0026434 | 0.00268 | 0.00268 | 0.99857 | -0.0062374 | 0.99855 | -0.0061259 | 1.2182
159 | 0.083609 | 0.04004 | -0.083609 | -0.040494 | 1.8299e-07 | -0.00045334 | 0.00268 | 0.0026857 | 0.0026857 | 0.99855 | -0.0061259 | 0.99855 | -0.0061071 | 1.2208

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.7618 | 10.0562

## res_load
| p_mw | q_mvar
0 | 0.40329 | 0.19532
1 | 0.41426 | 0.20064
2 | 0.36277 | 0.1757
3 | 0.32764 | 0.15868
4 | 0.078998 | 0.038261
5 | 0.3818 | 0.18491
6 | 0.10683 | 0.051742
7 | 0.11372 | 0.055077
8 | 0.17014 | 0.082401
9 | 0.076922 | 0.037255
10 | 0.080463 | 0.03897
11 | 0.39325 | 0.19046
12 | 0.072674 | 0.035198
13 | 0.28185 | 0.1365
14 | 0.16276 | 0.078828
15 | 0.34675 | 0.16794
16 | 0.31198 | 0.1511
17 | 0.34566 | 0.16741
18 | 0.26858 | 0.13008
19 | 0.28972 | 0.14032
20 | 0.11784 | 0.057071
21 | 0.22734 | 0.11011
22 | 0.32288 | 0.15638
23 | 0.38265 | 0.18533
24 | 0.074253 | 0.035962
25 | 0.57335 | 0.27768
26 | 0.11483 | 0.055616
27 | 1.1464 | 0.55523
28 | 0.27376 | 0.13259
29 | 0.25975 | 0.1258
30 | 0.27578 | 0.13357
31 | 0.14967 | 0.072487
32 | 0.10021 | 0.048534
33 | 0.41201 | 0.19955
34 | 0.12525 | 0.060661
35 | 1.3411 | 0.64954
36 | 0.42044 | 0.20363
37 | 0.25476 | 0.12339
38 | 0.33473 | 0.16212
39 | 0.36281 | 0.17572
40 | 0.23565 | 0.11413
41 | 0.087315 | 0.042289
42 | 0.32502 | 0.15742
43 | 0.4021 | 0.19475
44 | 0.21058 | 0.10199
45 | 0.37841 | 0.18327
46 | 0.38415 | 0.18605
47 | 0.27622 | 0.13378
48 | 0.34817 | 0.16862
49 | 0.29067 | 0.14078
50 | 0.22519 | 0.10906
51 | 0.072327 | 0.035029
52 | 0.23522 | 0.11392
53 | 0.07948 | 0.038494
54 | 0.30973 | 0.15001
55 | 0.32952 | 0.15959
56 | 0.073449 | 0.035573
57 | 0.20854 | 0.101
58 | 0.40834 | 0.19777
59 | 0.2287 | 0.11076
60 | 0.3889 | 0.18835
61 | 0.10203 | 0.049416
62 | 0.29501 | 0.14288
63 | 0.33384 | 0.16168
64 | 0.099542 | 0.048211
65 | 0.27628 | 0.13381
66 | 0.25462 | 0.12332
67 | 0.38783 | 0.18784
68 | 0.32844 | 0.15907
69 | 0.41317 | 0.20011
70 | 0.30792 | 0.14913
71 | 0.27378 | 0.1326
72 | 0.41097 | 0.19904
73 | 0.10462 | 0.050669
74 | 0.083609 | 0.040494
75 | 0.24743 | 0.11984

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1