## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_649_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_649_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_649_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_649_0_node_5 | 20 | n |  | TRUE
4 | bus_MV_649_0_node_7 | 20 | n |  | TRUE
5 | bus_MV_649_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_649_0_node_4 | 20 | n |  | TRUE
7 | bus_MV_649_0_node_98 | 20 | n |  | TRUE
8 | bus_MV_649_0_node_82 | 20 | n |  | TRUE
9 | bus_MV_649_0_node_85 | 20 | n |  | TRUE
10 | bus_MV_649_0_node_6 | 20 | n |  | TRUE
11 | bus_MV_649_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_649_0_node_9 | 20 | n |  | TRUE
13 | bus_MV_649_0_node_84 | 20 | n |  | TRUE
14 | bus_MV_649_0_node_170 | 20 | n |  | TRUE
15 | bus_MV_649_0_node_83 | 20 | n |  | TRUE
16 | bus_MV_649_0_node_155 | 20 | n |  | TRUE
17 | bus_MV_649_0_node_101 | 20 | n |  | TRUE
18 | bus_MV_649_0_node_104 | 20 | n |  | TRUE
19 | bus_MV_649_0_node_108 | 20 | n |  | TRUE
20 | bus_MV_649_0_node_86 | 20 | n |  | TRUE
21 | bus_MV_649_0_node_93 | 20 | n |  | TRUE
22 | bus_MV_649_0_node_127 | 20 | n |  | TRUE
23 | bus_MV_649_0_node_169 | 20 | n |  | TRUE
24 | bus_MV_649_0_node_177 | 20 | n |  | TRUE
25 | bus_MV_649_0_node_87 | 20 | n |  | TRUE
26 | bus_MV_649_0_node_10 | 20 | n |  | TRUE
27 | bus_MV_649_0_node_39 | 20 | n |  | TRUE
28 | bus_MV_649_0_node_11 | 20 | n |  | TRUE
29 | bus_MV_649_0_node_41 | 20 | n |  | TRUE
30 | bus_MV_649_0_node_12 | 20 | n |  | TRUE
31 | bus_MV_649_0_node_13 | 20 | n |  | TRUE
32 | bus_MV_649_0_node_32 | 20 | n |  | TRUE
33 | bus_MV_649_0_node_17 | 20 | n |  | TRUE
34 | bus_MV_649_0_node_14 | 20 | n |  | TRUE
35 | bus_MV_649_0_node_15 | 20 | n |  | TRUE
36 | bus_MV_649_0_node_34 | 20 | n |  | TRUE
37 | bus_MV_649_0_node_33 | 20 | n |  | TRUE
38 | bus_MV_649_0_node_31 | 20 | n |  | TRUE
39 | bus_MV_649_0_node_120 | 20 | n |  | TRUE
40 | bus_MV_649_0_node_16 | 20 | n |  | TRUE
41 | bus_MV_649_0_node_79 | 20 | n |  | TRUE
42 | bus_MV_649_0_node_181 | 20 | n |  | TRUE
43 | bus_MV_649_0_node_35 | 20 | n |  | TRUE
44 | bus_MV_649_0_node_18 | 20 | n |  | TRUE
45 | bus_MV_649_0_node_19 | 20 | n |  | TRUE
46 | bus_MV_649_0_node_25 | 20 | n |  | TRUE
47 | bus_MV_649_0_node_26 | 20 | n |  | TRUE
48 | bus_MV_649_0_node_24 | 20 | n |  | TRUE
49 | bus_MV_649_0_node_178 | 20 | n |  | TRUE
50 | bus_MV_649_0_node_174 | 20 | n |  | TRUE
51 | bus_MV_649_0_node_28 | 20 | n |  | TRUE
52 | bus_MV_649_0_node_59 | 20 | n |  | TRUE
53 | bus_MV_649_0_node_147 | 20 | n |  | TRUE
54 | bus_MV_649_0_node_61 | 20 | n |  | TRUE
55 | bus_MV_649_0_node_27 | 20 | n |  | TRUE
56 | bus_MV_649_0_node_29 | 20 | n |  | TRUE
57 | bus_MV_649_0_node_180 | 20 | n |  | TRUE
58 | bus_MV_649_0_node_143 | 20 | n |  | TRUE
59 | bus_MV_649_0_node_166 | 20 | n |  | TRUE
60 | bus_MV_649_0_node_30 | 20 | n |  | TRUE
61 | bus_MV_649_0_node_67 | 20 | n |  | TRUE
62 | bus_MV_649_0_node_66 | 20 | n |  | TRUE
63 | bus_MV_649_0_node_183 | 20 | n |  | TRUE
64 | bus_MV_649_0_node_20 | 20 | n |  | TRUE
65 | bus_MV_649_0_node_21 | 20 | n |  | TRUE
66 | bus_MV_649_0_node_22 | 20 | n |  | TRUE
67 | bus_MV_649_0_node_23 | 20 | n |  | TRUE
68 | bus_MV_649_0_node_62 | 20 | n |  | TRUE
69 | bus_MV_649_0_node_63 | 20 | n |  | TRUE
70 | bus_MV_649_0_node_42 | 20 | n |  | TRUE
71 | bus_MV_649_0_node_126 | 20 | n |  | TRUE
72 | bus_MV_649_0_node_40 | 20 | n |  | TRUE
73 | bus_MV_649_0_node_48 | 20 | n |  | TRUE
74 | bus_MV_649_0_node_43 | 20 | n |  | TRUE
75 | bus_MV_649_0_node_65 | 20 | n |  | TRUE
76 | bus_MV_649_0_node_46 | 20 | n |  | TRUE
77 | bus_MV_649_0_node_173 | 20 | n |  | TRUE
78 | bus_MV_649_0_node_57 | 20 | n |  | TRUE
79 | bus_MV_649_0_node_139 | 20 | n |  | TRUE
80 | bus_MV_649_0_node_60 | 20 | n |  | TRUE
81 | bus_MV_649_0_node_69 | 20 | n |  | TRUE
82 | bus_MV_649_0_node_77 | 20 | n |  | TRUE
83 | bus_MV_649_0_node_162 | 20 | n |  | TRUE
84 | bus_MV_649_0_node_38 | 20 | n |  | TRUE
85 | bus_MV_649_0_node_36 | 20 | n |  | TRUE
86 | bus_MV_649_0_node_179 | 20 | n |  | TRUE
87 | bus_MV_649_0_node_37 | 20 | n |  | TRUE
88 | bus_MV_649_0_node_124 | 20 | n |  | TRUE
89 | bus_MV_649_0_node_175 | 20 | n |  | TRUE
90 | bus_MV_649_0_node_123 | 20 | n |  | TRUE
91 | bus_MV_649_0_node_125 | 20 | n |  | TRUE
92 | bus_MV_649_0_node_44 | 20 | n |  | TRUE
93 | bus_MV_649_0_node_45 | 20 | n |  | TRUE
94 | bus_MV_649_0_node_49 | 20 | n |  | TRUE
95 | bus_MV_649_0_node_47 | 20 | n |  | TRUE
96 | bus_MV_649_0_node_94 | 20 | n |  | TRUE
97 | bus_MV_649_0_node_176 | 20 | n |  | TRUE
98 | bus_MV_649_0_node_171 | 20 | n |  | TRUE
99 | bus_MV_649_0_node_115 | 20 | n |  | TRUE
100 | bus_MV_649_0_node_54 | 20 | n |  | TRUE
101 | bus_MV_649_0_node_113 | 20 | n |  | TRUE
102 | bus_MV_649_0_node_114 | 20 | n |  | TRUE
103 | bus_MV_649_0_node_165 | 20 | n |  | TRUE
104 | bus_MV_649_0_node_168 | 20 | n |  | TRUE
105 | bus_MV_649_0_node_50 | 20 | n |  | TRUE
106 | bus_MV_649_0_node_51 | 20 | n |  | TRUE
107 | bus_MV_649_0_node_52 | 20 | n |  | TRUE
108 | bus_MV_649_0_node_53 | 20 | n |  | TRUE
109 | bus_MV_649_0_node_55 | 20 | n |  | TRUE
110 | bus_MV_649_0_node_129 | 20 | n |  | TRUE
111 | bus_MV_649_0_node_56 | 20 | n |  | TRUE
112 | bus_MV_649_0_node_138 | 20 | n |  | TRUE
113 | bus_MV_649_0_node_132 | 20 | n |  | TRUE
114 | bus_MV_649_0_node_130 | 20 | n |  | TRUE
115 | bus_MV_649_0_node_128 | 20 | n |  | TRUE
116 | bus_MV_649_0_node_172 | 20 | n |  | TRUE
117 | bus_MV_649_0_node_134 | 20 | n |  | TRUE
118 | bus_MV_649_0_node_131 | 20 | n |  | TRUE
119 | bus_MV_649_0_node_58 | 20 | n |  | TRUE
120 | bus_MV_649_0_node_140 | 20 | n |  | TRUE
121 | bus_MV_649_0_node_167 | 20 | n |  | TRUE
122 | bus_MV_649_0_node_118 | 20 | n |  | TRUE
123 | bus_MV_649_0_node_64 | 20 | n |  | TRUE
124 | bus_MV_649_0_node_163 | 20 | n |  | TRUE
125 | bus_MV_649_0_node_68 | 20 | n |  | TRUE
126 | bus_MV_649_0_node_71 | 20 | n |  | TRUE
127 | bus_MV_649_0_node_72 | 20 | n |  | TRUE
128 | bus_MV_649_0_node_73 | 20 | n |  | TRUE
129 | bus_MV_649_0_node_76 | 20 | n |  | TRUE
130 | bus_MV_649_0_node_90 | 20 | n |  | TRUE
131 | bus_MV_649_0_node_78 | 20 | n |  | TRUE
132 | bus_MV_649_0_node_75 | 20 | n |  | TRUE
133 | bus_MV_649_0_node_160 | 20 | n |  | TRUE
134 | bus_MV_649_0_node_112 | 20 | n |  | TRUE
135 | bus_MV_649_0_node_144 | 20 | n |  | TRUE
136 | bus_MV_649_0_node_161 | 20 | n |  | TRUE
137 | bus_MV_649_0_node_80 | 20 | n |  | TRUE
138 | bus_MV_649_0_node_81 | 20 | n |  | TRUE
139 | bus_MV_649_0_node_89 | 20 | n |  | TRUE
140 | bus_MV_649_0_node_88 | 20 | n |  | TRUE
141 | bus_MV_649_0_node_184 | 20 | n |  | TRUE
142 | bus_MV_649_0_node_142 | 20 | n |  | TRUE
143 | bus_MV_649_0_node_153 | 20 | n |  | TRUE
144 | bus_MV_649_0_node_100 | 20 | n |  | TRUE
145 | bus_MV_649_0_node_105 | 20 | n |  | TRUE
146 | bus_MV_649_0_node_159 | 20 | n |  | TRUE
147 | bus_MV_649_0_node_106 | 20 | n |  | TRUE
148 | bus_MV_649_0_node_103 | 20 | n |  | TRUE
149 | bus_MV_649_0_node_92 | 20 | n |  | TRUE
150 | bus_MV_649_0_node_119 | 20 | n |  | TRUE
151 | bus_MV_649_0_node_116 | 20 | n |  | TRUE
152 | bus_MV_649_0_node_146 | 20 | n |  | TRUE
153 | bus_MV_649_0_node_117 | 20 | n |  | TRUE
154 | bus_MV_649_0_node_95 | 20 | n |  | TRUE
155 | bus_MV_649_0_node_96 | 20 | n |  | TRUE
156 | bus_MV_649_0_node_97 | 20 | n |  | TRUE
157 | bus_MV_649_0_node_157 | 20 | n |  | TRUE
158 | bus_MV_649_0_node_158 | 20 | n |  | TRUE
159 | bus_MV_649_0_node_99 | 20 | n |  | TRUE
160 | bus_MV_649_0_node_109 | 20 | n |  | TRUE
161 | bus_MV_649_0_node_110 | 20 | n |  | TRUE
162 | bus_MV_649_0_node_102 | 20 | n |  | TRUE
163 | bus_MV_649_0_node_182 | 20 | n |  | TRUE
164 | bus_MV_649_0_node_111 | 20 | n |  | TRUE
165 | bus_MV_649_0_node_107 | 20 | n |  | TRUE
166 | bus_MV_649_0_node_141 | 20 | n |  | TRUE
167 | bus_MV_649_0_node_122 | 20 | n |  | TRUE
168 | bus_MV_649_0_node_121 | 20 | n |  | TRUE
169 | bus_MV_649_0_node_185 | 20 | n |  | TRUE
170 | bus_MV_649_0_node_164 | 20 | n |  | TRUE
171 | bus_MV_649_0_node_145 | 20 | n |  | TRUE
172 | bus_MV_649_0_node_133 | 20 | n |  | TRUE
173 | bus_MV_649_0_node_135 | 20 | n |  | TRUE
174 | bus_MV_649_0_node_136 | 20 | n |  | TRUE
175 | bus_MV_649_0_node_137 | 20 | n |  | TRUE
176 | bus_MV_649_0_node_156 | 20 | n |  | TRUE
177 | bus_MV_649_0_node_148 | 20 | n |  | TRUE
178 | bus_MV_649_0_node_149 | 20 | n |  | TRUE
179 | bus_MV_649_0_node_150 | 20 | n |  | TRUE
180 | bus_MV_649_0_node_151 | 20 | n |  | TRUE
181 | bus_MV_649_0_node_152 | 20 | n |  | TRUE
182 | bus_MV_649_0_node_154 | 20 | n |  | TRUE
183 | bus_HV_649_0_node_48 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_649_0_load_0 | 0 | 0.29339 | 0.1421 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_649_0_load_7 | 4 | 0.24681 | 0.11954 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_649_0_load_98 | 7 | 0.23716 | 0.11486 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_649_0_load_6 | 10 | 0.11161 | 0.054055 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_649_0_load_170 | 14 | 0.29756 | 0.14412 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_649_0_load_155 | 16 | 0.15216 | 0.073695 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_649_0_load_101 | 17 | 0.070511 | 0.03415 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_649_0_load_108 | 19 | 0.26897 | 0.13027 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_649_0_load_93 | 21 | 0.3342 | 0.16186 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_649_0_load_127 | 22 | 0.54991 | 0.26633 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_649_0_load_169 | 23 | 0.11738 | 0.056851 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_649_0_load_177 | 24 | 0.1578 | 0.076427 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_649_0_load_10 | 26 | 0.16367 | 0.079271 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_649_0_load_39 | 27 | 0.24546 | 0.11888 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_649_0_load_15 | 35 | 0.15881 | 0.076917 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_649_0_load_34 | 36 | 0.32725 | 0.15849 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_649_0_load_31 | 38 | 0.38593 | 0.18692 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_649_0_load_120 | 39 | 0.31661 | 0.15334 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_649_0_load_79 | 41 | 0.28955 | 0.14023 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_649_0_load_181 | 42 | 0.3076 | 0.14898 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_649_0_load_18 | 44 | 0.32993 | 0.15979 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_649_0_load_178 | 49 | 0.10651 | 0.051586 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_649_0_load_147 | 53 | 0.50041 | 0.24236 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_649_0_load_180 | 57 | 0.27137 | 0.13143 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_649_0_load_143 | 58 | 0.085922 | 0.041614 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_649_0_load_166 | 59 | 0.31032 | 0.1503 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_649_0_load_66 | 62 | 0.20025 | 0.096986 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_649_0_load_183 | 63 | 1.4838 | 0.71864 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_649_0_load_21 | 65 | 0.31826 | 0.15414 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_649_0_load_22 | 66 | 0.071802 | 0.034775 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_649_0_load_23 | 67 | 0.071551 | 0.034654 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_649_0_load_62 | 68 | 0.20557 | 0.099564 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_649_0_load_65 | 75 | 0.33005 | 0.15985 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_649_0_load_173 | 77 | 0.2332 | 0.11294 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_649_0_load_57 | 78 | 0.40094 | 0.19418 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_649_0_load_139 | 79 | 0.13223 | 0.06404 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_649_0_load_162 | 83 | 0.248 | 0.12011 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_649_0_load_179 | 86 | 0.082635 | 0.040022 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_649_0_load_124 | 88 | 0.11711 | 0.056719 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_649_0_load_175 | 89 | 0.084411 | 0.040882 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_649_0_load_123 | 90 | 0.22332 | 0.10816 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_649_0_load_125 | 91 | 0.11741 | 0.056867 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_649_0_load_44 | 92 | 0.27266 | 0.13206 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_649_0_load_94 | 96 | 0.34587 | 0.16751 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_649_0_load_176 | 97 | 0.29832 | 0.14448 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_649_0_load_171 | 98 | 0.076986 | 0.037286 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_649_0_load_165 | 103 | 0.27151 | 0.1315 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_649_0_load_168 | 104 | 0.36641 | 0.17746 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_649_0_load_50 | 105 | 0.37676 | 0.18247 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_649_0_load_129 | 110 | 0.30882 | 0.14957 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_649_0_load_138 | 112 | 0.36178 | 0.17522 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_649_0_load_132 | 113 | 0.18126 | 0.087789 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_649_0_load_130 | 114 | 0.10214 | 0.04947 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_649_0_load_172 | 116 | 0.24606 | 0.11917 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_649_0_load_140 | 120 | 0.069406 | 0.033615 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_649_0_load_167 | 121 | 0.41604 | 0.2015 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_649_0_load_68 | 125 | 0.28864 | 0.13979 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_649_0_load_76 | 129 | 0.24429 | 0.11832 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_649_0_load_90 | 130 | 0.37697 | 0.18257 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_649_0_load_78 | 131 | 0.27303 | 0.13224 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_649_0_load_160 | 133 | 0.17707 | 0.085761 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_649_0_load_112 | 134 | 0.26642 | 0.12903 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_649_0_load_161 | 136 | 0.34188 | 0.16558 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_649_0_load_80 | 137 | 0.32004 | 0.155 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_649_0_load_184 | 141 | 0.29721 | 0.14395 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_649_0_load_142 | 142 | 0.080447 | 0.038962 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_649_0_load_159 | 146 | 0.1811 | 0.087709 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_649_0_load_103 | 148 | 0.35054 | 0.16978 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_649_0_load_116 | 151 | 0.32784 | 0.15878 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_649_0_load_146 | 152 | 0.28406 | 0.13758 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_649_0_load_117 | 153 | 0.19675 | 0.095288 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_649_0_load_95 | 154 | 0.23666 | 0.11462 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_649_0_load_157 | 157 | 0.090623 | 0.043891 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_649_0_load_158 | 158 | 0.11319 | 0.054819 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_649_0_load_99 | 159 | 0.27358 | 0.1325 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_649_0_load_109 | 160 | 0.35873 | 0.17374 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_649_0_load_182 | 163 | 0.37223 | 0.18028 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_649_0_load_141 | 166 | 0.068181 | 0.033022 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_649_0_load_121 | 168 | 0.2558 | 0.12389 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_649_0_load_185 | 169 | 0.14691 | 0.071151 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_649_0_load_145 | 171 | 0.2755 | 0.13343 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_649_0_load_133 | 172 | 0.072795 | 0.035256 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_649_0_load_135 | 173 | 0.10777 | 0.052196 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_649_0_load_137 | 175 | 0.090512 | 0.043837 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_649_0_load_156 | 176 | 0.2284 | 0.11062 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_649_0_load_148 | 177 | 0.08362 | 0.040499 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_649_0_load_150 | 179 | 0.15731 | 0.076188 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_649_0_load_151 | 180 | 0.083004 | 0.0402 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_649_0_load_152 | 181 | 0.089753 | 0.043469 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_649_0_load_154 | 182 | 0.083896 | 0.040633 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 73 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_649_0_line_0 |  | 0 | 1 | 0.017244 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_649_0_line_1 |  | 1 | 2 | 0.53833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_649_0_line_2 |  | 1 | 3 | 0.95563 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_649_0_line_3 |  | 2 | 4 | 0.11609 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_649_0_line_4 |  | 3 | 10 | 0.030998 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_649_0_line_5 |  | 3 | 5 | 0.72234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_649_0_line_6 |  | 4 | 11 | 0.047322 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_649_0_line_7 |  | 5 | 6 | 0.14369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_649_0_line_8 |  | 5 | 7 | 0.012479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_649_0_line_9 |  | 6 | 8 | 0.21244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_649_0_line_10 |  | 6 | 9 | 0.30272 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
11 | MV_649_0_line_11 |  | 8 | 13 | 0.28095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_649_0_line_12 |  | 8 | 14 | 0.014543 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_649_0_line_13 |  | 9 | 20 | 0.24238 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
14 | MV_649_0_line_14 |  | 9 | 21 | 0.014422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_649_0_line_15 |  | 11 | 12 | 0.6331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_649_0_line_16 |  | 12 | 23 | 0.22029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_649_0_line_17 |  | 12 | 24 | 0.17778 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_649_0_line_18 |  | 13 | 18 | 0.19166 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_649_0_line_19 |  | 13 | 19 | 0.064611 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_649_0_line_20 |  | 13 | 15 | 0.43492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_649_0_line_21 |  | 15 | 16 | 0.016706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_649_0_line_22 |  | 15 | 17 | 0.01167 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_649_0_line_23 |  | 16 | 143 | 0.031952 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_649_0_line_24 |  | 17 | 144 | 0.026626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_649_0_line_25 |  | 18 | 147 | 0.087637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_649_0_line_26 |  | 18 | 148 | 0.023898 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_649_0_line_27 |  | 18 | 145 | 0.065668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_649_0_line_28 |  | 20 | 22 | 0.0083427 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
29 | MV_649_0_line_29 |  | 22 | 115 | 0.045712 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
30 | MV_649_0_line_30 |  | 24 | 25 | 0.063333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_649_0_line_31 |  | 25 | 139 | 0.45149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_649_0_line_32 |  | 26 | 27 | 0.059427 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_649_0_line_33 |  | 26 | 28 | 0.12792 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_649_0_line_34 |  | 27 | 29 | 0.006838 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_649_0_line_35 |  | 28 | 30 | 0.034475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_649_0_line_36 |  | 28 | 31 | 0.30848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_649_0_line_37 |  | 29 | 74 | 0.090261 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_649_0_line_38 |  | 29 | 72 | 0.06757 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
39 | MV_649_0_line_39 |  | 30 | 32 | 0.10205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_649_0_line_40 |  | 31 | 33 | 0.18124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_649_0_line_41 |  | 31 | 34 | 0.098559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_649_0_line_42 |  | 31 | 35 | 0.067298 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_649_0_line_43 |  | 32 | 37 | 0.22743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_649_0_line_44 |  | 32 | 38 | 0.00512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_649_0_line_45 |  | 33 | 42 | 0.01775 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_649_0_line_46 |  | 33 | 40 | 0.66337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_649_0_line_47 |  | 34 | 36 | 0.018354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_649_0_line_48 |  | 36 | 43 | 0.038591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_649_0_line_49 |  | 37 | 39 | 0.024895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_649_0_line_50 |  | 40 | 41 | 0.002387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_649_0_line_51 |  | 43 | 84 | 0.84247 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_649_0_line_52 |  | 44 | 45 | 0.004326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_649_0_line_53 |  | 45 | 46 | 0.24809 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_649_0_line_54 |  | 45 | 47 | 0.19709 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
55 | MV_649_0_line_55 |  | 46 | 51 | 0.23798 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
56 | MV_649_0_line_56 |  | 46 | 52 | 0.005004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_649_0_line_57 |  | 46 | 53 | 0.03209 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_649_0_line_58 |  | 47 | 54 | 0.078173 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_649_0_line_59 |  | 47 | 48 | 0.12984 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
60 | MV_649_0_line_60 |  | 48 | 49 | 0.026834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_649_0_line_61 |  | 48 | 50 | 0.020773 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
62 | MV_649_0_line_62 |  | 50 | 77 | 0.006057 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
63 | MV_649_0_line_63 |  | 51 | 59 | 0.005109 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_649_0_line_64 |  | 51 | 56 | 0.2015 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
65 | MV_649_0_line_65 |  | 52 | 78 | 0.036875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_649_0_line_66 |  | 54 | 79 | 0.022923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_649_0_line_67 |  | 54 | 80 | 0.078692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_649_0_line_68 |  | 55 | 56 | 0.088995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_649_0_line_69 |  | 55 | 57 | 0.020876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_649_0_line_70 |  | 55 | 58 | 0.073071 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_649_0_line_71 |  | 56 | 60 | 0.24331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_649_0_line_72 |  | 56 | 61 | 0.10967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_649_0_line_73 |  | 56 | 62 | 0.020884 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_649_0_line_74 |  | 57 | 81 | 0.061293 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_649_0_line_75 |  | 58 | 82 | 0.05938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_649_0_line_76 |  | 60 | 63 | 0.004673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_649_0_line_77 |  | 61 | 83 | 0.026361 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_649_0_line_78 |  | 64 | 65 | 0.004673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_649_0_line_79 |  | 64 | 66 | 0.077044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_649_0_line_80 |  | 66 | 67 | 0.02271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_649_0_line_81 |  | 67 | 71 | 0.01689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_649_0_line_82 |  | 68 | 69 | 0.0411 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
83 | MV_649_0_line_83 |  | 68 | 70 | 0.045022 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
84 | MV_649_0_line_84 |  | 69 | 123 | 0.044039 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
85 | MV_649_0_line_85 |  | 70 | 72 | 0.035736 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
86 | MV_649_0_line_86 |  | 71 | 73 | 0.1163 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
87 | MV_649_0_line_87 |  | 71 | 74 | 0.06334 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
88 | MV_649_0_line_88 |  | 73 | 75 | 0.03769 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
89 | MV_649_0_line_89 |  | 73 | 76 | 0.52843 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_649_0_line_90 |  | 74 | 91 | 0.013164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_649_0_line_91 |  | 75 | 100 | 0.004857 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
92 | MV_649_0_line_92 |  | 76 | 95 | 0.17834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_649_0_line_93 |  | 76 | 96 | 0.007127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_649_0_line_94 |  | 77 | 123 | 0.00477 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
95 | MV_649_0_line_95 |  | 80 | 121 | 0.003353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_649_0_line_96 |  | 80 | 119 | 0.037133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_649_0_line_97 |  | 81 | 125 | 0.007208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_649_0_line_98 |  | 82 | 135 | 0.050153 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_649_0_line_99 |  | 82 | 132 | 0.069536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_649_0_line_100 |  | 83 | 124 | 0.038265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_649_0_line_101 |  | 84 | 89 | 0.007996 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_649_0_line_102 |  | 84 | 85 | 0.73806 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_649_0_line_103 |  | 84 | 87 | 0.13339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_649_0_line_104 |  | 85 | 86 | 0.018372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_649_0_line_105 |  | 87 | 88 | 0.019156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_649_0_line_106 |  | 88 | 90 | 0.10269 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_649_0_line_107 |  | 92 | 93 | 0.037223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_649_0_line_108 |  | 93 | 94 | 0.24075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_649_0_line_109 |  | 94 | 98 | 0.019185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_649_0_line_110 |  | 94 | 99 | 0.14562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_649_0_line_111 |  | 95 | 97 | 0.011679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_649_0_line_112 |  | 99 | 104 | 0.003619 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_649_0_line_113 |  | 99 | 101 | 0.20536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_649_0_line_114 |  | 100 | 108 | 0.19871 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
115 | MV_649_0_line_115 |  | 101 | 102 | 0.049163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_649_0_line_116 |  | 102 | 103 | 0.008006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_649_0_line_117 |  | 103 | 170 | 0.049384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_649_0_line_118 |  | 105 | 106 | 0.019205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_649_0_line_119 |  | 105 | 107 | 0.067341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_649_0_line_120 |  | 106 | 108 | 0.16726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_649_0_line_121 |  | 107 | 109 | 0.085774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_649_0_line_122 |  | 108 | 110 | 0.041888 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
123 | MV_649_0_line_123 |  | 109 | 111 | 0.14523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_649_0_line_124 |  | 109 | 112 | 0.040142 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_649_0_line_125 |  | 110 | 115 | 0.064756 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
126 | MV_649_0_line_126 |  | 111 | 113 | 0.043278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_649_0_line_127 |  | 111 | 114 | 0.014991 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_649_0_line_128 |  | 112 | 116 | 0.12282 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
129 | MV_649_0_line_129 |  | 113 | 117 | 0.027857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_649_0_line_130 |  | 114 | 118 | 0.03301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_649_0_line_131 |  | 117 | 174 | 0.028034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_649_0_line_132 |  | 118 | 172 | 0.0058447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_649_0_line_133 |  | 119 | 120 | 0.041459 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
134 | MV_649_0_line_134 |  | 120 | 122 | 0.050805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_649_0_line_135 |  | 122 | 149 | 0.10496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_649_0_line_136 |  | 124 | 170 | 0.039775 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_649_0_line_137 |  | 124 | 134 | 0.091861 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
138 | MV_649_0_line_138 |  | 126 | 127 | 0.23154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_649_0_line_139 |  | 126 | 128 | 0.15508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_649_0_line_140 |  | 126 | 129 | 0.009647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_649_0_line_141 |  | 127 | 130 | 0.006283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_649_0_line_142 |  | 128 | 131 | 0.00636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_649_0_line_143 |  | 129 | 132 | 0.024938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_649_0_line_144 |  | 133 | 134 | 0.18217 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_649_0_line_145 |  | 135 | 136 | 0.006958 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_649_0_line_146 |  | 137 | 138 | 0.049457 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_649_0_line_147 |  | 138 | 139 | 0.5311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_649_0_line_148 |  | 139 | 142 | 0.021749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_649_0_line_149 |  | 139 | 140 | 0.18133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_649_0_line_150 |  | 140 | 141 | 0.035039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_649_0_line_151 |  | 143 | 181 | 0.010765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_649_0_line_152 |  | 144 | 162 | 0.45891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_649_0_line_153 |  | 145 | 146 | 0.023353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_649_0_line_154 |  | 147 | 165 | 0.034711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_649_0_line_155 |  | 147 | 166 | 0.019157 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_649_0_line_156 |  | 149 | 150 | 0.12359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_649_0_line_157 |  | 149 | 151 | 0.009822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_649_0_line_158 |  | 150 | 152 | 0.0048143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_649_0_line_159 |  | 151 | 153 | 0.030573 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_649_0_line_160 |  | 152 | 171 | 0.00041858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_649_0_line_161 |  | 154 | 155 | 0.008658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_649_0_line_162 |  | 155 | 156 | 0.006235 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_649_0_line_163 |  | 156 | 157 | 0.049665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_649_0_line_164 |  | 157 | 158 | 0.017947 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_649_0_line_165 |  | 158 | 164 | 0.081187 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_649_0_line_166 |  | 159 | 160 | 0.027683 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
167 | MV_649_0_line_167 |  | 160 | 161 | 0.026099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_649_0_line_168 |  | 161 | 162 | 0.17034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_649_0_line_169 |  | 162 | 163 | 0.008056 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_649_0_line_170 |  | 162 | 164 | 0.16898 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_649_0_line_171 |  | 165 | 167 | 0.56701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_649_0_line_172 |  | 165 | 168 | 0.005579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_649_0_line_173 |  | 167 | 169 | 0.017184 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_649_0_line_174 |  | 172 | 173 | 0.0074599 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_649_0_line_175 |  | 174 | 175 | 0.027946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_649_0_line_176 |  | 175 | 176 | 0.0067091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_649_0_line_177 |  | 177 | 178 | 0.0079755 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_649_0_line_178 |  | 177 | 179 | 0.016173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_649_0_line_179 |  | 178 | 180 | 0.013443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_649_0_line_180 |  | 179 | 181 | 0.0041097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_649_0_line_181 |  | 180 | 182 | 0.0066574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_649_0_trafo_48 | 25 MVA 110/20 kV | 183 | 73 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2502408.5299 | 1115557.9777
1 | 2502394.1216 | 1115548.5042
2 | 2502620.9268 | 1115929.3642
3 | 2502164.7132 | 1116026.2494
4 | 2502683.5255 | 1116027.1289
5 | 2501801.1117 | 1116235.4242
6 | 2501740.9683 | 1116350.85
7 | 2501789.9103 | 1116229.8692
8 | 2501611.2213 | 1116437.8234
9 | 2501570.3006 | 1116274.265
10 | 2502194.999 | 1116019.6446
11 | 2502664.8284 | 1116070.6121
12 | 2502410.2804 | 1116217.2582
13 | 2501783.1247 | 1116530.4328
14 | 2501598.2804 | 1116444.4602
15 | 2501698.5421 | 1116707.2383
16 | 2501695.6793 | 1116690.7791
17 | 2501700.5719 | 1116718.7307
18 | 2501900.5412 | 1116651.9146
19 | 2501730.3152 | 1116567.6577
20 | 2501420.7423 | 1116380.7213
21 | 2501581.6 | 1116280.9815
22 | 2501413.2208 | 1116384.3307
23 | 2502425.9165 | 1116062.688
24 | 2502233.8882 | 1116195.1028
25 | 2502182.6752 | 1116232.5648
26 | 2501032.2129 | 1116092.3613
27 | 2501007.368 | 1116146.3457
28 | 2501116.9983 | 1115996.5711
29 | 2501011.3737 | 1116151.8948
30 | 2501140.3294 | 1115997.7351
31 | 2500960.4167 | 1115912.2346
32 | 2501212.0535 | 1115929.9105
33 | 2500854.3625 | 1116018.1262
34 | 2500965.6682 | 1115838.7028
35 | 2500999.2465 | 1115967.2002
36 | 2500972.4274 | 1115824.7057
37 | 2501158.5386 | 1115786.6061
38 | 2501216.4265 | 1115927.2263
39 | 2501179.4042 | 1115772.9346
40 | 2500720.9537 | 1116301.3123
41 | 2500718.656 | 1116301.9838
42 | 2500871.8413 | 1116021.2195
43 | 2500954.7137 | 1115792.2087
44 | 2500852.3995 | 1116445.2026
45 | 2500854.8439 | 1116448.7758
46 | 2500713.126 | 1116560.5581
47 | 2500743.8995 | 1116388.2124
48 | 2500831.2901 | 1116329.3984
49 | 2500815.8436 | 1116307.5157
50 | 2500843.2232 | 1116313.6042
51 | 2500830.825 | 1116608.9694
52 | 2500709.1989 | 1116557.4429
53 | 2500684.5892 | 1116575.1125
54 | 2500675.7629 | 1116426.5321
55 | 2500729.5542 | 1116761.2472
56 | 2500791.4734 | 1116732.4248
57 | 2500711.5703 | 1116771.9378
58 | 2500764.0027 | 1116825.688
59 | 2500828.5265 | 1116604.4042
60 | 2500660.7582 | 1116665.6388
61 | 2500845.5035 | 1116806.7855
62 | 2500773.7034 | 1116743.3958
63 | 2500665.0672 | 1116663.8002
64 | 2500994.8829 | 1116342.1276
65 | 2500997.5402 | 1116345.9754
66 | 2501053.0593 | 1116293.5017
67 | 2501071.3375 | 1116280.0234
68 | 2500911.2813 | 1116246.7921
69 | 2500882.9148 | 1116276.6086
70 | 2500942.774 | 1116214.5342
71 | 2501084.2941 | 1116269.2978
72 | 2500966.7004 | 1116202.5907
73 | 2501164.6813 | 1116353.3478
74 | 2501065.8033 | 1116217.9792
75 | 2501196.3526 | 1116335.7641
76 | 2501335.6919 | 1116649.03
77 | 2500847.7355 | 1116309.5499
78 | 2500675.9036 | 1116573.3103
79 | 2500664.2051 | 1116411.1176
80 | 2500656.1211 | 1116460.4424
81 | 2500657.9108 | 1116801.5592
82 | 2500714.3305 | 1116858.2241
83 | 2500859.5278 | 1116829.1252
84 | 2500995.0895 | 1115358.9555
85 | 2500578.9355 | 1115473.2822
86 | 2500595.2677 | 1115464.7753
87 | 2501024.0989 | 1115398.7948
88 | 2501030.38 | 1115416.8922
89 | 2500999.3015 | 1115365.7575
90 | 2501122.9807 | 1115461.2841
91 | 2501073.6721 | 1116228.533
92 | 2500961.898 | 1116736.8468
93 | 2500945.8658 | 1116704.9783
94 | 2501092.2066 | 1116707.7417
95 | 2501471.5359 | 1116542.5058
96 | 2501331.5009 | 1116654.802
97 | 2501481.3063 | 1116536.065
98 | 2501107.394 | 1116695.9639
99 | 2501124.5593 | 1116790.5089
100 | 2501199.1433 | 1116339.7432
101 | 2500974.6145 | 1116866.4528
102 | 2500962.4835 | 1116828.1608
103 | 2500955.4992 | 1116832.1109
104 | 2501121.4474 | 1116792.3721
105 | 2501393.9247 | 1116187.4157
106 | 2501407.0259 | 1116201.4888
107 | 2501349.4032 | 1116136.821
108 | 2501326.0565 | 1116307.8748
109 | 2501384.7052 | 1116102.6576
110 | 2501343.9482 | 1116345.7496
111 | 2501424.946 | 1116112.8083
112 | 2501361.3473 | 1116070.0117
113 | 2501396.1041 | 1116084.4461
114 | 2501434.6626 | 1116101.3921
115 | 2501372.0085 | 1116404.1078
116 | 2501238.7572 | 1116077.5332
117 | 2501380.4038 | 1116061.4354
118 | 2501456.0867 | 1116076.2784
119 | 2500653.7463 | 1116490.2555
120 | 2500614.3787 | 1116503.2561
121 | 2500659.398 | 1116459.6881
122 | 2500567.4491 | 1116516.2336
123 | 2500851.289 | 1116306.3564
124 | 2500878.9151 | 1116862.1282
125 | 2500652.2951 | 1116806.0987
126 | 2500670.6129 | 1116897.9998
127 | 2500503.6015 | 1116839.0069
128 | 2500587.1754 | 1116969.8372
129 | 2500662.1439 | 1116893.3359
130 | 2500506.8015 | 1116833.5954
131 | 2500591.5822 | 1116974.4343
132 | 2500679.671 | 1116875.5482
133 | 2500668.9254 | 1117010.0641
134 | 2500839.0281 | 1116944.8778
135 | 2500728.9289 | 1116897.6425
136 | 2500734.7174 | 1116893.7563
137 | 2501798.3213 | 1116417.3603
138 | 2501830.5956 | 1116454.9044
139 | 2502134.0375 | 1116481.6057
140 | 2502019.6584 | 1116490.2954
141 | 2502043.2043 | 1116516.297
142 | 2502118.2112 | 1116496.5238
143 | 2501690.204 | 1116659.2996
144 | 2501699.1393 | 1116743.9737
145 | 2501924.2873 | 1116647.4158
146 | 2501912.5748 | 1116627.2118
147 | 2501955.8686 | 1116699.0138
148 | 2501881.9456 | 1116666.9254
149 | 2500562.7055 | 1116607.1572
150 | 2500606.4265 | 1116629.0415
151 | 2500552.8546 | 1116607.2303
152 | 2500609.2803 | 1116625.1642
153 | 2500532.2319 | 1116585.1087
154 | 2501542.1509 | 1116647.6551
155 | 2501544.5014 | 1116639.3228
156 | 2501550.7539 | 1116639.2321
157 | 2501578.7935 | 1116679.9035
158 | 2501586.5848 | 1116696.0332
159 | 2501642.3085 | 1116745.5315
160 | 2501649.4529 | 1116772.2765
161 | 2501624.3739 | 1116779.7555
162 | 2501567.7526 | 1116887.5989
163 | 2501560.2907 | 1116890.6889
164 | 2501612.4573 | 1116772.9005
165 | 2501957.1964 | 1116723.7632
166 | 2501972.1615 | 1116688.937
167 | 2502349.9713 | 1116680.7962
168 | 2501961.9273 | 1116720.7847
169 | 2502340.9562 | 1116666.1548
170 | 2500910.9091 | 1116853.6099
171 | 2500609.5284 | 1116624.8271
172 | 2501459.7335 | 1116071.7109
173 | 2501464.388 | 1116065.8812
174 | 2501365.3848 | 1116037.7432
175 | 2501391.7842 | 1116031.5091
176 | 2501394.4942 | 1116037.6465
177 | 2501672.2976 | 1116645.0259
178 | 2501669.1299 | 1116637.7064
179 | 2501678.721 | 1116659.8684
180 | 2501663.4992 | 1116625.4993
181 | 2501680.3532 | 1116663.6401
182 | 2501660.7107 | 1116619.4541
183 | 2501164.6813 | 1116353.3478

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99444 | -0.004971 | 0.29339 | 0.1421
1 | 0.99445 | -0.0049092 | 0 | 0
2 | 0.99362 | 0.000991 | 0 | 0
3 | 0.99628 | -0.017655 | 0 | 0
4 | 0.99335 | -0.0012751 | 0.24681 | 0.11954
5 | 0.99776 | -0.027305 | 0 | 0
6 | 0.9981 | -0.029533 | 0 | 0
7 | 0.99776 | -0.02727 | 0.23716 | 0.11486
8 | 0.99709 | -0.020956 | 0 | 0
9 | 0.99901 | -0.018659 | 0 | 0
10 | 0.99627 | -0.017697 | 0.11161 | 0.054055
11 | 0.99329 | -0.0008761 | 0 | 0
12 | 0.99251 | 0.0047944 | 0 | 0
13 | 0.99586 | -0.010487 | 0 | 0
14 | 0.99708 | -0.021008 | 0.29756 | 0.14412
15 | 0.99466 | -1.1991e-05 | 0 | 0
16 | 0.99465 | 0.00011675 | 0.15216 | 0.073695
17 | 0.99464 | 0.00018363 | 0.070511 | 0.03415
18 | 0.99562 | -0.0084364 | 0 | 0
19 | 0.99583 | -0.010699 | 0.26897 | 0.13027
20 | 0.99932 | -0.012743 | 0 | 0
21 | 0.999 | -0.018601 | 0.3342 | 0.16186
22 | 0.99933 | -0.012538 | 0.54991 | 0.26633
23 | 0.99248 | 0.0050715 | 0.11738 | 0.056851
24 | 0.99222 | 0.0024433 | 0.1578 | 0.076427
25 | 0.99216 | 0.0028549 | 0 | 0
26 | 0.99859 | -0.033212 | 0.16367 | 0.079271
27 | 0.99887 | -0.031021 | 0.24546 | 0.11888
28 | 0.99803 | -0.037677 | 0 | 0
29 | 0.99889 | -0.031207 | 0 | 0
30 | 0.998 | -0.037405 | 0 | 0
31 | 0.99741 | -0.03315 | 0 | 0
32 | 0.99791 | -0.036592 | 0 | 0
33 | 0.99727 | -0.032058 | 0 | 0
34 | 0.99731 | -0.032441 | 0 | 0
35 | 0.99739 | -0.033281 | 0.15881 | 0.076917
36 | 0.99729 | -0.032308 | 0.32725 | 0.15849
37 | 0.99782 | -0.035775 | 0 | 0
38 | 0.9979 | -0.036568 | 0.38593 | 0.18692
39 | 0.99781 | -0.035681 | 0.31661 | 0.15334
40 | 0.99703 | -0.030084 | 0 | 0
41 | 0.99703 | -0.030075 | 0.28955 | 0.14023
42 | 0.99726 | -0.032124 | 0.3076 | 0.14898
43 | 0.99726 | -0.032177 | 0 | 0
44 | 0.99767 | -0.057921 | 0.32993 | 0.15979
45 | 0.99767 | -0.057938 | 0 | 0
46 | 0.99732 | -0.064226 | 0 | 0
47 | 0.99796 | -0.052669 | 0 | 0
48 | 0.9982 | -0.048331 | 0 | 0
49 | 0.9982 | -0.048298 | 0.10651 | 0.051586
50 | 0.99824 | -0.047628 | 0 | 0
51 | 0.99703 | -0.069402 | 0 | 0
52 | 0.99731 | -0.064202 | 0 | 0
53 | 0.9973 | -0.064034 | 0.50041 | 0.24236
54 | 0.9977 | -0.05436 | 0 | 0
55 | 0.99624 | -0.073666 | 0 | 0
56 | 0.99645 | -0.075591 | 0 | 0
57 | 0.99622 | -0.073526 | 0.27137 | 0.13143
58 | 0.99605 | -0.074936 | 0.085922 | 0.041614
59 | 0.99702 | -0.069383 | 0.31032 | 0.1503
60 | 0.99599 | -0.071286 | 0 | 0
61 | 0.99622 | -0.073527 | 0 | 0
62 | 0.99645 | -0.075541 | 0.20025 | 0.096986
63 | 0.99598 | -0.071202 | 1.4838 | 0.71864
64 | 0.99923 | -0.023534 | 0 | 0
65 | 0.99923 | -0.023516 | 0.31826 | 0.15414
66 | 0.99926 | -0.023822 | 0.071802 | 0.034775
67 | 0.99928 | -0.023925 | 0.071551 | 0.034654
68 | 0.99843 | -0.044296 | 0.20557 | 0.099564
69 | 0.99835 | -0.045726 | 0 | 0
70 | 0.99851 | -0.042694 | 0 | 0
71 | 0.99929 | -0.024016 | 0 | 0
72 | 0.99859 | -0.041421 | 0 | 0
73 | 1 | 0 | -21.9277 | -10.1176
74 | 0.99912 | -0.026999 | 0 | 0
75 | 0.99993 | -0.0013594 | 0.33005 | 0.15985
76 | 0.99957 | 0.0037035 | 0 | 0
77 | 0.99825 | -0.047423 | 0.2332 | 0.11294
78 | 0.99729 | -0.064025 | 0.40094 | 0.19418
79 | 0.9977 | -0.054324 | 0.13223 | 0.06404
80 | 0.99755 | -0.052924 | 0 | 0
81 | 0.99619 | -0.073743 | 0 | 0
82 | 0.99596 | -0.074104 | 0 | 0
83 | 0.99616 | -0.073028 | 0.248 | 0.12011
84 | 0.99673 | -0.028752 | 0 | 0
85 | 0.99665 | -0.028453 | 0 | 0
86 | 0.99665 | -0.028435 | 0.082635 | 0.040022
87 | 0.99667 | -0.028224 | 0 | 0
88 | 0.99666 | -0.028145 | 0.11711 | 0.056719
89 | 0.99673 | -0.028744 | 0.084411 | 0.040882
90 | 0.99662 | -0.028425 | 0.22332 | 0.10816
91 | 0.99912 | -0.026981 | 0.11741 | 0.056867
92 | 0.99558 | -0.068031 | 0.27266 | 0.13206
93 | 0.99559 | -0.068152 | 0 | 0
94 | 0.99567 | -0.068887 | 0 | 0
95 | 0.9995 | 0.0043132 | 0 | 0
96 | 0.99957 | 0.003733 | 0.34587 | 0.16751
97 | 0.9995 | 0.0043549 | 0.29832 | 0.14448
98 | 0.99567 | -0.068869 | 0.076986 | 0.037286
99 | 0.99574 | -0.069419 | 0 | 0
100 | 0.99992 | -0.0015285 | 0 | 0
101 | 0.99593 | -0.071022 | 0 | 0
102 | 0.99597 | -0.071396 | 0 | 0
103 | 0.99598 | -0.071456 | 0.27151 | 0.1315
104 | 0.99574 | -0.069403 | 0.36641 | 0.17746
105 | 0.99913 | -0.0046651 | 0.37676 | 0.18247
106 | 0.99917 | -0.0050559 | 0 | 0
107 | 0.99901 | -0.0035944 | 0 | 0
108 | 0.99955 | -0.0084339 | 0 | 0
109 | 0.99886 | -0.0022203 | 0 | 0
110 | 0.99949 | -0.0095993 | 0.30882 | 0.14957
111 | 0.99871 | -0.00091586 | 0 | 0
112 | 0.99883 | -0.0019293 | 0.36178 | 0.17522
113 | 0.99869 | -0.0006636 | 0.18126 | 0.087789
114 | 0.99871 | -0.00086625 | 0.10214 | 0.04947
115 | 0.9994 | -0.011323 | 0 | 0
116 | 0.99877 | -0.0022961 | 0.24606 | 0.11917
117 | 0.99868 | -0.00056028 | 0 | 0
118 | 0.9987 | -0.00079625 | 0 | 0
119 | 0.99749 | -0.052428 | 0 | 0
120 | 0.9974 | -0.053037 | 0.069406 | 0.033615
121 | 0.99754 | -0.052907 | 0.41604 | 0.2015
122 | 0.99733 | -0.052397 | 0 | 0
123 | 0.99826 | -0.047257 | 0 | 0
124 | 0.99609 | -0.072416 | 0 | 0
125 | 0.99619 | -0.073718 | 0.28864 | 0.13979
126 | 0.99584 | -0.073081 | 0 | 0
127 | 0.99573 | -0.07207 | 0 | 0
128 | 0.99579 | -0.072589 | 0 | 0
129 | 0.99585 | -0.07315 | 0.24429 | 0.11832
130 | 0.99573 | -0.072042 | 0.37697 | 0.18257
131 | 0.99579 | -0.072569 | 0.27303 | 0.13224
132 | 0.99588 | -0.073403 | 0 | 0
133 | 0.99595 | -0.073309 | 0.17707 | 0.085761
134 | 0.99601 | -0.072914 | 0.26642 | 0.12903
135 | 0.99594 | -0.073899 | 0 | 0
136 | 0.99593 | -0.073871 | 0.34188 | 0.16558
137 | 0.99153 | 0.0079718 | 0.32004 | 0.155
138 | 0.99155 | 0.007781 | 0 | 0
139 | 0.99176 | 0.0059677 | 0 | 0
140 | 0.99169 | 0.0065886 | 0 | 0
141 | 0.99168 | 0.0067143 | 0.29721 | 0.14395
142 | 0.99176 | 0.0059886 | 0.080447 | 0.038962
143 | 0.99463 | 0.00030536 | 0 | 0
144 | 0.99459 | 0.00060804 | 0 | 0
145 | 0.9956 | -0.0082985 | 0 | 0
146 | 0.9956 | -0.0082478 | 0.1811 | 0.087709
147 | 0.99556 | -0.00803 | 0 | 0
148 | 0.9956 | -0.0085385 | 0.35054 | 0.16978
149 | 0.99718 | -0.051064 | 0 | 0
150 | 0.9971 | -0.050244 | 0 | 0
151 | 0.99718 | -0.051002 | 0.32784 | 0.15878
152 | 0.99709 | -0.050212 | 0.28406 | 0.13758
153 | 0.99717 | -0.050931 | 0.19675 | 0.095288
154 | 0.99357 | 0.0096065 | 0.23666 | 0.11462
155 | 0.99358 | 0.0095818 | 0 | 0
156 | 0.99358 | 0.009564 | 0 | 0
157 | 0.99359 | 0.0094246 | 0.090623 | 0.043891
158 | 0.9936 | 0.0093554 | 0.11319 | 0.054819
159 | 0.99357 | 0.0094818 | 0.27358 | 0.1325
160 | 0.99358 | 0.0095745 | 0.35873 | 0.17374
161 | 0.9936 | 0.0093751 | 0 | 0
162 | 0.99374 | 0.0080992 | 0 | 0
163 | 0.99374 | 0.0081355 | 0.37223 | 0.18028
164 | 0.99365 | 0.0089372 | 0 | 0
165 | 0.99555 | -0.0078933 | 0 | 0
166 | 0.99556 | -0.0080145 | 0.068181 | 0.033022
167 | 0.99544 | -0.0071471 | 0 | 0
168 | 0.99554 | -0.0078761 | 0.2558 | 0.12389
169 | 0.99544 | -0.0071169 | 0.14691 | 0.071151
170 | 0.99604 | -0.071989 | 0 | 0
171 | 0.99709 | -0.050211 | 0.2755 | 0.13343
172 | 0.9987 | -0.00078369 | 0.072795 | 0.035256
173 | 0.9987 | -0.00077409 | 0.10777 | 0.052196
174 | 0.99866 | -0.00045511 | 0 | 0
175 | 0.99865 | -0.00034908 | 0.090512 | 0.043837
176 | 0.99865 | -0.00033073 | 0.2284 | 0.11062
177 | 0.99461 | 0.00043735 | 0.08362 | 0.040499
178 | 0.99461 | 0.00045315 | 0 | 0
179 | 0.99462 | 0.00038924 | 0.15731 | 0.076188
180 | 0.99461 | 0.00048001 | 0.083004 | 0.0402
181 | 0.99462 | 0.00036926 | 0.089753 | 0.043469
182 | 0.99461 | 0.00048673 | 0.083896 | 0.040633
183 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.29339 | -0.1421 | 0.2934 | 0.14208 | 2.7513e-06 | -1.8634e-05 | 0.0094632 | 0.009463 | 0.0094632 | 0.99444 | -0.004971 | 0.99445 | -0.0049092 | 4.5063
1 | 1.2226 | 0.52622 | -1.2216 | -0.5386 | 0.001077 | -0.012381 | 0.038639 | 0.038787 | 0.038787 | 0.99445 | -0.0049092 | 0.99362 | 0.000991 | 17.6303
2 | -1.516 | -0.6683 | 1.519 | 0.64656 | 0.0029349 | -0.021735 | 0.048095 | 0.047834 | 0.048095 | 0.99445 | -0.0049092 | 0.99628 | -0.017655 | 21.8612
3 | 1.2216 | 0.5386 | -1.2213 | -0.53854 | 0.00031117 | 5.8123e-05 | 0.038787 | 0.038788 | 0.038788 | 0.99362 | 0.000991 | 0.99335 | -0.0012751 | 18.4706
4 | 0.11161 | 0.054019 | -0.11161 | -0.054055 | 7.13e-07 | -3.6284e-05 | 0.0035928 | 0.0035933 | 0.0035933 | 0.99628 | -0.017655 | 0.99627 | -0.017697 | 1.7111
5 | -1.6306 | -0.70058 | 1.6331 | 0.68419 | 0.0025403 | -0.01639 | 0.051423 | 0.051229 | 0.051423 | 0.99628 | -0.017655 | 0.99776 | -0.027305 | 23.3741
6 | 0.97444 | 0.419 | -0.97438 | -0.4201 | 6.0052e-05 | -0.001097 | 0.030825 | 0.030838 | 0.030838 | 0.99335 | -0.0012751 | 0.99329 | -0.0008761 | 14.0172
7 | -1.8703 | -0.79876 | 1.871 | 0.79554 | 0.00066367 | -0.0032196 | 0.05884 | 0.058801 | 0.05884 | 0.99776 | -0.027305 | 0.9981 | -0.029533 | 26.7454
8 | 0.23716 | 0.11456 | -0.23716 | -0.11486 | 9.6784e-07 | -0.00029633 | 0.0076202 | 0.0076239 | 0.0076239 | 0.99776 | -0.027305 | 0.99776 | -0.02727 | 3.4654
9 | 3.7477 | 1.7396 | -3.7437 | -1.7434 | 0.0040522 | -0.003846 | 0.1195 | 0.11956 | 0.11956 | 0.9981 | -0.029533 | 0.99709 | -0.020956 | 54.3464
10 | -5.6187 | -2.5351 | 5.6233 | 2.5281 | 0.0046441 | -0.0069803 | 0.17828 | 0.17816 | 0.17828 | 0.9981 | -0.029533 | 0.99901 | -0.018659 | 49.2488
11 | 3.4461 | 1.5993 | -3.4416 | -1.6046 | 0.004541 | -0.0053139 | 0.10999 | 0.11007 | 0.11007 | 0.99709 | -0.020956 | 0.99586 | -0.010487 | 50.0331
12 | 0.29756 | 0.1441 | -0.29756 | -0.14412 | 2.3742e-06 | -1.5774e-05 | 0.009572 | 0.0095722 | 0.0095722 | 0.99709 | -0.020956 | 0.99708 | -0.021008 | 4.5582
13 | -5.9575 | -2.6896 | 5.9591 | 2.6726 | 0.0015806 | -0.017037 | 0.18888 | 0.18866 | 0.18888 | 0.99901 | -0.018659 | 0.99932 | -0.012743 | 22.4323
14 | 0.3342 | 0.16152 | -0.3342 | -0.16186 | 2.2157e-06 | -0.00034299 | 0.010726 | 0.01073 | 0.01073 | 0.99901 | -0.018659 | 0.999 | -0.018601 | 4.8773
15 | 0.97438 | 0.4201 | -0.97357 | -0.43476 | 0.00080826 | -0.014662 | 0.030838 | 0.031012 | 0.031012 | 0.99329 | -0.0008761 | 0.99251 | 0.0047944 | 14.0963
16 | 0.11739 | 0.051671 | -0.11738 | -0.056851 | 4.1606e-06 | -0.0051797 | 0.0037304 | 0.0037936 | 0.0037936 | 0.99251 | 0.0047944 | 0.99248 | 0.0050715 | 1.7244
17 | 0.85619 | 0.38309 | -0.85595 | -0.38315 | 0.00023577 | -6.1324e-05 | 0.027282 | 0.027284 | 0.027284 | 0.99251 | 0.0047944 | 0.99222 | 0.0024433 | 12.9924
18 | 1.0029 | 0.46167 | -1.0026 | -0.46613 | 0.0002625 | -0.0044593 | 0.032003 | 0.032058 | 0.032058 | 0.99586 | -0.010487 | 0.99562 | -0.0084364 | 14.5718
19 | 0.26898 | 0.1302 | -0.26897 | -0.13027 | 8.6391e-06 | -7.1082e-05 | 0.0086624 | 0.0086634 | 0.0086634 | 0.99586 | -0.010487 | 0.99583 | -0.010699 | 4.1254
20 | 2.1697 | 1.0127 | -2.1669 | -1.0222 | 0.0028023 | -0.0094548 | 0.069409 | 0.069536 | 0.069536 | 0.99586 | -0.010487 | 0.99466 | -1.1991e-05 | 31.6071
21 | 0.64977 | 0.31215 | -0.64976 | -0.31254 | 9.7641e-06 | -0.00039173 | 0.020921 | 0.020926 | 0.020926 | 0.99466 | -1.1991e-05 | 0.99465 | 0.00011675 | 9.5118
22 | 1.5171 | 0.71006 | -1.5171 | -0.71032 | 3.6825e-05 | -0.00026474 | 0.048615 | 0.048619 | 0.048619 | 0.99466 | -1.1991e-05 | 0.99464 | 0.00018363 | 22.0994
23 | 0.4976 | 0.23884 | -0.49759 | -0.23959 | 1.0953e-05 | -0.00075148 | 0.016019 | 0.016029 | 0.016029 | 0.99465 | 0.00011675 | 0.99463 | 0.00030536 | 7.2858
24 | 1.4466 | 0.67617 | -1.4465 | -0.67678 | 7.6361e-05 | -0.00060625 | 0.046345 | 0.046353 | 0.046353 | 0.99464 | 0.00018363 | 0.99459 | 0.00060804 | 21.0694
25 | 0.47094 | 0.21078 | -0.47092 | -0.21284 | 2.6227e-05 | -0.0020662 | 0.01496 | 0.014985 | 0.014985 | 0.99562 | -0.0084364 | 0.99556 | -0.00803 | 6.8112
26 | 0.35055 | 0.16975 | -0.35054 | -0.16978 | 5.4304e-06 | -2.4878e-05 | 0.011293 | 0.011293 | 0.011293 | 0.99562 | -0.0084364 | 0.9956 | -0.0085385 | 5.3778
27 | 0.1811 | 0.085603 | -0.1811 | -0.087157 | 2.9671e-06 | -0.0015533 | 0.005808 | 0.0058274 | 0.0058274 | 0.99562 | -0.0084364 | 0.9956 | -0.0082985 | 2.6488
28 | -5.9591 | -2.6726 | 5.9591 | 2.672 | 5.4338e-05 | -0.00058667 | 0.18866 | 0.18865 | 0.18866 | 0.99932 | -0.012743 | 0.99933 | -0.012538 | 22.4062
29 | -6.509 | -2.9383 | 6.5094 | 2.9352 | 0.00035594 | -0.0031614 | 0.2063 | 0.20625 | 0.2063 | 0.99933 | -0.012538 | 0.9994 | -0.011323 | 24.5007
30 | 0.69815 | 0.30673 | -0.69811 | -0.3082 | 4.1649e-05 | -0.0014763 | 0.022186 | 0.022203 | 0.022203 | 0.99222 | 0.0024433 | 0.99216 | 0.0028549 | 10.0924
31 | 0.69811 | 0.3082 | -0.69781 | -0.31872 | 0.00029882 | -0.010519 | 0.022203 | 0.02233 | 0.02233 | 0.99216 | 0.0028549 | 0.99176 | 0.0059677 | 10.1499
32 | -2.4599 | -1.1086 | 2.4605 | 1.1089 | 0.00064417 | 0.00033272 | 0.077999 | 0.077999 | 0.077999 | 0.99859 | -0.033212 | 0.99887 | -0.031021 | 37.1426
33 | 2.2962 | 1.0293 | -2.295 | -1.0287 | 0.0012061 | 0.00060328 | 0.072744 | 0.072746 | 0.072746 | 0.99859 | -0.033212 | 0.99803 | -0.037677 | 34.641
34 | -2.706 | -1.2278 | 2.7061 | 1.2277 | 6.7323e-05 | -0.00014293 | 0.085878 | 0.085876 | 0.085878 | 0.99887 | -0.031021 | 0.99889 | -0.031207 | 39.0354
35 | 0.70267 | 0.33093 | -0.70265 | -0.33174 | 2.3239e-05 | -0.00081297 | 0.022466 | 0.022476 | 0.022476 | 0.99803 | -0.037677 | 0.998 | -0.037405 | 10.2162
36 | 1.5923 | 0.6978 | -1.5913 | -0.70482 | 0.0010431 | -0.0070224 | 0.050286 | 0.050372 | 0.050372 | 0.99803 | -0.037677 | 0.99741 | -0.03315 | 22.8962
37 | -11.7584 | -5.4732 | 11.7607 | 5.4684 | 0.0023201 | -0.0047526 | 0.37482 | 0.37474 | 0.37482 | 0.99889 | -0.031207 | 0.99912 | -0.026999 | 44.5157
38 | 9.0524 | 4.2455 | -9.0503 | -4.2428 | 0.0020107 | 0.0027366 | 0.28895 | 0.28895 | 0.28895 | 0.99889 | -0.031207 | 0.99859 | -0.041421 | 35.2382
39 | 0.70265 | 0.33174 | -0.70258 | -0.33415 | 6.8912e-05 | -0.0024061 | 0.022476 | 0.022506 | 0.022506 | 0.998 | -0.037405 | 0.99791 | -0.036592 | 10.2299
40 | 0.59731 | 0.26913 | -0.59723 | -0.27341 | 8.7227e-05 | -0.0042784 | 0.018962 | 0.019013 | 0.019013 | 0.99741 | -0.03315 | 0.99727 | -0.032058 | 8.6423
41 | 0.83517 | 0.35885 | -0.83508 | -0.36117 | 9.1164e-05 | -0.0023137 | 0.026309 | 0.026336 | 0.026336 | 0.99741 | -0.03315 | 0.99731 | -0.032441 | 11.9708
42 | 0.15882 | 0.076839 | -0.15881 | -0.076917 | 3.127e-06 | -7.7964e-05 | 0.0051063 | 0.0051073 | 0.0051073 | 0.99741 | -0.03315 | 0.99739 | -0.033281 | 2.432
43 | 0.31664 | 0.14735 | -0.31661 | -0.15275 | 3.1195e-05 | -0.0053977 | 0.010103 | 0.01017 | 0.01017 | 0.99791 | -0.036592 | 0.99782 | -0.035775 | 4.6228
44 | 0.38593 | 0.18679 | -0.38593 | -0.18692 | 1.0517e-06 | -0.00012142 | 0.012403 | 0.012405 | 0.012405 | 0.99791 | -0.036592 | 0.9979 | -0.036568 | 5.6386
45 | 0.3076 | 0.14896 | -0.3076 | -0.14898 | 3.0954e-06 | -1.9136e-05 | 0.0098931 | 0.0098934 | 0.0098934 | 0.99727 | -0.032058 | 0.99726 | -0.032124 | 4.7111
46 | 0.28962 | 0.12445 | -0.28955 | -0.14018 | 7.5237e-05 | -0.015726 | 0.0091248 | 0.0093142 | 0.0093142 | 0.99727 | -0.032058 | 0.99703 | -0.030084 | 4.2337
47 | 0.83508 | 0.36117 | -0.83506 | -0.3616 | 1.6997e-05 | -0.00043081 | 0.026336 | 0.026341 | 0.026341 | 0.99731 | -0.032441 | 0.99729 | -0.032308 | 11.973
48 | 0.50782 | 0.20311 | -0.5078 | -0.20402 | 1.292e-05 | -0.00091256 | 0.015831 | 0.015841 | 0.015841 | 0.99729 | -0.032308 | 0.99726 | -0.032177 | 7.2006
49 | 0.31661 | 0.15275 | -0.31661 | -0.15334 | 3.44e-06 | -0.00059078 | 0.01017 | 0.010178 | 0.010178 | 0.99782 | -0.035775 | 0.99781 | -0.035681 | 4.6262
50 | 0.28955 | 0.14018 | -0.28955 | -0.14023 | 2.7645e-07 | -5.6572e-05 | 0.0093142 | 0.0093149 | 0.0093149 | 0.99703 | -0.030084 | 0.99703 | -0.030075 | 4.2341
51 | 0.5078 | 0.20402 | -0.50752 | -0.22393 | 0.00028618 | -0.019909 | 0.015841 | 0.016066 | 0.016066 | 0.99726 | -0.032177 | 0.99673 | -0.028752 | 7.3028
52 | -0.32993 | -0.15979 | 0.32993 | 0.15969 | 6.4973e-07 | -0.00010261 | 0.010607 | 0.010606 | 0.010607 | 0.99767 | -0.057921 | 0.99767 | -0.057938 | 4.8214
53 | 6.4658 | 3.0402 | -6.4638 | -3.0573 | 0.0019426 | -0.017077 | 0.20674 | 0.20697 | 0.20697 | 0.99767 | -0.057938 | 0.99732 | -0.064226 | 24.5807
54 | -6.7957 | -3.1999 | 6.7974 | 3.1864 | 0.0017023 | -0.01343 | 0.21734 | 0.21716 | 0.21734 | 0.99767 | -0.057938 | 0.99796 | -0.052669 | 25.8125
55 | 5.5625 | 2.6225 | -5.5611 | -2.6393 | 0.0013816 | -0.016811 | 0.178 | 0.17823 | 0.17823 | 0.99732 | -0.064226 | 0.99703 | -0.069402 | 21.1671
56 | 0.40095 | 0.19319 | -0.40095 | -0.19331 | 1.1088e-06 | -0.00011851 | 0.012882 | 0.012884 | 0.012884 | 0.99732 | -0.064226 | 0.99731 | -0.064202 | 5.8564
57 | 0.50042 | 0.2416 | -0.50041 | -0.24236 | 1.109e-05 | -0.00075876 | 0.016084 | 0.016094 | 0.016094 | 0.99732 | -0.064226 | 0.9973 | -0.064034 | 7.3155
58 | 1.703 | 0.81351 | -1.7026 | -0.81334 | 0.00041513 | 0.0001671 | 0.054593 | 0.054595 | 0.054595 | 0.99796 | -0.052669 | 0.9977 | -0.05436 | 25.9974
59 | -8.5004 | -3.9999 | 8.5021 | 3.9917 | 0.0017539 | -0.0082723 | 0.27175 | 0.27163 | 0.27175 | 0.99796 | -0.052669 | 0.9982 | -0.048331 | 32.2743
60 | 0.10651 | 0.050947 | -0.10651 | -0.051586 | 4.1864e-07 | -0.00063826 | 0.0034145 | 0.0034225 | 0.0034225 | 0.9982 | -0.048331 | 0.9982 | -0.048298 | 1.5557
61 | -8.6086 | -4.0426 | 8.6089 | 4.0413 | 0.00028755 | -0.0013175 | 0.27504 | 0.27502 | 0.27504 | 0.9982 | -0.048331 | 0.99824 | -0.047628 | 32.6653
62 | -8.6089 | -4.0413 | 8.609 | 4.0409 | 8.3837e-05 | -0.00038419 | 0.27502 | 0.27502 | 0.27502 | 0.99824 | -0.047628 | 0.99825 | -0.047423 | 32.663
63 | 0.31032 | 0.15018 | -0.31032 | -0.1503 | 6.7967e-07 | -0.00012106 | 0.0099818 | 0.0099833 | 0.0099833 | 0.99703 | -0.069402 | 0.99702 | -0.069383 | 4.5379
64 | 5.2508 | 2.4891 | -5.248 | -2.494 | 0.0027563 | -0.0048646 | 0.16825 | 0.16833 | 0.16833 | 0.99703 | -0.069402 | 0.99645 | -0.075591 | 46.5002
65 | 0.40095 | 0.19331 | -0.40094 | -0.19418 | 8.1787e-06 | -0.00087326 | 0.012884 | 0.012895 | 0.012895 | 0.99731 | -0.064202 | 0.99729 | -0.064025 | 5.8614
66 | 0.13223 | 0.063495 | -0.13223 | -0.06404 | 5.521e-07 | -0.00054464 | 0.0042441 | 0.0042509 | 0.0042509 | 0.9977 | -0.05436 | 0.9977 | -0.054324 | 1.9322
67 | 1.5703 | 0.74985 | -1.5701 | -0.75164 | 0.00026645 | -0.0017909 | 0.050351 | 0.050374 | 0.050374 | 0.9977 | -0.05436 | 0.99755 | -0.052924 | 22.8972
68 | -1.8827 | -0.89629 | 1.8831 | 0.89431 | 0.00043353 | -0.0019808 | 0.06042 | 0.060394 | 0.06042 | 0.99624 | -0.073666 | 0.99645 | -0.075591 | 27.4636
69 | 0.56003 | 0.2705 | -0.56002 | -0.27099 | 9.0545e-06 | -0.000492 | 0.018022 | 0.018028 | 0.018028 | 0.99624 | -0.073666 | 0.99622 | -0.073526 | 8.1945
70 | 1.3226 | 0.62579 | -1.3224 | -0.62573 | 0.00023404 | 6.0036e-05 | 0.042399 | 0.0424 | 0.0424 | 0.99624 | -0.073666 | 0.99605 | -0.074936 | 20.1904
71 | 1.4846 | 0.71299 | -1.4838 | -0.71853 | 0.00074054 | -0.0055459 | 0.047711 | 0.047784 | 0.047784 | 0.99645 | -0.075591 | 0.99599 | -0.071286 | 21.7199
72 | 1.6801 | 0.79018 | -1.6797 | -0.79265 | 0.00042381 | -0.0024735 | 0.053787 | 0.053819 | 0.053819 | 0.99645 | -0.075591 | 0.99622 | -0.073527 | 24.4633
73 | 0.20025 | 0.096491 | -0.20025 | -0.096986 | 1.1573e-06 | -0.00049475 | 0.0064397 | 0.006446 | 0.006446 | 0.99645 | -0.075591 | 0.99645 | -0.075541 | 2.93
74 | 0.28865 | 0.13956 | -0.28864 | -0.13962 | 9.4267e-06 | -6.6712e-05 | 0.0092905 | 0.0092914 | 0.0092914 | 0.99622 | -0.073526 | 0.99619 | -0.073743 | 4.4245
75 | 1.2365 | 0.58412 | -1.2364 | -0.58549 | 0.00012457 | -0.0013695 | 0.039633 | 0.03965 | 0.03965 | 0.99605 | -0.074936 | 0.99596 | -0.074104 | 18.0229
76 | 1.4838 | 0.71853 | -1.4838 | -0.71864 | 1.4245e-05 | -0.00010645 | 0.047784 | 0.047785 | 0.047785 | 0.99599 | -0.071286 | 0.99598 | -0.071202 | 21.7205
77 | 1.6797 | 0.79265 | -1.6796 | -0.79324 | 0.00010195 | -0.00059437 | 0.053819 | 0.053827 | 0.053827 | 0.99622 | -0.073527 | 0.99616 | -0.073028 | 24.4668
78 | 0.31826 | 0.15403 | -0.31826 | -0.15414 | 6.5098e-07 | -0.00011121 | 0.010215 | 0.010216 | 0.010216 | 0.99923 | -0.023534 | 0.99923 | -0.023516 | 4.6437
79 | -0.31826 | -0.15403 | 0.31827 | 0.1522 | 1.0708e-05 | -0.0018336 | 0.010215 | 0.010192 | 0.010215 | 0.99923 | -0.023534 | 0.99926 | -0.023822 | 4.643
80 | -0.39007 | -0.18697 | 0.39008 | 0.18643 | 4.7319e-06 | -0.00054004 | 0.012496 | 0.01249 | 0.012496 | 0.99926 | -0.023822 | 0.99928 | -0.023925 | 5.6802
81 | -0.46163 | -0.22108 | 0.46163 | 0.22068 | 4.9281e-06 | -0.00040123 | 0.014786 | 0.014781 | 0.014786 | 0.99928 | -0.023925 | 0.99929 | -0.024016 | 6.721
82 | 8.8435 | 4.1482 | -8.8429 | -4.1508 | 0.00060001 | -0.0025792 | 0.28243 | 0.28246 | 0.28246 | 0.99843 | -0.044296 | 0.99835 | -0.045726 | 33.5468
83 | -9.0491 | -4.2478 | 9.0498 | 4.245 | 0.00068817 | -0.0027976 | 0.28903 | 0.28899 | 0.28903 | 0.99843 | -0.044296 | 0.99851 | -0.042694 | 34.3265
84 | 8.8429 | 4.1508 | -8.8423 | -4.1536 | 0.0006431 | -0.002763 | 0.28246 | 0.28251 | 0.28251 | 0.99835 | -0.045726 | 0.99826 | -0.047257 | 33.5517
85 | -9.0498 | -4.245 | 9.0503 | 4.2428 | 0.00054609 | -0.0022211 | 0.28899 | 0.28895 | 0.28899 | 0.99851 | -0.042694 | 0.99859 | -0.041421 | 34.3215
86 | -12.3414 | -5.7424 | 12.3479 | 5.7513 | 0.0064093 | 0.0089786 | 0.39322 | 0.39322 | 0.39322 | 0.99929 | -0.024016 | 1 | 0 | 47.9542
87 | 11.8798 | 5.5217 | -11.8782 | -5.525 | 0.0016604 | -0.0033074 | 0.37844 | 0.3785 | 0.3785 | 0.99929 | -0.024016 | 0.99912 | -0.026999 | 44.9529
88 | 8.9213 | 4.061 | -8.9208 | -4.0634 | 0.00055232 | -0.0023724 | 0.28296 | 0.283 | 0.283 | 1 | 0 | 0.99993 | -0.0013594 | 33.6102
89 | 0.64452 | 0.29478 | -0.64422 | -0.3073 | 0.0002975 | -0.012523 | 0.020459 | 0.020613 | 0.020613 | 1 | 0 | 0.99957 | 0.0037035 | 9.3697
90 | 0.11742 | 0.056553 | -0.11741 | -0.056867 | 2.4944e-07 | -0.00031369 | 0.0037655 | 0.0037694 | 0.0037694 | 0.99912 | -0.026999 | 0.99912 | -0.026981 | 1.7134
91 | 8.5907 | 3.9035 | -8.5907 | -3.9038 | 6.5961e-05 | -0.00031048 | 0.27241 | 0.27242 | 0.27242 | 0.99993 | -0.0013594 | 0.99992 | -0.0015285 | 32.3537
92 | 0.29834 | 0.13996 | -0.29832 | -0.1442 | 2.1683e-05 | -0.0042476 | 0.0095171 | 0.0095699 | 0.0095699 | 0.99957 | 0.0037035 | 0.9995 | 0.0043132 | 4.35
93 | 0.34587 | 0.16734 | -0.34587 | -0.16751 | 1.1718e-06 | -0.00016967 | 0.011097 | 0.011099 | 0.011099 | 0.99957 | 0.0037035 | 0.99957 | 0.003733 | 5.0449
94 | -8.8422 | -4.1539 | 8.8423 | 4.1536 | 6.9667e-05 | -0.00029922 | 0.28251 | 0.28251 | 0.28251 | 0.99825 | -0.047423 | 0.99826 | -0.047257 | 33.5522
95 | 0.41604 | 0.20142 | -0.41604 | -0.2015 | 8.0099e-07 | -7.9426e-05 | 0.013376 | 0.013377 | 0.013377 | 0.99755 | -0.052924 | 0.99754 | -0.052907 | 6.0805
96 | 1.154 | 0.55022 | -1.154 | -0.55108 | 6.7877e-05 | -0.00086206 | 0.036998 | 0.037009 | 0.037009 | 0.99755 | -0.052924 | 0.99749 | -0.052428 | 16.8222
97 | 0.28864 | 0.13962 | -0.28864 | -0.13979 | 8.3092e-07 | -0.00017054 | 0.0092914 | 0.0092935 | 0.0092935 | 0.99619 | -0.073743 | 0.99619 | -0.073718 | 4.2243
98 | 0.34189 | 0.16423 | -0.34188 | -0.16542 | 8.103e-06 | -0.0011854 | 0.010994 | 0.011008 | 0.011008 | 0.99596 | -0.074104 | 0.99594 | -0.073899 | 5.0039
99 | 0.89447 | 0.42126 | -0.89439 | -0.42288 | 7.629e-05 | -0.0016241 | 0.028657 | 0.028678 | 0.028678 | 0.99596 | -0.074104 | 0.99588 | -0.073403 | 13.0353
100 | 1.4316 | 0.67313 | -1.4315 | -0.67401 | 0.00010738 | -0.0008747 | 0.045842 | 0.045853 | 0.045853 | 0.99616 | -0.073028 | 0.99609 | -0.072416 | 20.8425
101 | 0.084411 | 0.040692 | -0.084411 | -0.040882 | 7.8694e-08 | -0.00018964 | 0.002714 | 0.0027164 | 0.0027164 | 0.99673 | -0.028752 | 0.99673 | -0.028744 | 1.2347
102 | 0.082641 | 0.022083 | -0.082635 | -0.039586 | 6.4305e-06 | -0.017503 | 0.0024775 | 0.0026539 | 0.0026539 | 0.99673 | -0.028752 | 0.99665 | -0.028453 | 1.2063
103 | 0.34047 | 0.16115 | -0.34045 | -0.16431 | 2.127e-05 | -0.0031575 | 0.01091 | 0.010949 | 0.010949 | 0.99673 | -0.028752 | 0.99667 | -0.028224 | 4.9768
104 | 0.082635 | 0.039586 | -0.082635 | -0.040022 | 1.731e-07 | -0.00043567 | 0.0026539 | 0.0026594 | 0.0026594 | 0.99665 | -0.028453 | 0.99665 | -0.028435 | 1.2088
105 | 0.34045 | 0.16431 | -0.34044 | -0.16476 | 3.0674e-06 | -0.00045343 | 0.010949 | 0.010955 | 0.010955 | 0.99667 | -0.028224 | 0.99666 | -0.028145 | 4.9794
106 | 0.22333 | 0.10804 | -0.22332 | -0.10816 | 9.4497e-06 | -0.00011585 | 0.0071858 | 0.0071874 | 0.0071874 | 0.99666 | -0.028145 | 0.99662 | -0.028425 | 3.4226
107 | -0.27266 | -0.13206 | 0.27266 | 0.13118 | 3.8298e-06 | -0.00087978 | 0.0087844 | 0.0087733 | 0.0087844 | 0.99558 | -0.068031 | 0.99559 | -0.068152 | 3.9929
108 | -0.27266 | -0.13118 | 0.27269 | 0.12548 | 2.4539e-05 | -0.0056908 | 0.0087733 | 0.008703 | 0.0087733 | 0.99559 | -0.068152 | 0.99567 | -0.068887 | 3.9879
109 | 0.076986 | 0.036832 | -0.076986 | -0.037286 | 1.5718e-07 | -0.00045406 | 0.0024744 | 0.0024801 | 0.0024801 | 0.99567 | -0.068887 | 0.99567 | -0.068869 | 1.1273
110 | -0.34968 | -0.16232 | 0.3497 | 0.15888 | 2.4196e-05 | -0.00344 | 0.011177 | 0.011135 | 0.011177 | 0.99567 | -0.068887 | 0.99574 | -0.069419 | 5.0805
111 | 0.29832 | 0.1442 | -0.29832 | -0.14448 | 1.4284e-06 | -0.00027815 | 0.0095699 | 0.0095734 | 0.0095734 | 0.9995 | 0.0043132 | 0.9995 | 0.0043549 | 4.3516
112 | 0.36641 | 0.17737 | -0.36641 | -0.17746 | 6.73e-07 | -8.5473e-05 | 0.011802 | 0.011803 | 0.011803 | 0.99574 | -0.069419 | 0.99574 | -0.069403 | 5.3649
113 | -0.71611 | -0.33625 | 0.71625 | 0.33143 | 0.00014384 | -0.0048198 | 0.022936 | 0.022876 | 0.022936 | 0.99574 | -0.069419 | 0.99593 | -0.071022 | 10.4252
114 | 8.5907 | 3.9038 | -8.588 | -3.9165 | 0.0027004 | -0.012695 | 0.27242 | 0.2726 | 0.2726 | 0.99992 | -0.0015285 | 0.99955 | -0.0084339 | 32.3753
115 | -0.71625 | -0.33143 | 0.71629 | 0.33028 | 3.4325e-05 | -0.0011541 | 0.022876 | 0.022862 | 0.022876 | 0.99593 | -0.071022 | 0.99597 | -0.071396 | 10.3982
116 | -0.71629 | -0.33028 | 0.71629 | 0.33009 | 5.5857e-06 | -0.00018796 | 0.022862 | 0.022859 | 0.022862 | 0.99597 | -0.071396 | 0.99598 | -0.071456 | 10.3917
117 | -0.9878 | -0.46159 | 0.98786 | 0.46044 | 6.5811e-05 | -0.0011502 | 0.031602 | 0.031588 | 0.031602 | 0.99598 | -0.071456 | 0.99604 | -0.071989 | 14.3646
118 | -1.7681 | -0.84336 | 1.7682 | 0.84292 | 8.2122e-05 | -0.0004334 | 0.056598 | 0.056593 | 0.056598 | 0.99913 | -0.0046651 | 0.99917 | -0.0050559 | 25.7265
119 | 1.3913 | 0.66088 | -1.3911 | -0.66243 | 0.00017813 | -0.001552 | 0.044503 | 0.044523 | 0.044523 | 0.99913 | -0.0046651 | 0.99901 | -0.0035944 | 20.2379
120 | -1.7682 | -0.84292 | 1.7689 | 0.83915 | 0.0007145 | -0.0037764 | 0.056593 | 0.056543 | 0.056593 | 0.99917 | -0.0050559 | 0.99955 | -0.0084339 | 25.7239
121 | 1.3911 | 0.66243 | -1.3909 | -0.66441 | 0.00022712 | -0.0019762 | 0.044523 | 0.044549 | 0.044549 | 0.99901 | -0.0035944 | 0.99886 | -0.0022203 | 20.2494
122 | 6.8191 | 3.0774 | -6.8187 | -3.0803 | 0.00035792 | -0.0028687 | 0.21606 | 0.2161 | 0.2161 | 0.99955 | -0.0084339 | 0.99949 | -0.0095993 | 25.6654
123 | 0.78303 | 0.37111 | -0.78291 | -0.37453 | 0.0001218 | -0.003423 | 0.025043 | 0.025086 | 0.025086 | 0.99886 | -0.0022203 | 0.99871 | -0.00091586 | 11.4027
124 | 0.60788 | 0.2933 | -0.60786 | -0.29426 | 2.0403e-05 | -0.00095016 | 0.019506 | 0.019518 | 0.019518 | 0.99886 | -0.0022203 | 0.99883 | -0.0019293 | 8.8719
125 | 6.5099 | 2.9307 | -6.5094 | -2.9352 | 0.00050398 | -0.0044794 | 0.2062 | 0.20625 | 0.20625 | 0.99949 | -0.0095993 | 0.9994 | -0.011323 | 24.4958
126 | 0.5002 | 0.23907 | -0.50019 | -0.24009 | 1.4848e-05 | -0.0010262 | 0.016025 | 0.016037 | 0.016037 | 0.99871 | -0.00091586 | 0.99869 | -0.0006636 | 7.2898
127 | 0.28271 | 0.13546 | -0.28271 | -0.13582 | 1.6441e-06 | -0.00035653 | 0.0090613 | 0.0090658 | 0.0090658 | 0.99871 | -0.00091586 | 0.99871 | -0.00086625 | 4.1208
128 | 0.24608 | 0.11904 | -0.24606 | -0.11917 | 1.3662e-05 | -0.00013771 | 0.0079003 | 0.0079022 | 0.0079022 | 0.99883 | -0.0019293 | 0.99877 | -0.0022961 | 3.7629
129 | 0.31892 | 0.1523 | -0.31892 | -0.15297 | 3.8843e-06 | -0.0006622 | 0.010216 | 0.010224 | 0.010224 | 0.99869 | -0.0006636 | 0.99868 | -0.00056028 | 4.6474
130 | 0.18057 | 0.086349 | -0.18057 | -0.087135 | 1.4775e-06 | -0.00078568 | 0.0057854 | 0.0057952 | 0.0057952 | 0.99871 | -0.00086625 | 0.9987 | -0.00079625 | 2.6342
131 | 0.31892 | 0.15297 | -0.31892 | -0.15363 | 3.9154e-06 | -0.0006664 | 0.010224 | 0.010233 | 0.010233 | 0.99868 | -0.00056028 | 0.99866 | -0.00045511 | 4.6512
132 | 0.18057 | 0.087135 | -0.18057 | -0.087274 | 2.6213e-07 | -0.00013911 | 0.0057952 | 0.0057969 | 0.0057969 | 0.9987 | -0.00079625 | 0.9987 | -0.00078369 | 2.635
133 | 1.154 | 0.55108 | -1.1539 | -0.55107 | 0.00010117 | 1.4131e-05 | 0.037009 | 0.037009 | 0.037009 | 0.99749 | -0.052428 | 0.9974 | -0.053037 | 17.6235
134 | 1.0845 | 0.51746 | -1.0844 | -0.51864 | 8.2067e-05 | -0.0011823 | 0.034777 | 0.034793 | 0.034793 | 0.9974 | -0.053037 | 0.99733 | -0.052397 | 15.8148
135 | 1.0844 | 0.51864 | -1.0842 | -0.52108 | 0.00016978 | -0.002442 | 0.034793 | 0.034824 | 0.034824 | 0.99733 | -0.052397 | 0.99718 | -0.051064 | 15.829
136 | 0.98792 | 0.45951 | -0.98786 | -0.46044 | 5.2962e-05 | -0.00092649 | 0.031576 | 0.031588 | 0.031588 | 0.99609 | -0.072416 | 0.99604 | -0.071989 | 14.3581
137 | 0.44354 | 0.2145 | -0.44351 | -0.21459 | 3.3371e-05 | -8.7898e-05 | 0.014278 | 0.01428 | 0.01428 | 0.99609 | -0.072416 | 0.99601 | -0.072914 | 6.7999
138 | 0.37702 | 0.17696 | -0.37697 | -0.18243 | 4.5308e-05 | -0.0054683 | 0.012073 | 0.012141 | 0.012141 | 0.99584 | -0.073081 | 0.99573 | -0.07207 | 5.5188
139 | 0.27305 | 0.12842 | -0.27303 | -0.13209 | 1.5922e-05 | -0.0036671 | 0.0087469 | 0.0087927 | 0.0087927 | 0.99584 | -0.073081 | 0.99579 | -0.072589 | 3.9967
140 | -0.65007 | -0.30538 | 0.65007 | 0.30515 | 5.5817e-06 | -0.00022677 | 0.02082 | 0.020817 | 0.02082 | 0.99584 | -0.073081 | 0.99585 | -0.07315 | 9.4635
141 | 0.37697 | 0.18243 | -0.37697 | -0.18257 | 1.2366e-06 | -0.00014837 | 0.012141 | 0.012143 | 0.012143 | 0.99573 | -0.07207 | 0.99573 | -0.072042 | 5.5196
142 | 0.27303 | 0.13209 | -0.27303 | -0.13224 | 6.5658e-07 | -0.00015038 | 0.0087927 | 0.0087946 | 0.0087946 | 0.99579 | -0.072589 | 0.99579 | -0.072569 | 3.9975
143 | -0.89436 | -0.42347 | 0.89439 | 0.42288 | 2.7387e-05 | -0.00058238 | 0.028685 | 0.028678 | 0.028685 | 0.99585 | -0.07315 | 0.99588 | -0.073403 | 13.0386
144 | -0.17707 | -0.085761 | 0.17708 | 0.085552 | 1.055e-05 | -0.00020912 | 0.0057028 | 0.0057 | 0.0057028 | 0.99595 | -0.073309 | 0.99601 | -0.072914 | 2.7156
145 | 0.34188 | 0.16542 | -0.34188 | -0.16558 | 1.1259e-06 | -0.00016445 | 0.011008 | 0.011011 | 0.011011 | 0.99594 | -0.073899 | 0.99593 | -0.073871 | 5.0048
146 | -0.32004 | -0.155 | 0.32005 | 0.15384 | 7.0668e-06 | -0.0011588 | 0.010353 | 0.010338 | 0.010353 | 0.99153 | 0.0079718 | 0.99155 | 0.007781 | 4.7059
147 | -0.32005 | -0.15384 | 0.32012 | 0.1414 | 7.4652e-05 | -0.012448 | 0.010338 | 0.010186 | 0.010338 | 0.99155 | 0.007781 | 0.99176 | 0.0059677 | 4.6992
148 | 0.080448 | 0.038452 | -0.080447 | -0.038962 | 1.9606e-07 | -0.0005107 | 0.0025953 | 0.0026018 | 0.0026018 | 0.99176 | 0.0059677 | 0.99176 | 0.0059886 | 1.1826
149 | 0.29724 | 0.13887 | -0.29722 | -0.14313 | 2.2199e-05 | -0.0042516 | 0.0095496 | 0.0096027 | 0.0096027 | 0.99176 | 0.0059677 | 0.99169 | 0.0065886 | 4.3649
150 | 0.29722 | 0.14313 | -0.29721 | -0.14395 | 4.3181e-06 | -0.00082146 | 0.0096027 | 0.0096131 | 0.0096131 | 0.99169 | 0.0065886 | 0.99168 | 0.0067143 | 4.3696
151 | 0.49759 | 0.23959 | -0.49758 | -0.23985 | 3.6929e-06 | -0.00025317 | 0.016029 | 0.016032 | 0.016032 | 0.99463 | 0.00030536 | 0.99462 | 0.00036926 | 7.2872
152 | 1.4465 | 0.67678 | -1.4452 | -0.68721 | 0.0013201 | -0.010438 | 0.046353 | 0.046487 | 0.046487 | 0.99459 | 0.00060804 | 0.99374 | 0.0080992 | 21.1304
153 | 0.1811 | 0.087157 | -0.1811 | -0.087709 | 1.06e-06 | -0.00055238 | 0.0058274 | 0.0058344 | 0.0058344 | 0.9956 | -0.0082985 | 0.9956 | -0.0082478 | 2.652
154 | 0.40274 | 0.18027 | -0.40273 | -0.18109 | 7.5912e-06 | -0.00081916 | 0.012794 | 0.012804 | 0.012804 | 0.99556 | -0.00803 | 0.99555 | -0.0078933 | 5.82
155 | 0.068181 | 0.032568 | -0.068181 | -0.033022 | 1.2308e-07 | -0.00045331 | 0.002191 | 0.0021967 | 0.0021967 | 0.99556 | -0.00803 | 0.99556 | -0.0080145 | 0.99848
156 | 0.55962 | 0.26797 | -0.55957 | -0.27089 | 5.3343e-05 | -0.0029183 | 0.017962 | 0.017999 | 0.017999 | 0.99718 | -0.051064 | 0.9971 | -0.050244 | 8.1813
157 | 0.52459 | 0.25311 | -0.52459 | -0.25334 | 3.7287e-06 | -0.00023208 | 0.016862 | 0.016865 | 0.016865 | 0.99718 | -0.051064 | 0.99718 | -0.051002 | 7.6657
158 | 0.55957 | 0.27089 | -0.55957 | -0.271 | 2.0823e-06 | -0.00011366 | 0.017999 | 0.018 | 0.018 | 0.9971 | -0.050244 | 0.99709 | -0.050212 | 8.182
159 | 0.19675 | 0.094563 | -0.19675 | -0.095288 | 1.6323e-06 | -0.00072535 | 0.0063194 | 0.0063285 | 0.0063285 | 0.99718 | -0.051002 | 0.99717 | -0.050931 | 2.8766
160 | 0.2755 | 0.13342 | -0.2755 | -0.13343 | 4.4005e-08 | -9.923e-06 | 0.0088624 | 0.0088626 | 0.0088626 | 0.99709 | -0.050212 | 0.99709 | -0.050211 | 4.0284
161 | -0.23666 | -0.11462 | 0.23666 | 0.11442 | 6.7443e-07 | -0.00020387 | 0.00764 | 0.0076374 | 0.00764 | 0.99357 | 0.0096065 | 0.99358 | 0.0095818 | 3.4727
162 | -0.23666 | -0.11442 | 0.23666 | 0.11427 | 4.8541e-07 | -0.00014682 | 0.0076374 | 0.0076356 | 0.0076374 | 0.99358 | 0.0095818 | 0.99358 | 0.009564 | 3.4716
163 | -0.23666 | -0.11427 | 0.23667 | 0.1131 | 3.8581e-06 | -0.0011695 | 0.0076356 | 0.0076208 | 0.0076356 | 0.99358 | 0.009564 | 0.99359 | 0.0094246 | 3.4707
164 | -0.32729 | -0.15699 | 0.32729 | 0.15657 | 2.6636e-06 | -0.00042225 | 0.010546 | 0.010541 | 0.010546 | 0.99359 | 0.0094246 | 0.9936 | 0.0093554 | 4.7938
165 | -0.44048 | -0.21139 | 0.4405 | 0.20948 | 2.1802e-05 | -0.0019073 | 0.014195 | 0.014171 | 0.014195 | 0.9936 | 0.0093554 | 0.99365 | 0.0089372 | 6.4522
166 | -0.27358 | -0.1325 | 0.27359 | 0.13247 | 3.8472e-06 | -3.0215e-05 | 0.008832 | 0.0088316 | 0.008832 | 0.99357 | 0.0094818 | 0.99358 | 0.0095745 | 4.2057
167 | -0.63232 | -0.30621 | 0.63233 | 0.3056 | 1.4512e-05 | -0.00061088 | 0.020412 | 0.020404 | 0.020412 | 0.99358 | 0.0095745 | 0.9936 | 0.0093751 | 9.2782
168 | -0.63233 | -0.3056 | 0.63243 | 0.30161 | 9.444e-05 | -0.0039877 | 0.020404 | 0.020354 | 0.020404 | 0.9936 | 0.0093751 | 0.99374 | 0.0080992 | 9.2747
169 | 0.37223 | 0.18009 | -0.37223 | -0.18028 | 1.5521e-06 | -0.00018948 | 0.012012 | 0.012015 | 0.012015 | 0.99374 | 0.0080992 | 0.99374 | 0.0081355 | 5.4612
170 | 0.44055 | 0.20551 | -0.4405 | -0.20948 | 4.5144e-05 | -0.0039705 | 0.014122 | 0.014171 | 0.014171 | 0.99374 | 0.0080992 | 0.99365 | 0.0089372 | 6.4413
171 | 0.14693 | 0.057333 | -0.14691 | -0.070745 | 1.6349e-05 | -0.013411 | 0.0045732 | 0.0047286 | 0.0047286 | 0.99555 | -0.0078933 | 0.99544 | -0.0071471 | 2.1493
172 | 0.2558 | 0.12376 | -0.2558 | -0.12389 | 5.0576e-07 | -0.00013187 | 0.0082399 | 0.0082416 | 0.0082416 | 0.99555 | -0.0078933 | 0.99554 | -0.0078761 | 3.7462
173 | 0.14691 | 0.070745 | -0.14691 | -0.071151 | 5.135e-07 | -0.0004064 | 0.0047286 | 0.0047337 | 0.0047337 | 0.99544 | -0.0071471 | 0.99544 | -0.0071169 | 2.1517
174 | 0.10777 | 0.052018 | -0.10777 | -0.052196 | 1.1924e-07 | -0.00017761 | 0.003459 | 0.0034612 | 0.0034612 | 0.9987 | -0.00078369 | 0.9987 | -0.00077409 | 1.5733
175 | 0.31892 | 0.15363 | -0.31891 | -0.1543 | 3.9096e-06 | -0.0006643 | 0.010233 | 0.010241 | 0.010241 | 0.99866 | -0.00045511 | 0.99865 | -0.00034908 | 4.655
176 | 0.2284 | 0.11046 | -0.2284 | -0.11062 | 4.8188e-07 | -0.00015961 | 0.0073338 | 0.0073358 | 0.0073358 | 0.99865 | -0.00034908 | 0.99865 | -0.00033073 | 3.3345
177 | 0.1669 | 0.08017 | -0.1669 | -0.080359 | 3.0763e-07 | -0.00018829 | 0.005374 | 0.0053764 | 0.0053764 | 0.99461 | 0.00043735 | 0.99461 | 0.00045315 | 2.4438
178 | -0.25052 | -0.12067 | 0.25052 | 0.12029 | 1.4055e-06 | -0.00038158 | 0.0080706 | 0.0080658 | 0.0080706 | 0.99461 | 0.00043735 | 0.99462 | 0.00038924 | 3.6685
179 | 0.1669 | 0.080359 | -0.1669 | -0.080676 | 5.1914e-07 | -0.00031736 | 0.0053764 | 0.0053804 | 0.0053804 | 0.99461 | 0.00045315 | 0.99461 | 0.00048001 | 2.4456
180 | -0.40783 | -0.19648 | 0.40783 | 0.19638 | 9.4703e-07 | -9.679e-05 | 0.013139 | 0.013138 | 0.013139 | 0.99462 | 0.00038924 | 0.99462 | 0.00036926 | 5.9722
181 | 0.083896 | 0.040476 | -0.083896 | -0.040633 | 6.5005e-08 | -0.00015722 | 0.0027036 | 0.0027056 | 0.0027056 | 0.99461 | 0.00048001 | 0.99461 | 0.00048673 | 1.2298

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.9277 | 10.1176

## res_load
| p_mw | q_mvar
0 | 0.29339 | 0.1421
1 | 0.24681 | 0.11954
2 | 0.23716 | 0.11486
3 | 0.11161 | 0.054055
4 | 0.29756 | 0.14412
5 | 0.15216 | 0.073695
6 | 0.070511 | 0.03415
7 | 0.26897 | 0.13027
8 | 0.3342 | 0.16186
9 | 0.54991 | 0.26633
10 | 0.11738 | 0.056851
11 | 0.1578 | 0.076427
12 | 0.16367 | 0.079271
13 | 0.24546 | 0.11888
14 | 0.15881 | 0.076917
15 | 0.32725 | 0.15849
16 | 0.38593 | 0.18692
17 | 0.31661 | 0.15334
18 | 0.28955 | 0.14023
19 | 0.3076 | 0.14898
20 | 0.32993 | 0.15979
21 | 0.10651 | 0.051586
22 | 0.50041 | 0.24236
23 | 0.27137 | 0.13143
24 | 0.085922 | 0.041614
25 | 0.31032 | 0.1503
26 | 0.20025 | 0.096986
27 | 1.4838 | 0.71864
28 | 0.31826 | 0.15414
29 | 0.071802 | 0.034775
30 | 0.071551 | 0.034654
31 | 0.20557 | 0.099564
32 | 0.33005 | 0.15985
33 | 0.2332 | 0.11294
34 | 0.40094 | 0.19418
35 | 0.13223 | 0.06404
36 | 0.248 | 0.12011
37 | 0.082635 | 0.040022
38 | 0.11711 | 0.056719
39 | 0.084411 | 0.040882
40 | 0.22332 | 0.10816
41 | 0.11741 | 0.056867
42 | 0.27266 | 0.13206
43 | 0.34587 | 0.16751
44 | 0.29832 | 0.14448
45 | 0.076986 | 0.037286
46 | 0.27151 | 0.1315
47 | 0.36641 | 0.17746
48 | 0.37676 | 0.18247
49 | 0.30882 | 0.14957
50 | 0.36178 | 0.17522
51 | 0.18126 | 0.087789
52 | 0.10214 | 0.04947
53 | 0.24606 | 0.11917
54 | 0.069406 | 0.033615
55 | 0.41604 | 0.2015
56 | 0.28864 | 0.13979
57 | 0.24429 | 0.11832
58 | 0.37697 | 0.18257
59 | 0.27303 | 0.13224
60 | 0.17707 | 0.085761
61 | 0.26642 | 0.12903
62 | 0.34188 | 0.16558
63 | 0.32004 | 0.155
64 | 0.29721 | 0.14395
65 | 0.080447 | 0.038962
66 | 0.1811 | 0.087709
67 | 0.35054 | 0.16978
68 | 0.32784 | 0.15878
69 | 0.28406 | 0.13758
70 | 0.19675 | 0.095288
71 | 0.23666 | 0.11462
72 | 0.090623 | 0.043891
73 | 0.11319 | 0.054819
74 | 0.27358 | 0.1325
75 | 0.35873 | 0.17374
76 | 0.37223 | 0.18028
77 | 0.068181 | 0.033022
78 | 0.2558 | 0.12389
79 | 0.14691 | 0.071151
80 | 0.2755 | 0.13343
81 | 0.072795 | 0.035256
82 | 0.10777 | 0.052196
83 | 0.090512 | 0.043837
84 | 0.2284 | 0.11062
85 | 0.08362 | 0.040499
86 | 0.15731 | 0.076188
87 | 0.083004 | 0.0402
88 | 0.089753 | 0.043469
89 | 0.083896 | 0.040633

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1