## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_653_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_653_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_653_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_653_0_node_85 | 20 | n |  | TRUE
4 | bus_MV_653_0_node_6 | 20 | n |  | TRUE
5 | bus_MV_653_0_node_7 | 20 | n |  | TRUE
6 | bus_MV_653_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_653_0_node_73 | 20 | n |  | TRUE
8 | bus_MV_653_0_node_81 | 20 | n |  | TRUE
9 | bus_MV_653_0_node_59 | 20 | n |  | TRUE
10 | bus_MV_653_0_node_80 | 20 | n |  | TRUE
11 | bus_MV_653_0_node_84 | 20 | n |  | TRUE
12 | bus_MV_653_0_node_9 | 20 | n |  | TRUE
13 | bus_MV_653_0_node_48 | 20 | n |  | TRUE
14 | bus_MV_653_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_653_0_node_51 | 20 | n |  | TRUE
16 | bus_MV_653_0_node_82 | 20 | n |  | TRUE
17 | bus_MV_653_0_node_79 | 20 | n |  | TRUE
18 | bus_MV_653_0_node_66 | 20 | n |  | TRUE
19 | bus_MV_653_0_node_116 | 20 | n |  | TRUE
20 | bus_MV_653_0_node_68 | 20 | n |  | TRUE
21 | bus_MV_653_0_node_117 | 20 | n |  | TRUE
22 | bus_MV_653_0_node_32 | 20 | n |  | TRUE
23 | bus_MV_653_0_node_63 | 20 | n |  | TRUE
24 | bus_MV_653_0_node_35 | 20 | n |  | TRUE
25 | bus_MV_653_0_node_52 | 20 | n |  | TRUE
26 | bus_MV_653_0_node_53 | 20 | n |  | TRUE
27 | bus_MV_653_0_node_34 | 20 | n |  | TRUE
28 | bus_MV_653_0_node_10 | 20 | n |  | TRUE
29 | bus_MV_653_0_node_11 | 20 | n |  | TRUE
30 | bus_MV_653_0_node_12 | 20 | n |  | TRUE
31 | bus_MV_653_0_node_13 | 20 | n |  | TRUE
32 | bus_MV_653_0_node_104 | 20 | n |  | TRUE
33 | bus_MV_653_0_node_38 | 20 | n |  | TRUE
34 | bus_MV_653_0_node_158 | 20 | n |  | TRUE
35 | bus_MV_653_0_node_103 | 20 | n |  | TRUE
36 | bus_MV_653_0_node_33 | 20 | n |  | TRUE
37 | bus_MV_653_0_node_36 | 20 | n |  | TRUE
38 | bus_MV_653_0_node_37 | 20 | n |  | TRUE
39 | bus_MV_653_0_node_42 | 20 | n |  | TRUE
40 | bus_MV_653_0_node_112 | 20 | n |  | TRUE
41 | bus_MV_653_0_node_74 | 20 | n |  | TRUE
42 | bus_MV_653_0_node_140 | 20 | n |  | TRUE
43 | bus_MV_653_0_node_14 | 20 | n |  | TRUE
44 | bus_MV_653_0_node_15 | 20 | n |  | TRUE
45 | bus_MV_653_0_node_16 | 20 | n |  | TRUE
46 | bus_MV_653_0_node_71 | 20 | n |  | TRUE
47 | bus_MV_653_0_node_17 | 20 | n |  | TRUE
48 | bus_MV_653_0_node_26 | 20 | n |  | TRUE
49 | bus_MV_653_0_node_57 | 20 | n |  | TRUE
50 | bus_MV_653_0_node_98 | 20 | n |  | TRUE
51 | bus_MV_653_0_node_24 | 20 | n |  | TRUE
52 | bus_MV_653_0_node_70 | 20 | n |  | TRUE
53 | bus_MV_653_0_node_55 | 20 | n |  | TRUE
54 | bus_MV_653_0_node_18 | 20 | n |  | TRUE
55 | bus_MV_653_0_node_19 | 20 | n |  | TRUE
56 | bus_MV_653_0_node_20 | 20 | n |  | TRUE
57 | bus_MV_653_0_node_21 | 20 | n |  | TRUE
58 | bus_MV_653_0_node_72 | 20 | n |  | TRUE
59 | bus_MV_653_0_node_141 | 20 | n |  | TRUE
60 | bus_MV_653_0_node_149 | 20 | n |  | TRUE
61 | bus_MV_653_0_node_23 | 20 | n |  | TRUE
62 | bus_MV_653_0_node_22 | 20 | n |  | TRUE
63 | bus_MV_653_0_node_137 | 20 | n |  | TRUE
64 | bus_MV_653_0_node_150 | 20 | n |  | TRUE
65 | bus_MV_653_0_node_25 | 20 | n |  | TRUE
66 | bus_MV_653_0_node_27 | 20 | n |  | TRUE
67 | bus_MV_653_0_node_28 | 20 | n |  | TRUE
68 | bus_MV_653_0_node_106 | 20 | n |  | TRUE
69 | bus_MV_653_0_node_153 | 20 | n |  | TRUE
70 | bus_MV_653_0_node_105 | 20 | n |  | TRUE
71 | bus_MV_653_0_node_29 | 20 | n |  | TRUE
72 | bus_MV_653_0_node_30 | 20 | n |  | TRUE
73 | bus_MV_653_0_node_31 | 20 | n |  | TRUE
74 | bus_MV_653_0_node_139 | 20 | n |  | TRUE
75 | bus_MV_653_0_node_138 | 20 | n |  | TRUE
76 | bus_MV_653_0_node_118 | 20 | n |  | TRUE
77 | bus_MV_653_0_node_142 | 20 | n |  | TRUE
78 | bus_MV_653_0_node_60 | 20 | n |  | TRUE
79 | bus_MV_653_0_node_41 | 20 | n |  | TRUE
80 | bus_MV_653_0_node_49 | 20 | n |  | TRUE
81 | bus_MV_653_0_node_40 | 20 | n |  | TRUE
82 | bus_MV_653_0_node_164 | 20 | n |  | TRUE
83 | bus_MV_653_0_node_96 | 20 | n |  | TRUE
84 | bus_MV_653_0_node_39 | 20 | n |  | TRUE
85 | bus_MV_653_0_node_46 | 20 | n |  | TRUE
86 | bus_MV_653_0_node_43 | 20 | n |  | TRUE
87 | bus_MV_653_0_node_44 | 20 | n |  | TRUE
88 | bus_MV_653_0_node_45 | 20 | n |  | TRUE
89 | bus_MV_653_0_node_47 | 20 | n |  | TRUE
90 | bus_MV_653_0_node_157 | 20 | n |  | TRUE
91 | bus_MV_653_0_node_54 | 20 | n |  | TRUE
92 | bus_MV_653_0_node_56 | 20 | n |  | TRUE
93 | bus_MV_653_0_node_65 | 20 | n |  | TRUE
94 | bus_MV_653_0_node_58 | 20 | n |  | TRUE
95 | bus_MV_653_0_node_64 | 20 | n |  | TRUE
96 | bus_MV_653_0_node_61 | 20 | n |  | TRUE
97 | bus_MV_653_0_node_69 | 20 | n |  | TRUE
98 | bus_MV_653_0_node_97 | 20 | n |  | TRUE
99 | bus_MV_653_0_node_115 | 20 | n |  | TRUE
100 | bus_MV_653_0_node_88 | 20 | n |  | TRUE
101 | bus_MV_653_0_node_78 | 20 | n |  | TRUE
102 | bus_MV_653_0_node_114 | 20 | n |  | TRUE
103 | bus_MV_653_0_node_77 | 20 | n |  | TRUE
104 | bus_MV_653_0_node_75 | 20 | n |  | TRUE
105 | bus_MV_653_0_node_76 | 20 | n |  | TRUE
106 | bus_MV_653_0_node_62 | 20 | n |  | TRUE
107 | bus_MV_653_0_node_99 | 20 | n |  | TRUE
108 | bus_MV_653_0_node_113 | 20 | n |  | TRUE
109 | bus_MV_653_0_node_163 | 20 | n |  | TRUE
110 | bus_MV_653_0_node_83 | 20 | n |  | TRUE
111 | bus_MV_653_0_node_159 | 20 | n |  | TRUE
112 | bus_MV_653_0_node_160 | 20 | n |  | TRUE
113 | bus_MV_653_0_node_86 | 20 | n |  | TRUE
114 | bus_MV_653_0_node_87 | 20 | n |  | TRUE
115 | bus_MV_653_0_node_89 | 20 | n |  | TRUE
116 | bus_MV_653_0_node_95 | 20 | n |  | TRUE
117 | bus_MV_653_0_node_94 | 20 | n |  | TRUE
118 | bus_MV_653_0_node_90 | 20 | n |  | TRUE
119 | bus_MV_653_0_node_91 | 20 | n |  | TRUE
120 | bus_MV_653_0_node_92 | 20 | n |  | TRUE
121 | bus_MV_653_0_node_93 | 20 | n |  | TRUE
122 | bus_MV_653_0_node_100 | 20 | n |  | TRUE
123 | bus_MV_653_0_node_162 | 20 | n |  | TRUE
124 | bus_MV_653_0_node_123 | 20 | n |  | TRUE
125 | bus_MV_653_0_node_131 | 20 | n |  | TRUE
126 | bus_MV_653_0_node_120 | 20 | n |  | TRUE
127 | bus_MV_653_0_node_122 | 20 | n |  | TRUE
128 | bus_MV_653_0_node_119 | 20 | n |  | TRUE
129 | bus_MV_653_0_node_126 | 20 | n |  | TRUE
130 | bus_MV_653_0_node_127 | 20 | n |  | TRUE
131 | bus_MV_653_0_node_133 | 20 | n |  | TRUE
132 | bus_MV_653_0_node_129 | 20 | n |  | TRUE
133 | bus_MV_653_0_node_101 | 20 | n |  | TRUE
134 | bus_MV_653_0_node_102 | 20 | n |  | TRUE
135 | bus_MV_653_0_node_107 | 20 | n |  | TRUE
136 | bus_MV_653_0_node_108 | 20 | n |  | TRUE
137 | bus_MV_653_0_node_109 | 20 | n |  | TRUE
138 | bus_MV_653_0_node_110 | 20 | n |  | TRUE
139 | bus_MV_653_0_node_111 | 20 | n |  | TRUE
140 | bus_MV_653_0_node_143 | 20 | n |  | TRUE
141 | bus_MV_653_0_node_148 | 20 | n |  | TRUE
142 | bus_MV_653_0_node_121 | 20 | n |  | TRUE
143 | bus_MV_653_0_node_124 | 20 | n |  | TRUE
144 | bus_MV_653_0_node_125 | 20 | n |  | TRUE
145 | bus_MV_653_0_node_128 | 20 | n |  | TRUE
146 | bus_MV_653_0_node_154 | 20 | n |  | TRUE
147 | bus_MV_653_0_node_155 | 20 | n |  | TRUE
148 | bus_MV_653_0_node_130 | 20 | n |  | TRUE
149 | bus_MV_653_0_node_132 | 20 | n |  | TRUE
150 | bus_MV_653_0_node_135 | 20 | n |  | TRUE
151 | bus_MV_653_0_node_136 | 20 | n |  | TRUE
152 | bus_MV_653_0_node_134 | 20 | n |  | TRUE
153 | bus_MV_653_0_node_156 | 20 | n |  | TRUE
154 | bus_MV_653_0_node_146 | 20 | n |  | TRUE
155 | bus_MV_653_0_node_144 | 20 | n |  | TRUE
156 | bus_MV_653_0_node_145 | 20 | n |  | TRUE
157 | bus_MV_653_0_node_147 | 20 | n |  | TRUE
158 | bus_MV_653_0_node_152 | 20 | n |  | TRUE
159 | bus_MV_653_0_node_151 | 20 | n |  | TRUE
160 | bus_MV_653_0_node_161 | 20 | n |  | TRUE
161 | bus_HV_653_0_node_61 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_653_0_load_0 | 0 | 0.3964 | 0.19199 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_653_0_load_85 | 3 | 0.1421 | 0.06882 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_653_0_load_73 | 7 | 0.32094 | 0.15544 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_653_0_load_59 | 9 | 0.37973 | 0.18391 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_653_0_load_84 | 11 | 0.096791 | 0.046878 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_653_0_load_48 | 13 | 0.25401 | 0.12302 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_653_0_load_8 | 14 | 0.31869 | 0.15435 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_653_0_load_79 | 17 | 0.072204 | 0.03497 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_653_0_load_116 | 19 | 0.40971 | 0.19843 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_653_0_load_117 | 21 | 0.11729 | 0.056808 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_653_0_load_10 | 28 | 0.23337 | 0.11303 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_653_0_load_104 | 32 | 0.077305 | 0.03744 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_653_0_load_158 | 34 | 0.29817 | 0.14441 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_653_0_load_33 | 36 | 0.21796 | 0.10556 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_653_0_load_42 | 39 | 0.2154 | 0.10432 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_653_0_load_112 | 40 | 0.11461 | 0.055508 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_653_0_load_74 | 41 | 0.10553 | 0.051112 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_653_0_load_14 | 43 | 0.25963 | 0.12575 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_653_0_load_26 | 48 | 0.072581 | 0.035153 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_653_0_load_57 | 49 | 0.17099 | 0.082815 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_653_0_load_98 | 50 | 0.3411 | 0.1652 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_653_0_load_24 | 51 | 0.2494 | 0.12079 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_653_0_load_70 | 52 | 0.33558 | 0.16253 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_653_0_load_55 | 53 | 0.10554 | 0.051114 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_653_0_load_18 | 54 | 0.24302 | 0.1177 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_653_0_load_141 | 59 | 0.0705 | 0.034145 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_653_0_load_149 | 60 | 0.086148 | 0.041723 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_653_0_load_22 | 62 | 0.2558 | 0.12389 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_653_0_load_137 | 63 | 0.068208 | 0.033035 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_653_0_load_153 | 69 | 0.30623 | 0.14831 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_653_0_load_105 | 70 | 0.091779 | 0.04445 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_653_0_load_29 | 71 | 0.31462 | 0.15238 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_653_0_load_138 | 75 | 0.095322 | 0.046167 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_653_0_load_118 | 76 | 0.1419 | 0.068723 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_653_0_load_142 | 77 | 0.10182 | 0.049312 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_653_0_load_60 | 78 | 0.31918 | 0.15458 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_653_0_load_49 | 80 | 0.24393 | 0.11814 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_653_0_load_164 | 82 | 0.4108 | 0.19896 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_653_0_load_96 | 83 | 0.084473 | 0.040912 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_653_0_load_39 | 84 | 0.28267 | 0.1369 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_653_0_load_43 | 86 | 0.27093 | 0.13122 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_653_0_load_157 | 90 | 0.078825 | 0.038177 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_653_0_load_54 | 91 | 0.40327 | 0.19531 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_653_0_load_69 | 97 | 0.23884 | 0.11568 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_653_0_load_97 | 98 | 0.07194 | 0.034842 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_653_0_load_115 | 99 | 0.40713 | 0.19718 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_653_0_load_114 | 102 | 0.26043 | 0.12613 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_653_0_load_75 | 104 | 0.086893 | 0.042084 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_653_0_load_62 | 106 | 0.071811 | 0.03478 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_653_0_load_113 | 108 | 0.13019 | 0.063053 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_653_0_load_163 | 109 | 0.2679 | 0.12975 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_653_0_load_159 | 111 | 0.088942 | 0.043077 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_653_0_load_86 | 113 | 0.10531 | 0.051006 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_653_0_load_95 | 116 | 0.087295 | 0.042279 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_653_0_load_90 | 118 | 0.16484 | 0.079835 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_653_0_load_93 | 121 | 0.06907 | 0.033452 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_653_0_load_162 | 123 | 0.092532 | 0.044815 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_653_0_load_119 | 128 | 0.82524 | 0.39968 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_653_0_load_126 | 129 | 0.11404 | 0.055231 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_653_0_load_127 | 130 | 0.084339 | 0.040847 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_653_0_load_133 | 131 | 0.73889 | 0.35786 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_653_0_load_129 | 132 | 0.11147 | 0.053986 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_653_0_load_101 | 133 | 0.075055 | 0.036351 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_653_0_load_107 | 135 | 0.093509 | 0.045288 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_653_0_load_110 | 138 | 0.069579 | 0.033699 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_653_0_load_148 | 141 | 0.095003 | 0.046012 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_653_0_load_125 | 144 | 0.069393 | 0.033608 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_653_0_load_128 | 145 | 0.085244 | 0.041285 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_653_0_load_155 | 147 | 0.36204 | 0.17535 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_653_0_load_135 | 150 | 0.27092 | 0.13121 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_653_0_load_134 | 152 | 0.075875 | 0.036748 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_653_0_load_156 | 153 | 0.15913 | 0.07707 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_653_0_load_144 | 155 | 0.074936 | 0.036293 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_653_0_load_145 | 156 | 0.069381 | 0.033603 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_653_0_load_152 | 158 | 0.086807 | 0.042042 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_653_0_load_161 | 160 | 0.30874 | 0.14953 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 96 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_653_0_line_0 |  | 0 | 1 | 0.002689 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
1 | MV_653_0_line_1 |  | 0 | 2 | 0.006156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_653_0_line_2 |  | 0 | 3 | 0.11228 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_653_0_line_3 |  | 1 | 4 | 0.091124 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
4 | MV_653_0_line_4 |  | 2 | 5 | 0.012368 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_653_0_line_5 |  | 4 | 9 | 0.002869 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
6 | MV_653_0_line_6 |  | 5 | 10 | 0.050162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_653_0_line_7 |  | 5 | 11 | 0.024315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_653_0_line_8 |  | 6 | 7 | 0.006333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_653_0_line_9 |  | 6 | 8 | 0.075868 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_653_0_line_10 |  | 7 | 15 | 0.037742 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_653_0_line_11 |  | 8 | 16 | 0.084907 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_653_0_line_12 |  | 8 | 17 | 0.014642 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_653_0_line_13 |  | 9 | 18 | 0.0889 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_653_0_line_14 |  | 9 | 19 | 0.07855 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
15 | MV_653_0_line_15 |  | 10 | 17 | 0.013784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_653_0_line_16 |  | 12 | 13 | 0.18342 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_653_0_line_17 |  | 12 | 14 | 0.069879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_653_0_line_18 |  | 13 | 24 | 0.006048 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_653_0_line_19 |  | 15 | 25 | 0.15046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_653_0_line_20 |  | 16 | 109 | 0.011271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_653_0_line_21 |  | 16 | 110 | 0.027318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_653_0_line_22 |  | 18 | 104 | 0.016362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_653_0_line_23 |  | 19 | 95 | 0.03506 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
24 | MV_653_0_line_24 |  | 20 | 21 | 0.026714 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_653_0_line_25 |  | 20 | 22 | 0.038801 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
26 | MV_653_0_line_26 |  | 20 | 23 | 0.037231 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_653_0_line_27 |  | 22 | 76 | 0.013339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_653_0_line_28 |  | 22 | 73 | 0.032232 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_653_0_line_29 |  | 23 | 78 | 0.011245 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
30 | MV_653_0_line_30 |  | 24 | 25 | 0.13271 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_653_0_line_31 |  | 24 | 26 | 0.18112 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_653_0_line_32 |  | 24 | 27 | 0.10327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_653_0_line_33 |  | 25 | 82 | 0.010396 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_653_0_line_34 |  | 26 | 83 | 0.045356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_653_0_line_35 |  | 27 | 36 | 0.00522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_653_0_line_36 |  | 28 | 29 | 0.026475 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_653_0_line_37 |  | 29 | 30 | 0.11717 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_653_0_line_38 |  | 29 | 31 | 0.79198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_653_0_line_39 |  | 30 | 32 | 0.015123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_653_0_line_40 |  | 31 | 33 | 0.093467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_653_0_line_41 |  | 31 | 34 | 0.028346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_653_0_line_42 |  | 32 | 35 | 0.037665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_653_0_line_43 |  | 33 | 41 | 0.003091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_653_0_line_44 |  | 34 | 42 | 0.015726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_653_0_line_45 |  | 35 | 134 | 0.016377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_653_0_line_46 |  | 36 | 79 | 0.14783 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_653_0_line_47 |  | 37 | 38 | 0.15464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_653_0_line_48 |  | 37 | 39 | 0.005375 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_653_0_line_49 |  | 38 | 40 | 0.021211 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_653_0_line_50 |  | 39 | 84 | 0.11058 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_653_0_line_51 |  | 40 | 85 | 0.021915 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_653_0_line_52 |  | 42 | 74 | 0.28446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_653_0_line_53 |  | 43 | 44 | 0.053523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_653_0_line_54 |  | 44 | 45 | 0.083975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_653_0_line_55 |  | 45 | 46 | 0.012749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_653_0_line_56 |  | 45 | 47 | 0.015001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_653_0_line_57 |  | 46 | 50 | 0.016005 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_653_0_line_58 |  | 47 | 48 | 0.014916 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
59 | MV_653_0_line_59 |  | 47 | 49 | 0.032188 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_653_0_line_60 |  | 48 | 51 | 0.016845 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
61 | MV_653_0_line_61 |  | 49 | 52 | 0.024578 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_653_0_line_62 |  | 49 | 53 | 0.045534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_653_0_line_63 |  | 50 | 107 | 0.011113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_653_0_line_64 |  | 51 | 65 | 0.013633 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_653_0_line_65 |  | 54 | 55 | 0.012029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_653_0_line_66 |  | 55 | 56 | 0.06303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_653_0_line_67 |  | 56 | 57 | 0.069728 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
68 | MV_653_0_line_68 |  | 56 | 58 | 0.068275 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
69 | MV_653_0_line_69 |  | 56 | 59 | 0.03088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_653_0_line_70 |  | 57 | 60 | 0.0086119 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
71 | MV_653_0_line_71 |  | 58 | 63 | 0.037258 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
72 | MV_653_0_line_72 |  | 58 | 61 | 0.067645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_653_0_line_73 |  | 60 | 64 | 0.0097176 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
74 | MV_653_0_line_74 |  | 61 | 62 | 0.01269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_653_0_line_75 |  | 63 | 66 | 0.010454 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
76 | MV_653_0_line_76 |  | 64 | 159 | 0.004952 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
77 | MV_653_0_line_77 |  | 65 | 66 | 0.062641 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
78 | MV_653_0_line_78 |  | 65 | 67 | 0.028516 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_653_0_line_79 |  | 67 | 68 | 0.057282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_653_0_line_80 |  | 67 | 69 | 0.036837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_653_0_line_81 |  | 68 | 70 | 0.037645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_653_0_line_82 |  | 71 | 72 | 0.020592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_653_0_line_83 |  | 72 | 73 | 0.027696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_653_0_line_84 |  | 73 | 74 | 0.27375 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
85 | MV_653_0_line_85 |  | 73 | 75 | 0.00635 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_653_0_line_86 |  | 74 | 77 | 0.01694 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
87 | MV_653_0_line_87 |  | 77 | 139 | 0.020737 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_653_0_line_88 |  | 78 | 106 | 0.0067272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_653_0_line_89 |  | 78 | 96 | 0.05874 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
90 | MV_653_0_line_90 |  | 79 | 80 | 0.003969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_653_0_line_91 |  | 79 | 81 | 0.066488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_653_0_line_92 |  | 81 | 84 | 0.004994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_653_0_line_93 |  | 85 | 87 | 0.004024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_653_0_line_94 |  | 86 | 87 | 0.004286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_653_0_line_95 |  | 86 | 88 | 0.004427 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_653_0_line_96 |  | 88 | 89 | 0.023765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_653_0_line_97 |  | 89 | 90 | 0.019055 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_653_0_line_98 |  | 91 | 92 | 0.004934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_653_0_line_99 |  | 91 | 93 | 0.054788 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_653_0_line_100 |  | 92 | 94 | 0.027761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_653_0_line_101 |  | 93 | 97 | 0.005961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_653_0_line_102 |  | 93 | 95 | 0.045674 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_653_0_line_103 |  | 94 | 98 | 0.010885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_653_0_line_104 |  | 94 | 99 | 0.065965 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_653_0_line_105 |  | 95 | 96 | 0.059166 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
106 | MV_653_0_line_106 |  | 98 | 100 | 0.014831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_653_0_line_107 |  | 100 | 114 | 0.31023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_653_0_line_108 |  | 101 | 102 | 0.012401 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_653_0_line_109 |  | 101 | 103 | 0.034864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_653_0_line_110 |  | 103 | 108 | 0.033639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_653_0_line_111 |  | 103 | 105 | 0.086021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_653_0_line_112 |  | 104 | 105 | 0.020338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_653_0_line_113 |  | 107 | 122 | 0.0098888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_653_0_line_114 |  | 110 | 111 | 0.029744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_653_0_line_115 |  | 111 | 112 | 0.04226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_653_0_line_116 |  | 112 | 160 | 0.060717 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_653_0_line_117 |  | 113 | 114 | 0.012897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_653_0_line_118 |  | 114 | 115 | 0.20832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_653_0_line_119 |  | 115 | 116 | 0.014255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_653_0_line_120 |  | 116 | 117 | 0.012585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_653_0_line_121 |  | 117 | 120 | 0.028112 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_653_0_line_122 |  | 118 | 119 | 0.021296 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_653_0_line_123 |  | 119 | 120 | 0.07393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_653_0_line_124 |  | 120 | 121 | 0.013579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_653_0_line_125 |  | 122 | 123 | 0.003301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_653_0_line_126 |  | 122 | 124 | 0.019162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_653_0_line_127 |  | 122 | 125 | 0.013184 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_653_0_line_128 |  | 124 | 130 | 0.021473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_653_0_line_129 |  | 124 | 126 | 0.015391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_653_0_line_130 |  | 125 | 131 | 0.053381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_653_0_line_131 |  | 125 | 132 | 0.01221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_653_0_line_132 |  | 126 | 127 | 0.015242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_653_0_line_133 |  | 126 | 128 | 0.019128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_653_0_line_134 |  | 127 | 129 | 0.0064366 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_653_0_line_135 |  | 128 | 142 | 0.031888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_653_0_line_136 |  | 130 | 145 | 0.012955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_653_0_line_137 |  | 131 | 152 | 0.014076 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_653_0_line_138 |  | 132 | 148 | 0.009228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_653_0_line_139 |  | 133 | 134 | 0.0057136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_653_0_line_140 |  | 135 | 136 | 0.014757 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_653_0_line_141 |  | 136 | 137 | 0.004378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_653_0_line_142 |  | 137 | 138 | 0.0090084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_653_0_line_143 |  | 137 | 139 | 0.02244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_653_0_line_144 |  | 139 | 140 | 0.024337 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
145 | MV_653_0_line_145 |  | 140 | 141 | 0.012993 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
146 | MV_653_0_line_146 |  | 141 | 154 | 0.0059725 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
147 | MV_653_0_line_147 |  | 142 | 143 | 0.014378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_653_0_line_148 |  | 143 | 144 | 0.018617 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_653_0_line_149 |  | 144 | 146 | 0.028849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_653_0_line_150 |  | 146 | 147 | 0.003717 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_653_0_line_151 |  | 148 | 149 | 0.00601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_653_0_line_152 |  | 149 | 150 | 0.031162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_653_0_line_153 |  | 149 | 151 | 0.02128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_653_0_line_154 |  | 151 | 153 | 0.012875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_653_0_line_155 |  | 154 | 157 | 0.005541 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
156 | MV_653_0_line_156 |  | 154 | 156 | 0.012616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_653_0_line_157 |  | 155 | 156 | 0.018854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_653_0_line_158 |  | 157 | 158 | 0.008542 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
159 | MV_653_0_line_159 |  | 158 | 159 | 0.0044083 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_653_0_trafo_61 | 25 MVA 110/20 kV | 161 | 96 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2499891.226 | 1118184.9166
1 | 2499893.4074 | 1118183.3351
2 | 2499894.9049 | 1118189.8588
3 | 2499801.151 | 1118117.8773
4 | 2499923.8917 | 1118117.2227
5 | 2499902.2179 | 1118199.8329
6 | 2499777.8178 | 1118191.454
7 | 2499773.7998 | 1118186.5509
8 | 2499841.3683 | 1118232.8941
9 | 2499926.0447 | 1118115.3192
10 | 2499863.5044 | 1118215.061
11 | 2499916.6024 | 1118219.4364
12 | 2499620.0685 | 1118203.377
13 | 2499737.6941 | 1118344.1145
14 | 2499553.865 | 1118226.3125
15 | 2499744.2566 | 1118210.1441
16 | 2499871.0478 | 1118278.0978
17 | 2499852.7702 | 1118223.7086
18 | 2499932.4043 | 1118026.6474
19 | 2500004.5659 | 1118117.4348
20 | 2499953.194 | 1118237.1241
21 | 2499955.3832 | 1118213.3988
22 | 2499985.7185 | 1118248.1265
23 | 2499975.9827 | 1118229.3313
24 | 2499732.9871 | 1118347.9282
25 | 2499649.7296 | 1118244.5774
26 | 2499554.8625 | 1118315.1516
27 | 2499742.5353 | 1118378.1778
28 | 2500315.224 | 1118235.8468
29 | 2500335.5383 | 1118218.8682
30 | 2500321.5202 | 1118149.0889
31 | 2500005.6735 | 1118505.3464
32 | 2500333.3891 | 1118139.7169
33 | 2499959.7977 | 1118519.5693
34 | 2499987.9078 | 1118483.2582
35 | 2500362.9498 | 1118116.3749
36 | 2499740.4145 | 1118382.9492
37 | 2499748.2895 | 1118515.246
38 | 2499811.3445 | 1118616.8649
39 | 2499744.3311 | 1118511.5982
40 | 2499790.3133 | 1118619.6196
41 | 2499961.8957 | 1118520.0712
42 | 2499978.0514 | 1118471.0038
43 | 2500267.4112 | 1118262.0404
44 | 2500233.2765 | 1118221.1775
45 | 2500196.5002 | 1118172.3647
46 | 2500206.3746 | 1118179.484
47 | 2500189.4349 | 1118185.3116
48 | 2500178.6438 | 1118195.6072
49 | 2500168.651 | 1118161.4975
50 | 2500217.9462 | 1118168.4265
51 | 2500183.9711 | 1118211.5737
52 | 2500162.4888 | 1118137.7043
53 | 2500134.4447 | 1118134.7014
54 | 2500102.7813 | 1118282.3515
55 | 2500110.3587 | 1118291.6944
56 | 2500081.4362 | 1118287.5028
57 | 2500113.5331 | 1118343.1964
58 | 2500097.5094 | 1118250.7476
59 | 2500057.6122 | 1118307.15
60 | 2500106.8557 | 1118348.6349
61 | 2500090.2462 | 1118240.4945
62 | 2500082.8735 | 1118230.1543
63 | 2500134.0827 | 1118243.6406
64 | 2500099.321 | 1118354.7716
65 | 2500181.7307 | 1118225.0191
66 | 2500144.3444 | 1118241.6465
67 | 2500194.8381 | 1118248.8955
68 | 2500231.4032 | 1118291.0187
69 | 2500166.489 | 1118272.291
70 | 2500202.0038 | 1118314.5303
71 | 2500011.0825 | 1118286.8314
72 | 2500007.3052 | 1118266.5923
73 | 2499986.8149 | 1118276.137
74 | 2500020.1826 | 1118389.9455
75 | 2499987.9655 | 1118282.3819
76 | 2499998.8424 | 1118245.7432
77 | 2500033.4317 | 1118379.3911
78 | 2499983.4084 | 1118220.8868
79 | 2499606.1385 | 1118444.7927
80 | 2499603.8919 | 1118441.5168
81 | 2499636.0637 | 1118473.6031
82 | 2499649.7809 | 1118234.1811
83 | 2499511.7436 | 1118301.0838
84 | 2499639.1242 | 1118477.5548
85 | 2499768.5842 | 1118622.4657
86 | 2499760.6045 | 1118624.8661
87 | 2499764.7211 | 1118623.6304
88 | 2499756.4871 | 1118626.5242
89 | 2499734.4759 | 1118635.4835
90 | 2499725.2313 | 1118618.8209
91 | 2500102.316 | 1118090.8461
92 | 2500105.8641 | 1118087.4076
93 | 2500059.4836 | 1118125.0082
94 | 2500108.1466 | 1118074.1838
95 | 2500029.355 | 1118142.2279
96 | 2500022.3248 | 1118176.888
97 | 2500063.4097 | 1118129.5017
98 | 2500115.3172 | 1118065.9945
99 | 2500054.0366 | 1118036.454
100 | 2500125.0871 | 1118054.8365
101 | 2500000.5032 | 1117986.9521
102 | 2500009.6207 | 1117995.1225
103 | 2500008.5581 | 1117967.1066
104 | 2499945.2237 | 1118016.4801
105 | 2499960.6413 | 1118003.3214
106 | 2499988.4602 | 1118225.3291
107 | 2500225.9805 | 1118160.7489
108 | 2500039.6748 | 1117979.8878
109 | 2499867.2749 | 1118267.4758
110 | 2499860.9766 | 1118293.1294
111 | 2499879.5069 | 1118316.3957
112 | 2499906.422 | 1118348.8566
113 | 2500230.8144 | 1117834.5075
114 | 2500218.3096 | 1117837.6625
115 | 2500368.2097 | 1117817.2459
116 | 2500363.5129 | 1117803.7875
117 | 2500359.4238 | 1117791.8859
118 | 2500459.3924 | 1117787.5169
119 | 2500439.0682 | 1117793.8759
120 | 2500386.0668 | 1117782.6858
121 | 2500390.9035 | 1117795.3741
122 | 2500232.951 | 1118153.7407
123 | 2500235.2743 | 1118151.3898
124 | 2500228.4122 | 1118144.3875
125 | 2500242.4977 | 1118158.7753
126 | 2500218.1809 | 1118132.9491
127 | 2500218.2934 | 1118145.8442
128 | 2500231.5922 | 1118119.311
129 | 2500213.7673 | 1118141.2678
130 | 2500243.571 | 1118129.179
131 | 2500282.3658 | 1118123.1513
132 | 2500251.0401 | 1118167.5001
133 | 2500377.9524 | 1118122.941
134 | 2500374.4008 | 1118118.4654
135 | 2500023.8932 | 1118342.8141
136 | 2500032.8274 | 1118354.5589
137 | 2500036.2636 | 1118351.8337
138 | 2500043.3195 | 1118346.2332
139 | 2500050.5057 | 1118369.1648
140 | 2500066.4341 | 1118381.576
141 | 2500076.5043 | 1118373.3663
142 | 2500254.0003 | 1118096.6246
143 | 2500243.7675 | 1118086.4981
144 | 2500226.335 | 1118082.9237
145 | 2500252.7163 | 1118120.0037
146 | 2500199.3627 | 1118072.6885
147 | 2500195.8015 | 1118071.591
148 | 2500258.0781 | 1118173.0162
149 | 2500263.1018 | 1118170.1204
150 | 2500287.4741 | 1118150.702
151 | 2500276.1616 | 1118186.9156
152 | 2500293.0569 | 1118113.9951
153 | 2500284.1943 | 1118196.9778
154 | 2500081.1333 | 1118369.5924
155 | 2500100.8285 | 1118394.1374
156 | 2500089.0288 | 1118379.4321
157 | 2500085.4365 | 1118366.0858
158 | 2500092.0577 | 1118360.6889
159 | 2500095.4747 | 1118357.9038
160 | 2499860.1512 | 1118388.1612
161 | 2500022.3248 | 1118176.888

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9994 | -0.016318 | 0.3964 | 0.19199
1 | 0.9994 | -0.016253 | 0 | 0
2 | 0.99937 | -0.01606 | 0 | 0
3 | 0.99937 | -0.016512 | 0.1421 | 0.06882
4 | 0.99953 | -0.015767 | 0 | 0
5 | 0.99931 | -0.015541 | 0 | 0
6 | 0.99854 | -0.015048 | 0 | 0
7 | 0.99852 | -0.014842 | 0.32094 | 0.15544
8 | 0.99896 | -0.012335 | 0 | 0
9 | 0.99953 | -0.015751 | 0.37973 | 0.18391
10 | 0.99908 | -0.013488 | 0 | 0
11 | 0.99931 | -0.015513 | 0.096791 | 0.046878
12 | 0.99727 | -0.013616 | 0 | 0
13 | 0.99739 | -0.012878 | 0.25401 | 0.12302
14 | 0.99724 | -0.013352 | 0.31869 | 0.15435
15 | 0.9984 | -0.013756 | 0 | 0
16 | 0.99889 | -0.011685 | 0 | 0
17 | 0.99902 | -0.012923 | 0.072204 | 0.03497
18 | 0.99945 | -0.016302 | 0 | 0
19 | 0.9998 | -0.00077848 | 0.40971 | 0.19843
20 | 0.99956 | -0.018508 | 0 | 0
21 | 0.99955 | -0.018471 | 0.11729 | 0.056808
22 | 0.99946 | -0.018912 | 0 | 0
23 | 0.99965 | -0.018114 | 0 | 0
24 | 0.99739 | -0.012919 | 0 | 0
25 | 0.99792 | -0.0094026 | 0 | 0
26 | 0.99736 | -0.013123 | 0 | 0
27 | 0.9972 | -0.011212 | 0 | 0
28 | 0.99804 | -0.016592 | 0.23337 | 0.11303
29 | 0.99805 | -0.016517 | 0 | 0
30 | 0.99803 | -0.016326 | 0 | 0
31 | 0.99844 | -0.019474 | 0 | 0
32 | 0.99803 | -0.0163 | 0.077305 | 0.03744
33 | 0.99843 | -0.019363 | 0 | 0
34 | 0.99846 | -0.019594 | 0.29817 | 0.14441
35 | 0.99802 | -0.016268 | 0 | 0
36 | 0.99719 | -0.011126 | 0.21796 | 0.10556
37 | 0.99661 | -0.013547 | 0 | 0
38 | 0.99652 | -0.012723 | 0 | 0
39 | 0.99662 | -0.013575 | 0.2154 | 0.10432
40 | 0.99651 | -0.012607 | 0.11461 | 0.055508
41 | 0.99843 | -0.019359 | 0.10553 | 0.051112
42 | 0.99847 | -0.019717 | 0 | 0
43 | 0.9979 | -0.023892 | 0.25963 | 0.12575
44 | 0.99792 | -0.024057 | 0 | 0
45 | 0.99795 | -0.024306 | 0 | 0
46 | 0.99789 | -0.023805 | 0 | 0
47 | 0.99802 | -0.02494 | 0 | 0
48 | 0.99805 | -0.024583 | 0.072581 | 0.035153
49 | 0.99799 | -0.024706 | 0.17099 | 0.082815
50 | 0.99783 | -0.023174 | 0.3411 | 0.1652
51 | 0.99807 | -0.024494 | 0.2494 | 0.12079
52 | 0.99798 | -0.024807 | 0.33558 | 0.16253
53 | 0.99799 | -0.02465 | 0.10554 | 0.051114
54 | 0.99837 | -0.023074 | 0.24302 | 0.1177
55 | 0.99837 | -0.023109 | 0 | 0
56 | 0.99839 | -0.023289 | 0 | 0
57 | 0.99852 | -0.022795 | 0 | 0
58 | 0.99827 | -0.02374 | 0 | 0
59 | 0.99839 | -0.023263 | 0.0705 | 0.034145
60 | 0.99853 | -0.022734 | 0.086148 | 0.041723
61 | 0.99825 | -0.023537 | 0 | 0
62 | 0.99825 | -0.023498 | 0.2558 | 0.12389
63 | 0.99821 | -0.023972 | 0.068208 | 0.033035
64 | 0.99855 | -0.022664 | 0 | 0
65 | 0.99809 | -0.024419 | 0 | 0
66 | 0.9982 | -0.024036 | 0 | 0
67 | 0.99808 | -0.024289 | 0 | 0
68 | 0.99807 | -0.024231 | 0 | 0
69 | 0.99807 | -0.024154 | 0.30623 | 0.14831
70 | 0.99807 | -0.024191 | 0.091779 | 0.04445
71 | 0.99936 | -0.019061 | 0.31462 | 0.15238
72 | 0.99937 | -0.019138 | 0 | 0
73 | 0.99938 | -0.019241 | 0 | 0
74 | 0.99876 | -0.021862 | 0 | 0
75 | 0.99938 | -0.019234 | 0.095322 | 0.046167
76 | 0.99946 | -0.018889 | 0.1419 | 0.068723
77 | 0.99872 | -0.021998 | 0.10182 | 0.049312
78 | 0.99968 | -0.017995 | 0.31918 | 0.15458
79 | 0.99685 | -0.013397 | 0 | 0
80 | 0.99685 | -0.013386 | 0.24393 | 0.11814
81 | 0.99677 | -0.012657 | 0 | 0
82 | 0.99792 | -0.0094544 | 0.4108 | 0.19896
83 | 0.99736 | -0.013079 | 0.084473 | 0.040912
84 | 0.99676 | -0.012601 | 0.28267 | 0.1369
85 | 0.9965 | -0.012517 | 0 | 0
86 | 0.99649 | -0.012483 | 0.27093 | 0.13122
87 | 0.9965 | -0.0125 | 0 | 0
88 | 0.99649 | -0.012479 | 0 | 0
89 | 0.99649 | -0.012457 | 0 | 0
90 | 0.99649 | -0.012439 | 0.078825 | 0.038177
91 | 0.99964 | -0.00069584 | 0.40327 | 0.19531
92 | 0.99963 | -0.000648 | 0 | 0
93 | 0.99977 | 0.00025577 | 0 | 0
94 | 0.9996 | -0.00037817 | 0 | 0
95 | 0.99986 | -0.00053567 | 0 | 0
96 | 1 | 0 | -15.1242 | -7.1568
97 | 0.99977 | 0.00027279 | 0.23884 | 0.11568
98 | 0.99959 | -0.00032505 | 0.07194 | 0.034842
99 | 0.99955 | -0.00070319 | 0.40713 | 0.19718
100 | 0.99958 | -0.00026516 | 0 | 0
101 | 0.99938 | -0.01563 | 0 | 0
102 | 0.99937 | -0.015591 | 0.26043 | 0.12613
103 | 0.99939 | -0.015737 | 0 | 0
104 | 0.99944 | -0.016213 | 0.086893 | 0.042084
105 | 0.99943 | -0.016123 | 0 | 0
106 | 0.99968 | -0.017989 | 0.071811 | 0.03478
107 | 0.99778 | -0.022782 | 0 | 0
108 | 0.99938 | -0.015686 | 0.13019 | 0.063053
109 | 0.99888 | -0.011649 | 0.2679 | 0.12975
110 | 0.99887 | -0.011561 | 0 | 0
111 | 0.99886 | -0.011424 | 0.088942 | 0.043077
112 | 0.99884 | -0.011273 | 0 | 0
113 | 0.99942 | 0.0010807 | 0.10531 | 0.051006
114 | 0.99942 | 0.0010645 | 0 | 0
115 | 0.99933 | 0.0017811 | 0 | 0
116 | 0.99933 | 0.0018326 | 0.087295 | 0.042279
117 | 0.99932 | 0.0018651 | 0 | 0
118 | 0.99929 | 0.0021198 | 0.16484 | 0.079835
119 | 0.9993 | 0.0020781 | 0 | 0
120 | 0.99931 | 0.0019386 | 0 | 0
121 | 0.99931 | 0.0019497 | 0.06907 | 0.033452
122 | 0.99775 | -0.022432 | 0 | 0
123 | 0.99775 | -0.022429 | 0.092532 | 0.044815
124 | 0.99771 | -0.022083 | 0 | 0
125 | 0.99772 | -0.022221 | 0 | 0
126 | 0.99768 | -0.021833 | 0 | 0
127 | 0.99768 | -0.021813 | 0 | 0
128 | 0.99765 | -0.021548 | 0.82524 | 0.39968
129 | 0.99768 | -0.021804 | 0.11404 | 0.055231
130 | 0.9977 | -0.02204 | 0.084339 | 0.040847
131 | 0.99767 | -0.021701 | 0.73889 | 0.35786
132 | 0.99771 | -0.022143 | 0.11147 | 0.053986
133 | 0.99802 | -0.016249 | 0.075055 | 0.036351
134 | 0.99802 | -0.016254 | 0 | 0
135 | 0.99867 | -0.022098 | 0.093509 | 0.045288
136 | 0.99867 | -0.022114 | 0 | 0
137 | 0.99867 | -0.022119 | 0 | 0
138 | 0.99867 | -0.022112 | 0.069579 | 0.033699
139 | 0.99868 | -0.022162 | 0 | 0
140 | 0.99863 | -0.022348 | 0 | 0
141 | 0.99861 | -0.022448 | 0.095003 | 0.046012
142 | 0.99763 | -0.021386 | 0 | 0
143 | 0.99763 | -0.021313 | 0 | 0
144 | 0.99762 | -0.021217 | 0.069393 | 0.033608
145 | 0.9977 | -0.022027 | 0.085244 | 0.041285
146 | 0.9976 | -0.021093 | 0 | 0
147 | 0.9976 | -0.021077 | 0.36204 | 0.17535
148 | 0.99771 | -0.022096 | 0 | 0
149 | 0.99771 | -0.022066 | 0 | 0
150 | 0.9977 | -0.021965 | 0.27092 | 0.13121
151 | 0.9977 | -0.022026 | 0 | 0
152 | 0.99767 | -0.021689 | 0.075875 | 0.036748
153 | 0.9977 | -0.022002 | 0.15913 | 0.07707
154 | 0.99859 | -0.022493 | 0 | 0
155 | 0.99859 | -0.022455 | 0.074936 | 0.036293
156 | 0.99859 | -0.022471 | 0.069381 | 0.033603
157 | 0.99858 | -0.022533 | 0 | 0
158 | 0.99857 | -0.022596 | 0.086807 | 0.042042
159 | 0.99856 | -0.022628 | 0 | 0
160 | 0.99882 | -0.011051 | 0.30874 | 0.14953
161 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -4.1929 | -2.0022 | 4.1929 | 2.0022 | 2.3395e-05 | -7.5138e-05 | 0.13421 | 0.13421 | 0.13421 | 0.9994 | -0.016318 | 0.9994 | -0.016253 | 37.0752
1 | 3.6544 | 1.7416 | -3.6543 | -1.7417 | 0.00011237 | -0.00011347 | 0.11693 | 0.11693 | 0.11693 | 0.9994 | -0.016318 | 0.99937 | -0.01606 | 53.1514
2 | 0.1421 | 0.068689 | -0.1421 | -0.06882 | 4.1595e-06 | -0.00013127 | 0.0045589 | 0.0045606 | 0.0045606 | 0.9994 | -0.016318 | 0.99937 | -0.016512 | 2.1717
3 | -4.1929 | -2.0022 | 4.1934 | 1.9967 | 0.00050692 | -0.0054339 | 0.13421 | 0.13414 | 0.13421 | 0.9994 | -0.016253 | 0.99953 | -0.015767 | 21.0362
4 | 3.6543 | 1.7417 | -3.6541 | -1.7419 | 0.00022577 | -0.00022794 | 0.11693 | 0.11694 | 0.11694 | 0.99937 | -0.01606 | 0.99931 | -0.015541 | 53.153
5 | -4.1934 | -1.9967 | 4.1935 | 1.9965 | 1.5951e-05 | -0.00017111 | 0.13414 | 0.13414 | 0.13414 | 0.99953 | -0.015767 | 0.99953 | -0.015751 | 21.0251
6 | 3.5573 | 1.6956 | -3.5564 | -1.6965 | 0.00086792 | -0.0009383 | 0.11384 | 0.11385 | 0.11385 | 0.99931 | -0.015541 | 0.99908 | -0.013488 | 51.751
7 | 0.096791 | 0.046298 | -0.096791 | -0.046878 | 3.1256e-07 | -0.00057965 | 0.0030994 | 0.0031067 | 0.0031067 | 0.99931 | -0.015541 | 0.99931 | -0.015513 | 1.4121
8 | 2.817 | 1.3452 | -2.8169 | -1.3454 | 6.8859e-05 | -0.00013034 | 0.090247 | 0.090249 | 0.090249 | 0.99854 | -0.015048 | 0.99852 | -0.014842 | 41.022
9 | -2.817 | -1.3452 | 2.8181 | 1.3458 | 0.0011009 | 0.00059923 | 0.090247 | 0.090246 | 0.090247 | 0.99854 | -0.015048 | 0.99896 | -0.012335 | 42.9746
10 | 2.496 | 1.1899 | -2.4956 | -1.1907 | 0.00032202 | -0.00080284 | 0.079939 | 0.079951 | 0.079951 | 0.99852 | -0.014842 | 0.9984 | -0.013756 | 36.3412
11 | 0.66566 | 0.31628 | -0.66561 | -0.31828 | 5.1472e-05 | -0.0020076 | 0.021297 | 0.021322 | 0.021322 | 0.99896 | -0.012335 | 0.99889 | -0.011685 | 9.6918
12 | -3.4837 | -1.6621 | 3.484 | 1.6618 | 0.00024318 | -0.00027674 | 0.11154 | 0.11154 | 0.11154 | 0.99896 | -0.012335 | 0.99902 | -0.012923 | 50.7011
13 | 0.47758 | 0.22634 | -0.47755 | -0.22642 | 3.6906e-05 | -8.2904e-05 | 0.015264 | 0.015265 | 0.015265 | 0.99953 | -0.015751 | 0.99945 | -0.016302 | 7.2691
14 | -5.0508 | -2.4068 | 5.0515 | 2.4087 | 0.00073218 | 0.0018604 | 0.16159 | 0.16159 | 0.16159 | 0.99953 | -0.015751 | 0.9998 | -0.00077848 | 25.0522
15 | 3.5564 | 1.6965 | -3.5562 | -1.6968 | 0.00023854 | -0.00025773 | 0.11385 | 0.11386 | 0.11386 | 0.99908 | -0.013488 | 0.99902 | -0.012923 | 51.7528
16 | -0.3187 | -0.15269 | 0.31874 | 0.1525 | 3.4188e-05 | -0.00019639 | 0.01023 | 0.010227 | 0.01023 | 0.99727 | -0.013616 | 0.99739 | -0.012878 | 4.8712
17 | 0.3187 | 0.15269 | -0.31869 | -0.15435 | 9.7819e-06 | -0.0016564 | 0.01023 | 0.01025 | 0.01025 | 0.99727 | -0.013616 | 0.99724 | -0.013352 | 4.6593
18 | -0.57275 | -0.27552 | 0.57275 | 0.27538 | 2.7319e-06 | -0.00014284 | 0.018396 | 0.018394 | 0.018396 | 0.99739 | -0.012878 | 0.99739 | -0.012919 | 8.3616
19 | 2.4956 | 1.1907 | -2.4944 | -1.1939 | 0.0012846 | -0.0031981 | 0.079951 | 0.079995 | 0.079995 | 0.9984 | -0.013756 | 0.99792 | -0.0094026 | 36.3615
20 | 0.2679 | 0.12948 | -0.2679 | -0.12975 | 1.1131e-06 | -0.00026818 | 0.0085991 | 0.0086024 | 0.0086024 | 0.99889 | -0.011685 | 0.99888 | -0.011649 | 3.9102
21 | 0.39771 | 0.1888 | -0.39771 | -0.18945 | 5.9073e-06 | -0.00064903 | 0.012723 | 0.012731 | 0.012731 | 0.99889 | -0.011685 | 0.99887 | -0.011561 | 5.7869
22 | 0.47755 | 0.22642 | -0.47754 | -0.22681 | 5.0915e-06 | -0.00038871 | 0.015265 | 0.01527 | 0.01527 | 0.99945 | -0.016302 | 0.99944 | -0.016213 | 6.9409
23 | -5.4612 | -2.6071 | 5.4615 | 2.6051 | 0.0003307 | -0.0020159 | 0.17473 | 0.1747 | 0.17473 | 0.9998 | -0.00077848 | 0.99986 | -0.00053567 | 27.387
24 | 0.11729 | 0.05617 | -0.11729 | -0.056808 | 5.0414e-07 | -0.0006371 | 0.0037559 | 0.0037639 | 0.0037639 | 0.99956 | -0.018508 | 0.99955 | -0.018471 | 1.7108
25 | 7.589 | 3.5675 | -7.5883 | -3.5695 | 0.00070329 | -0.0020395 | 0.24218 | 0.24221 | 0.24221 | 0.99956 | -0.018508 | 0.99946 | -0.018912 | 37.9641
26 | -7.7063 | -3.6236 | 7.707 | 3.6217 | 0.00069577 | -0.0019457 | 0.24594 | 0.24591 | 0.24594 | 0.99956 | -0.018508 | 0.99965 | -0.018114 | 38.5481
27 | 0.1419 | 0.068405 | -0.1419 | -0.068723 | 3.6894e-07 | -0.00031802 | 0.0045498 | 0.0045538 | 0.0045538 | 0.99946 | -0.018912 | 0.99946 | -0.018889 | 2.0699
28 | 7.4464 | 3.5011 | -7.4458 | -3.5028 | 0.00056261 | -0.001706 | 0.23766 | 0.23769 | 0.23769 | 0.99946 | -0.018912 | 0.99938 | -0.019241 | 37.2549
29 | -7.707 | -3.6217 | 7.7072 | 3.6211 | 0.00021011 | -0.00058775 | 0.24591 | 0.2459 | 0.24591 | 0.99965 | -0.018114 | 0.99968 | -0.017995 | 38.5436
30 | -2.0825 | -0.99447 | 2.0836 | 0.99497 | 0.0010549 | 0.00050306 | 0.066794 | 0.066792 | 0.066794 | 0.99739 | -0.012919 | 0.99792 | -0.0094026 | 31.8065
31 | 0.084476 | 0.039622 | -0.084474 | -0.039835 | 2.3557e-06 | -0.00021361 | 0.0027006 | 0.0027032 | 0.0027032 | 0.99739 | -0.012919 | 0.99736 | -0.013123 | 1.2872
32 | 1.4253 | 0.67947 | -1.425 | -0.68183 | 0.00028811 | -0.0023668 | 0.045699 | 0.04573 | 0.04573 | 0.99739 | -0.012919 | 0.9972 | -0.011212 | 20.7864
33 | 0.4108 | 0.19895 | -0.4108 | -0.19896 | 3.2294e-06 | -1.0337e-05 | 0.013204 | 0.013204 | 0.013204 | 0.99792 | -0.0094026 | 0.99792 | -0.0094544 | 6.2876
34 | 0.084474 | 0.039835 | -0.084473 | -0.040912 | 4.4466e-07 | -0.0010771 | 0.0027032 | 0.0027167 | 0.0027167 | 0.99736 | -0.013123 | 0.99736 | -0.013079 | 1.2348
35 | 1.425 | 0.68183 | -1.425 | -0.68195 | 1.4574e-05 | -0.00011961 | 0.04573 | 0.045732 | 0.045732 | 0.9972 | -0.011212 | 0.99719 | -0.011126 | 20.7871
36 | -0.23337 | -0.11303 | 0.23337 | 0.113 | 2.6533e-06 | -2.9821e-05 | 0.0075001 | 0.0074997 | 0.0075001 | 0.99804 | -0.016592 | 0.99805 | -0.016517 | 3.5715
37 | 0.15236 | 0.069225 | -0.15236 | -0.072011 | 3.6906e-06 | -0.0027856 | 0.0048405 | 0.0048744 | 0.0048744 | 0.99805 | -0.016517 | 0.99803 | -0.016326 | 2.2156
38 | -0.38574 | -0.18222 | 0.3859 | 0.16343 | 0.00015802 | -0.018796 | 0.012339 | 0.012117 | 0.012339 | 0.99805 | -0.016517 | 0.99844 | -0.019474 | 5.6088
39 | 0.15236 | 0.072011 | -0.15236 | -0.07237 | 4.8013e-07 | -0.00035951 | 0.0048744 | 0.0048788 | 0.0048788 | 0.99803 | -0.016326 | 0.99803 | -0.0163 | 2.2177
40 | 0.10554 | 0.048815 | -0.10553 | -0.051039 | 1.4217e-06 | -0.0022242 | 0.0033619 | 0.0033894 | 0.0033894 | 0.99844 | -0.019474 | 0.99843 | -0.019363 | 1.5406
41 | -0.49143 | -0.21224 | 0.49144 | 0.21157 | 9.0602e-06 | -0.00067201 | 0.015477 | 0.015469 | 0.015477 | 0.99844 | -0.019474 | 0.99846 | -0.019594 | 7.035
42 | 0.075055 | 0.03493 | -0.075055 | -0.035825 | 2.8963e-07 | -0.00089567 | 0.0023945 | 0.0024056 | 0.0024056 | 0.99803 | -0.0163 | 0.99802 | -0.016268 | 1.0934
43 | 0.10553 | 0.051039 | -0.10553 | -0.051112 | 4.7431e-08 | -7.3554e-05 | 0.0033894 | 0.0033903 | 0.0033903 | 0.99843 | -0.019363 | 0.99843 | -0.019359 | 1.5411
44 | -0.78961 | -0.35598 | 0.78963 | 0.35561 | 1.3164e-05 | -0.00037043 | 0.025042 | 0.025038 | 0.025042 | 0.99846 | -0.019594 | 0.99847 | -0.019717 | 11.3828
45 | 0.075055 | 0.035825 | -0.075055 | -0.036215 | 1.2677e-07 | -0.00038944 | 0.0024056 | 0.0024104 | 0.0024104 | 0.99802 | -0.016268 | 0.99802 | -0.016254 | 1.0957
46 | 1.207 | 0.57639 | -1.2066 | -0.57632 | 0.00039494 | 7.1941e-05 | 0.038721 | 0.038723 | 0.038723 | 0.99719 | -0.011126 | 0.99685 | -0.013397 | 18.4397
47 | 0.46442 | 0.21891 | -0.46438 | -0.22257 | 4.5801e-05 | -0.0036534 | 0.014872 | 0.014917 | 0.014917 | 0.99661 | -0.013547 | 0.99652 | -0.012723 | 6.7807
48 | -0.46442 | -0.21891 | 0.46442 | 0.21879 | 1.5869e-06 | -0.000127 | 0.014872 | 0.01487 | 0.014872 | 0.99661 | -0.013547 | 0.99662 | -0.013575 | 6.7599
49 | 0.46438 | 0.22257 | -0.46437 | -0.22307 | 6.304e-06 | -0.00050104 | 0.014917 | 0.014924 | 0.014924 | 0.99652 | -0.012723 | 0.99651 | -0.012607 | 6.7835
50 | -0.67983 | -0.32311 | 0.67992 | 0.32304 | 9.3645e-05 | -7.2479e-05 | 0.021803 | 0.021801 | 0.021803 | 0.99662 | -0.013575 | 0.99676 | -0.012601 | 10.3822
51 | 0.34976 | 0.16756 | -0.34976 | -0.16808 | 3.6949e-06 | -0.00051849 | 0.011235 | 0.011241 | 0.011241 | 0.99651 | -0.012607 | 0.9965 | -0.012517 | 5.1097
52 | -0.78963 | -0.35561 | 0.78986 | 0.34891 | 0.0002373 | -0.0067026 | 0.025038 | 0.024958 | 0.025038 | 0.99847 | -0.019717 | 0.99876 | -0.021862 | 11.3808
53 | -0.25963 | -0.12575 | 0.25964 | 0.12447 | 4.9667e-06 | -0.0012711 | 0.0083452 | 0.0083293 | 0.0083452 | 0.9979 | -0.023892 | 0.99792 | -0.024057 | 3.7933
54 | -0.25964 | -0.12447 | 0.25965 | 0.12248 | 7.7544e-06 | -0.0019944 | 0.0083293 | 0.0083044 | 0.0083293 | 0.99792 | -0.024057 | 0.99795 | -0.024306 | 3.786
55 | 3.3312 | 1.6029 | -3.331 | -1.6031 | 0.00019464 | -0.0002454 | 0.10694 | 0.10694 | 0.10694 | 0.99795 | -0.024306 | 0.99789 | -0.023805 | 48.6087
56 | -3.5908 | -1.7254 | 3.5911 | 1.7251 | 0.00026594 | -0.00027784 | 0.11524 | 0.11524 | 0.11524 | 0.99795 | -0.024306 | 0.99802 | -0.02494 | 52.3816
57 | 3.331 | 1.6031 | -3.3307 | -1.6034 | 0.00024437 | -0.00030803 | 0.10694 | 0.10694 | 0.10694 | 0.99789 | -0.023805 | 0.99783 | -0.023174 | 48.6108
58 | -4.2032 | -2.0197 | 4.2033 | 2.0192 | 0.00013107 | -0.00041444 | 0.13488 | 0.13488 | 0.13488 | 0.99802 | -0.02494 | 0.99805 | -0.024583 | 37.2609
59 | 0.61213 | 0.29459 | -0.61211 | -0.29535 | 1.6599e-05 | -0.00076053 | 0.019649 | 0.019659 | 0.019659 | 0.99802 | -0.02494 | 0.99799 | -0.024706 | 8.9359
60 | -4.2759 | -2.0544 | 4.276 | 2.0534 | 9.7984e-05 | -0.00099911 | 0.13721 | 0.1372 | 0.13721 | 0.99805 | -0.024583 | 0.99807 | -0.024494 | 21.5064
61 | 0.33558 | 0.1625 | -0.33558 | -0.16253 | 5.094e-06 | -2.6033e-05 | 0.010785 | 0.010786 | 0.010786 | 0.99799 | -0.024706 | 0.99798 | -0.024807 | 5.136
62 | 0.10554 | 0.050032 | -0.10554 | -0.051114 | 6.9659e-07 | -0.0010826 | 0.0033784 | 0.003392 | 0.003392 | 0.99799 | -0.024706 | 0.99799 | -0.02465 | 1.5418
63 | 2.9896 | 1.4382 | -2.9895 | -1.4384 | 0.00013667 | -0.00022363 | 0.095979 | 0.095982 | 0.095982 | 0.99783 | -0.023174 | 0.99778 | -0.022782 | 43.6284
64 | -4.5254 | -2.1742 | 4.5255 | 2.1734 | 8.8823e-05 | -0.00080329 | 0.14521 | 0.1452 | 0.14521 | 0.99807 | -0.024494 | 0.99809 | -0.024419 | 22.7605
65 | -0.24302 | -0.1177 | 0.24302 | 0.11741 | 9.7849e-07 | -0.00028599 | 0.0078075 | 0.0078039 | 0.0078075 | 0.99837 | -0.023074 | 0.99837 | -0.023109 | 3.5489
66 | -0.24302 | -0.11741 | 0.24302 | 0.11591 | 5.1122e-06 | -0.0014985 | 0.0078039 | 0.0077852 | 0.0078039 | 0.99837 | -0.023109 | 0.99839 | -0.023289 | 3.5472
67 | -5.5625 | -2.6563 | 5.5632 | 2.6523 | 0.00068424 | -0.0039823 | 0.17823 | 0.17818 | 0.17823 | 0.99839 | -0.023289 | 0.99852 | -0.022795 | 27.9362
68 | 5.249 | 2.507 | -5.2484 | -2.5109 | 0.00059699 | -0.0039394 | 0.16819 | 0.16825 | 0.16825 | 0.99839 | -0.023289 | 0.99827 | -0.02374 | 26.3707
69 | 0.070501 | 0.03341 | -0.0705 | -0.034145 | 2.1063e-07 | -0.00073487 | 0.0022558 | 0.002265 | 0.002265 | 0.99839 | -0.023289 | 0.99839 | -0.023263 | 1.0295
70 | -5.5632 | -2.6523 | 5.5633 | 2.6518 | 8.4479e-05 | -0.00049194 | 0.17818 | 0.17817 | 0.17818 | 0.99852 | -0.022795 | 0.99853 | -0.022734 | 27.9276
71 | 4.9926 | 2.389 | -4.9923 | -2.3911 | 0.00029496 | -0.0021666 | 0.16005 | 0.16008 | 0.16008 | 0.99827 | -0.02374 | 0.99821 | -0.023972 | 25.0908
72 | 0.25581 | 0.12198 | -0.2558 | -0.12359 | 6.08e-06 | -0.0016077 | 0.0081952 | 0.0082154 | 0.0082154 | 0.99827 | -0.02374 | 0.99825 | -0.023537 | 3.7343
73 | -5.6494 | -2.6936 | 5.6495 | 2.693 | 9.8302e-05 | -0.00055344 | 0.18094 | 0.18093 | 0.18094 | 0.99853 | -0.022734 | 0.99855 | -0.022664 | 28.3603
74 | 0.2558 | 0.12359 | -0.2558 | -0.12389 | 1.1439e-06 | -0.00030159 | 0.0082154 | 0.0082192 | 0.0082192 | 0.99825 | -0.023537 | 0.99825 | -0.023498 | 3.736
75 | 4.9241 | 2.3581 | -4.924 | -2.3587 | 8.0527e-05 | -0.00060912 | 0.15789 | 0.1579 | 0.1579 | 0.99821 | -0.023972 | 0.9982 | -0.024036 | 24.7485
76 | -5.6495 | -2.693 | 5.6496 | 2.6927 | 5.0091e-05 | -0.00028204 | 0.18093 | 0.18093 | 0.18093 | 0.99855 | -0.022664 | 0.99856 | -0.022628 | 28.3591
77 | -4.9235 | -2.3623 | 4.924 | 2.3587 | 0.00048272 | -0.0036494 | 0.15794 | 0.1579 | 0.15794 | 0.99809 | -0.024419 | 0.9982 | -0.024036 | 24.7562
78 | 0.39802 | 0.18895 | -0.39801 | -0.18963 | 6.186e-06 | -0.00067642 | 0.012743 | 0.012752 | 0.012752 | 0.99809 | -0.024419 | 0.99808 | -0.024289 | 5.7961
79 | 0.09178 | 0.042193 | -0.091779 | -0.043555 | 6.5646e-07 | -0.0013622 | 0.0029216 | 0.0029383 | 0.0029383 | 0.99808 | -0.024289 | 0.99807 | -0.024231 | 1.3356
80 | 0.30623 | 0.14744 | -0.30623 | -0.14831 | 4.7575e-06 | -0.00087473 | 0.0098303 | 0.0098413 | 0.0098413 | 0.99808 | -0.024289 | 0.99807 | -0.024154 | 4.4733
81 | 0.091779 | 0.043555 | -0.091779 | -0.04445 | 4.3554e-07 | -0.00089522 | 0.0029383 | 0.0029495 | 0.0029495 | 0.99807 | -0.024231 | 0.99807 | -0.024191 | 1.3407
82 | -0.31462 | -0.15238 | 0.31462 | 0.15189 | 2.8013e-06 | -0.0004902 | 0.010098 | 0.010092 | 0.010098 | 0.99936 | -0.019061 | 0.99937 | -0.019138 | 4.5899
83 | -0.31462 | -0.15189 | 0.31462 | 0.15123 | 3.7623e-06 | -0.00065932 | 0.010092 | 0.010083 | 0.010092 | 0.99937 | -0.019138 | 0.99938 | -0.019241 | 4.5871
84 | 7.0359 | 3.3056 | -7.0316 | -3.3203 | 0.0042691 | -0.014764 | 0.22455 | 0.22476 | 0.22476 | 0.99938 | -0.019241 | 0.99876 | -0.021862 | 35.2285
85 | 0.095322 | 0.046015 | -0.095322 | -0.046167 | 7.9295e-08 | -0.0001514 | 0.0030575 | 0.0030594 | 0.0030594 | 0.99938 | -0.019241 | 0.99938 | -0.019234 | 1.3906
86 | 6.2418 | 2.9714 | -6.2415 | -2.9724 | 0.00020899 | -0.00094401 | 0.19981 | 0.19982 | 0.19982 | 0.99876 | -0.021862 | 0.99872 | -0.021998 | 31.32
87 | 6.1397 | 2.9231 | -6.1395 | -2.9242 | 0.00024757 | -0.0011601 | 0.19655 | 0.19657 | 0.19657 | 0.99872 | -0.021998 | 0.99868 | -0.022162 | 30.81
88 | 0.071811 | 0.034619 | -0.071811 | -0.03478 | 4.7623e-08 | -0.0001605 | 0.0023021 | 0.0023041 | 0.0023041 | 0.99968 | -0.017995 | 0.99968 | -0.017989 | 1.0473
89 | -8.0982 | -3.8103 | 8.0996 | 3.814 | 0.0014006 | 0.0036852 | 0.25844 | 0.25844 | 0.25844 | 0.99968 | -0.017995 | 1 | 0 | 40.0685
90 | 0.24393 | 0.11805 | -0.24393 | -0.11814 | 3.2635e-07 | -9.4071e-05 | 0.0078477 | 0.0078489 | 0.0078489 | 0.99685 | -0.013397 | 0.99685 | -0.013386 | 3.5677
91 | 0.96268 | 0.45827 | -0.9626 | -0.45982 | 8.4671e-05 | -0.0015522 | 0.030876 | 0.030895 | 0.030895 | 0.99685 | -0.013397 | 0.99677 | -0.012657 | 14.0434
92 | 0.9626 | 0.45982 | -0.96259 | -0.45994 | 6.3641e-06 | -0.00011658 | 0.030895 | 0.030897 | 0.030897 | 0.99677 | -0.012657 | 0.99676 | -0.012601 | 14.044
93 | 0.34976 | 0.16808 | -0.34976 | -0.16817 | 6.7891e-07 | -9.5204e-05 | 0.011241 | 0.011242 | 0.011242 | 0.9965 | -0.012517 | 0.9965 | -0.0125 | 5.1102
94 | -0.34976 | -0.16827 | 0.34976 | 0.16817 | 7.2329e-07 | -0.0001014 | 0.011244 | 0.011242 | 0.011244 | 0.99649 | -0.012483 | 0.9965 | -0.0125 | 5.1108
95 | 0.078825 | 0.037057 | -0.078825 | -0.037162 | 3.7637e-08 | -0.00010495 | 0.0025232 | 0.0025245 | 0.0025245 | 0.99649 | -0.012483 | 0.99649 | -0.012479 | 1.1475
96 | 0.078825 | 0.037162 | -0.078825 | -0.037725 | 2.0276e-07 | -0.00056338 | 0.0025245 | 0.0025315 | 0.0025315 | 0.99649 | -0.012479 | 0.99649 | -0.012457 | 1.1507
97 | 0.078825 | 0.037725 | -0.078825 | -0.038177 | 1.634e-07 | -0.00045173 | 0.0025315 | 0.0025372 | 0.0025372 | 0.99649 | -0.012457 | 0.99649 | -0.012439 | 1.1533
98 | 0.90576 | 0.4206 | -0.90576 | -0.42072 | 5.4786e-06 | -0.00011609 | 0.028839 | 0.028841 | 0.028841 | 0.99964 | -0.00069584 | 0.99963 | -0.000648 | 13.1094
99 | -1.309 | -0.61592 | 1.3092 | 0.61596 | 0.00017037 | 4.1348e-05 | 0.041778 | 0.041777 | 0.041778 | 0.99964 | -0.00069584 | 0.99977 | 0.00025577 | 19.8941
100 | 0.90576 | 0.42072 | -0.90573 | -0.42137 | 3.0835e-05 | -0.00065316 | 0.028841 | 0.028849 | 0.028849 | 0.99963 | -0.000648 | 0.9996 | -0.00037817 | 13.113
101 | 0.23884 | 0.11553 | -0.23884 | -0.11568 | 4.6716e-07 | -0.00014212 | 0.0076608 | 0.0076626 | 0.0076626 | 0.99977 | 0.00025577 | 0.99977 | 0.00027279 | 3.483
102 | -1.548 | -0.73149 | 1.5482 | 0.73045 | 0.00014898 | -0.0010459 | 0.049437 | 0.049424 | 0.049437 | 0.99977 | 0.00025577 | 0.99986 | -0.00053567 | 22.4715
103 | 0.49858 | 0.22426 | -0.49858 | -0.22452 | 3.6228e-06 | -0.00025861 | 0.015788 | 0.015791 | 0.015791 | 0.9996 | -0.00037817 | 0.99959 | -0.00032505 | 7.1778
104 | 0.40715 | 0.19711 | -0.40713 | -0.19718 | 2.0059e-05 | -6.6119e-05 | 0.013064 | 0.013065 | 0.013065 | 0.9996 | -0.00037817 | 0.99955 | -0.00070319 | 6.2212
105 | -7.0097 | -3.3355 | 7.0107 | 3.3323 | 0.00091818 | -0.0032 | 0.22413 | 0.22408 | 0.22413 | 0.99986 | -0.00053567 | 1 | 0 | 35.1293
106 | 0.42664 | 0.18967 | -0.42663 | -0.19003 | 3.6008e-06 | -0.00035274 | 0.013484 | 0.013488 | 0.013488 | 0.99959 | -0.00032505 | 0.99958 | -0.00026516 | 6.1309
107 | 0.42663 | 0.19003 | -0.42656 | -0.1974 | 7.5834e-05 | -0.0073771 | 0.013488 | 0.013576 | 0.013576 | 0.99958 | -0.00026516 | 0.99942 | 0.0010645 | 6.171
108 | 0.26044 | 0.12584 | -0.26043 | -0.12613 | 1.1562e-06 | -0.00029537 | 0.008355 | 0.0083587 | 0.0083587 | 0.99938 | -0.01563 | 0.99937 | -0.015591 | 3.7994
109 | -0.26044 | -0.12584 | 0.26044 | 0.12501 | 3.245e-06 | -0.00083043 | 0.008355 | 0.0083446 | 0.008355 | 0.99938 | -0.01563 | 0.99939 | -0.015737 | 3.7977
110 | 0.13019 | 0.062251 | -0.13019 | -0.063053 | 7.8215e-07 | -0.00080196 | 0.0041683 | 0.0041783 | 0.0041783 | 0.99939 | -0.015737 | 0.99938 | -0.015686 | 1.8992
111 | -0.39063 | -0.18726 | 0.39064 | 0.18521 | 1.7944e-05 | -0.0020461 | 0.012513 | 0.012487 | 0.012513 | 0.99939 | -0.015737 | 0.99943 | -0.016123 | 5.6877
112 | 0.39065 | 0.18473 | -0.39064 | -0.18521 | 4.2317e-06 | -0.00048378 | 0.012481 | 0.012487 | 0.012487 | 0.99944 | -0.016213 | 0.99943 | -0.016123 | 5.6761
113 | 2.9895 | 1.4384 | -2.9894 | -1.4386 | 0.00012162 | -0.00019897 | 0.095982 | 0.095985 | 0.095985 | 0.99778 | -0.022782 | 0.99775 | -0.022432 | 43.6297
114 | 0.39771 | 0.18945 | -0.3977 | -0.19016 | 6.4404e-06 | -0.00070664 | 0.012731 | 0.01274 | 0.01274 | 0.99887 | -0.011561 | 0.99886 | -0.011424 | 5.7909
115 | 0.30876 | 0.14708 | -0.30875 | -0.14809 | 5.5186e-06 | -0.0010051 | 0.009884 | 0.0098965 | 0.0098965 | 0.99886 | -0.011424 | 0.99884 | -0.011273 | 4.4984
116 | 0.30875 | 0.14809 | -0.30874 | -0.14953 | 7.9534e-06 | -0.0014439 | 0.0098965 | 0.0099147 | 0.0099147 | 0.99884 | -0.011273 | 0.99882 | -0.011051 | 4.5067
117 | -0.10531 | -0.051006 | 0.10531 | 0.050699 | 1.9646e-07 | -0.00030751 | 0.0033799 | 0.0033761 | 0.0033799 | 0.99942 | 0.0010807 | 0.99942 | 0.0010645 | 1.5363
118 | 0.32124 | 0.14671 | -0.32121 | -0.15166 | 2.9109e-05 | -0.0049591 | 0.010201 | 0.010261 | 0.010261 | 0.99942 | 0.0010645 | 0.99933 | 0.0017811 | 4.6641
119 | 0.32121 | 0.15166 | -0.32121 | -0.152 | 2.0045e-06 | -0.0003393 | 0.010261 | 0.010265 | 0.010265 | 0.99933 | 0.0017811 | 0.99933 | 0.0018326 | 4.6661
120 | 0.23392 | 0.10973 | -0.23392 | -0.11002 | 9.3633e-07 | -0.00029979 | 0.0074636 | 0.0074673 | 0.0074673 | 0.99933 | 0.0018326 | 0.99932 | 0.0018651 | 3.3942
121 | 0.23392 | 0.11002 | -0.23391 | -0.11069 | 2.095e-06 | -0.00066967 | 0.0074673 | 0.0074755 | 0.0074755 | 0.99932 | 0.0018651 | 0.99931 | 0.0019386 | 3.398
122 | -0.16484 | -0.079835 | 0.16484 | 0.079328 | 7.9491e-07 | -0.00050751 | 0.0052909 | 0.0052846 | 0.0052909 | 0.99929 | 0.0021198 | 0.9993 | 0.0020781 | 2.405
123 | -0.16484 | -0.079328 | 0.16484 | 0.077566 | 2.7448e-06 | -0.0017619 | 0.0052846 | 0.0052627 | 0.0052846 | 0.9993 | 0.0020781 | 0.99931 | 0.0019386 | 2.4021
124 | 0.069071 | 0.033129 | -0.06907 | -0.033452 | 8.8933e-08 | -0.00032374 | 0.0022129 | 0.002217 | 0.002217 | 0.99931 | 0.0019386 | 0.99931 | 0.0019497 | 1.0077
125 | 0.092532 | 0.044737 | -0.092532 | -0.044815 | 3.8959e-08 | -7.8448e-05 | 0.0029737 | 0.0029747 | 0.0029747 | 0.99775 | -0.022432 | 0.99775 | -0.022429 | 1.3521
126 | 1.5405 | 0.74113 | -1.5404 | -0.74156 | 6.2586e-05 | -0.00043687 | 0.04946 | 0.049466 | 0.049466 | 0.99775 | -0.022432 | 0.99771 | -0.022083 | 22.4843
127 | 1.3564 | 0.65278 | -1.3563 | -0.65309 | 3.3388e-05 | -0.00030346 | 0.043552 | 0.043556 | 0.043556 | 0.99775 | -0.022432 | 0.99772 | -0.022221 | 19.7981
128 | 0.16958 | 0.081315 | -0.16958 | -0.081825 | 8.4984e-07 | -0.00051009 | 0.0054416 | 0.005448 | 0.005448 | 0.99771 | -0.022083 | 0.9977 | -0.02204 | 2.4764
129 | 1.3708 | 0.66025 | -1.3708 | -0.6606 | 3.9826e-05 | -0.00035397 | 0.044024 | 0.044029 | 0.044029 | 0.99771 | -0.022083 | 0.99768 | -0.021833 | 20.013
130 | 0.81481 | 0.39302 | -0.81476 | -0.39427 | 4.8852e-05 | -0.0012542 | 0.026174 | 0.02619 | 0.02619 | 0.99772 | -0.022221 | 0.99767 | -0.021701 | 11.9047
131 | 0.54153 | 0.26007 | -0.54153 | -0.26036 | 4.9258e-06 | -0.00028875 | 0.017381 | 0.017385 | 0.017385 | 0.99772 | -0.022221 | 0.99771 | -0.022143 | 7.9023
132 | 0.11404 | 0.054716 | -0.11404 | -0.055078 | 2.7288e-07 | -0.00036216 | 0.0036598 | 0.0036644 | 0.0036644 | 0.99768 | -0.021833 | 0.99768 | -0.021813 | 1.6656
133 | 1.2567 | 0.60589 | -1.2567 | -0.60633 | 4.1619e-05 | -0.00044222 | 0.040369 | 0.040374 | 0.040374 | 0.99768 | -0.021833 | 0.99765 | -0.021548 | 18.352
134 | 0.11404 | 0.055078 | -0.11404 | -0.055231 | 1.1543e-07 | -0.00015293 | 0.0036644 | 0.0036663 | 0.0036663 | 0.99768 | -0.021813 | 0.99768 | -0.021804 | 1.6665
135 | 0.43146 | 0.20665 | -0.43145 | -0.2074 | 8.1627e-06 | -0.00075535 | 0.013843 | 0.013852 | 0.013852 | 0.99765 | -0.021548 | 0.99763 | -0.021386 | 6.2964
136 | 0.085244 | 0.040978 | -0.085244 | -0.041285 | 1.297e-07 | -0.00030785 | 0.0027366 | 0.0027405 | 0.0027405 | 0.9977 | -0.02204 | 0.9977 | -0.022027 | 1.2457
137 | 0.075875 | 0.036413 | -0.075875 | -0.036748 | 1.1163e-07 | -0.00033448 | 0.0024352 | 0.0024394 | 0.0024394 | 0.99767 | -0.021701 | 0.99767 | -0.021689 | 1.1088
138 | 0.43006 | 0.20637 | -0.43005 | -0.20659 | 2.3471e-06 | -0.00021862 | 0.013802 | 0.013804 | 0.013804 | 0.99771 | -0.022143 | 0.99771 | -0.022096 | 6.2747
139 | -0.075055 | -0.036351 | 0.075055 | 0.036215 | 4.4382e-08 | -0.00013587 | 0.0024122 | 0.0024104 | 0.0024122 | 0.99802 | -0.016249 | 0.99802 | -0.016254 | 1.0964
140 | -0.093509 | -0.045288 | 0.093509 | 0.044937 | 1.7743e-07 | -0.00035135 | 0.0030033 | 0.0029989 | 0.0030033 | 0.99867 | -0.022098 | 0.99867 | -0.022114 | 1.3651
141 | -0.093509 | -0.044937 | 0.093509 | 0.044833 | 5.2552e-08 | -0.00010424 | 0.0029989 | 0.0029976 | 0.0029989 | 0.99867 | -0.022114 | 0.99867 | -0.022119 | 1.3631
142 | 0.069579 | 0.033484 | -0.069579 | -0.033699 | 5.9992e-08 | -0.0002145 | 0.002232 | 0.0022347 | 0.0022347 | 0.99867 | -0.022119 | 0.99867 | -0.022112 | 1.0158
143 | -0.16309 | -0.078317 | 0.16309 | 0.077783 | 8.1827e-07 | -0.00053413 | 0.0052296 | 0.0052229 | 0.0052296 | 0.99867 | -0.022119 | 0.99868 | -0.022162 | 2.3771
144 | 5.9764 | 2.8464 | -5.9761 | -2.8478 | 0.00027536 | -0.00137 | 0.19135 | 0.19136 | 0.19136 | 0.99868 | -0.022162 | 0.99863 | -0.022348 | 29.9944
145 | 5.9761 | 2.8478 | -5.976 | -2.8485 | 0.00014703 | -0.00073131 | 0.19136 | 0.19137 | 0.19137 | 0.99863 | -0.022348 | 0.99861 | -0.022448 | 29.9959
146 | 5.881 | 2.8025 | -5.8809 | -2.8029 | 6.5453e-05 | -0.00033735 | 0.18832 | 0.18833 | 0.18833 | 0.99861 | -0.022448 | 0.99859 | -0.022493 | 29.5184
147 | 0.43145 | 0.2074 | -0.43145 | -0.20774 | 3.6842e-06 | -0.00034057 | 0.013852 | 0.013856 | 0.013856 | 0.99763 | -0.021386 | 0.99763 | -0.021313 | 6.2983
148 | 0.43145 | 0.20774 | -0.43144 | -0.20818 | 4.7738e-06 | -0.00044098 | 0.013856 | 0.013862 | 0.013862 | 0.99763 | -0.021313 | 0.99762 | -0.021217 | 6.3009
149 | 0.36205 | 0.17457 | -0.36205 | -0.17526 | 5.2138e-06 | -0.00068396 | 0.011631 | 0.011639 | 0.011639 | 0.99762 | -0.021217 | 0.9976 | -0.021093 | 5.2906
150 | 0.36205 | 0.17526 | -0.36204 | -0.17535 | 6.7231e-07 | -8.8123e-05 | 0.011639 | 0.011641 | 0.011641 | 0.9976 | -0.021093 | 0.9976 | -0.021077 | 5.2911
151 | 0.43005 | 0.20659 | -0.43005 | -0.20673 | 1.5291e-06 | -0.00014238 | 0.013804 | 0.013806 | 0.013806 | 0.99771 | -0.022096 | 0.99771 | -0.022066 | 6.2755
152 | 0.27092 | 0.13047 | -0.27092 | -0.13121 | 3.1526e-06 | -0.00073968 | 0.0087005 | 0.0087098 | 0.0087098 | 0.99771 | -0.022066 | 0.9977 | -0.021965 | 3.959
153 | 0.15913 | 0.076258 | -0.15913 | -0.076764 | 7.4145e-07 | -0.00050552 | 0.0051056 | 0.005112 | 0.005112 | 0.99771 | -0.022066 | 0.9977 | -0.022026 | 2.3236
154 | 0.15913 | 0.076764 | -0.15913 | -0.07707 | 4.4951e-07 | -0.00030586 | 0.005112 | 0.0051158 | 0.0051158 | 0.9977 | -0.022026 | 0.9977 | -0.022002 | 2.3254
155 | 5.7366 | 2.7337 | -5.7365 | -2.734 | 5.778e-05 | -0.00031463 | 0.1837 | 0.18371 | 0.18371 | 0.99859 | -0.022493 | 0.99858 | -0.022533 | 28.794
156 | 0.14432 | 0.069147 | -0.14432 | -0.069447 | 3.6073e-07 | -0.00030026 | 0.0046261 | 0.0046299 | 0.0046299 | 0.99859 | -0.022493 | 0.99859 | -0.022471 | 2.1045
157 | -0.074936 | -0.036293 | 0.074937 | 0.035845 | 1.4549e-07 | -0.00044885 | 0.002407 | 0.0024014 | 0.002407 | 0.99859 | -0.022455 | 0.99859 | -0.022471 | 1.0941
158 | 5.7365 | 2.734 | -5.7364 | -2.7345 | 8.908e-05 | -0.00048502 | 0.18371 | 0.18371 | 0.18371 | 0.99858 | -0.022533 | 0.99857 | -0.022596 | 28.795
159 | 5.6496 | 2.6925 | -5.6496 | -2.6927 | 4.4589e-05 | -0.00025108 | 0.18092 | 0.18093 | 0.18093 | 0.99857 | -0.022596 | 0.99856 | -0.022628 | 28.3585

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 15.1242 | 7.1568

## res_load
| p_mw | q_mvar
0 | 0.3964 | 0.19199
1 | 0.1421 | 0.06882
2 | 0.32094 | 0.15544
3 | 0.37973 | 0.18391
4 | 0.096791 | 0.046878
5 | 0.25401 | 0.12302
6 | 0.31869 | 0.15435
7 | 0.072204 | 0.03497
8 | 0.40971 | 0.19843
9 | 0.11729 | 0.056808
10 | 0.23337 | 0.11303
11 | 0.077305 | 0.03744
12 | 0.29817 | 0.14441
13 | 0.21796 | 0.10556
14 | 0.2154 | 0.10432
15 | 0.11461 | 0.055508
16 | 0.10553 | 0.051112
17 | 0.25963 | 0.12575
18 | 0.072581 | 0.035153
19 | 0.17099 | 0.082815
20 | 0.3411 | 0.1652
21 | 0.2494 | 0.12079
22 | 0.33558 | 0.16253
23 | 0.10554 | 0.051114
24 | 0.24302 | 0.1177
25 | 0.0705 | 0.034145
26 | 0.086148 | 0.041723
27 | 0.2558 | 0.12389
28 | 0.068208 | 0.033035
29 | 0.30623 | 0.14831
30 | 0.091779 | 0.04445
31 | 0.31462 | 0.15238
32 | 0.095322 | 0.046167
33 | 0.1419 | 0.068723
34 | 0.10182 | 0.049312
35 | 0.31918 | 0.15458
36 | 0.24393 | 0.11814
37 | 0.4108 | 0.19896
38 | 0.084473 | 0.040912
39 | 0.28267 | 0.1369
40 | 0.27093 | 0.13122
41 | 0.078825 | 0.038177
42 | 0.40327 | 0.19531
43 | 0.23884 | 0.11568
44 | 0.07194 | 0.034842
45 | 0.40713 | 0.19718
46 | 0.26043 | 0.12613
47 | 0.086893 | 0.042084
48 | 0.071811 | 0.03478
49 | 0.13019 | 0.063053
50 | 0.2679 | 0.12975
51 | 0.088942 | 0.043077
52 | 0.10531 | 0.051006
53 | 0.087295 | 0.042279
54 | 0.16484 | 0.079835
55 | 0.06907 | 0.033452
56 | 0.092532 | 0.044815
57 | 0.82524 | 0.39968
58 | 0.11404 | 0.055231
59 | 0.084339 | 0.040847
60 | 0.73889 | 0.35786
61 | 0.11147 | 0.053986
62 | 0.075055 | 0.036351
63 | 0.093509 | 0.045288
64 | 0.069579 | 0.033699
65 | 0.095003 | 0.046012
66 | 0.069393 | 0.033608
67 | 0.085244 | 0.041285
68 | 0.36204 | 0.17535
69 | 0.27092 | 0.13121
70 | 0.075875 | 0.036748
71 | 0.15913 | 0.07707
72 | 0.074936 | 0.036293
73 | 0.069381 | 0.033603
74 | 0.086807 | 0.042042
75 | 0.30874 | 0.14953

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1