## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_668_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_668_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_668_0_node_4 | 20 | n |  | TRUE
3 | bus_MV_668_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_668_0_node_116 | 20 | n |  | TRUE
5 | bus_MV_668_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_668_0_node_169 | 20 | n |  | TRUE
7 | bus_MV_668_0_node_157 | 20 | n |  | TRUE
8 | bus_MV_668_0_node_146 | 20 | n |  | TRUE
9 | bus_MV_668_0_node_160 | 20 | n |  | TRUE
10 | bus_MV_668_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_668_0_node_52 | 20 | n |  | TRUE
12 | bus_MV_668_0_node_143 | 20 | n |  | TRUE
13 | bus_MV_668_0_node_171 | 20 | n |  | TRUE
14 | bus_MV_668_0_node_117 | 20 | n |  | TRUE
15 | bus_MV_668_0_node_167 | 20 | n |  | TRUE
16 | bus_MV_668_0_node_155 | 20 | n |  | TRUE
17 | bus_MV_668_0_node_172 | 20 | n |  | TRUE
18 | bus_MV_668_0_node_144 | 20 | n |  | TRUE
19 | bus_MV_668_0_node_142 | 20 | n |  | TRUE
20 | bus_MV_668_0_node_6 | 20 | n |  | TRUE
21 | bus_MV_668_0_node_7 | 20 | n |  | TRUE
22 | bus_MV_668_0_node_10 | 20 | n |  | TRUE
23 | bus_MV_668_0_node_12 | 20 | n |  | TRUE
24 | bus_MV_668_0_node_8 | 20 | n |  | TRUE
25 | bus_MV_668_0_node_11 | 20 | n |  | TRUE
26 | bus_MV_668_0_node_64 | 20 | n |  | TRUE
27 | bus_MV_668_0_node_9 | 20 | n |  | TRUE
28 | bus_MV_668_0_node_105 | 20 | n |  | TRUE
29 | bus_MV_668_0_node_61 | 20 | n |  | TRUE
30 | bus_MV_668_0_node_104 | 20 | n |  | TRUE
31 | bus_MV_668_0_node_57 | 20 | n |  | TRUE
32 | bus_MV_668_0_node_103 | 20 | n |  | TRUE
33 | bus_MV_668_0_node_62 | 20 | n |  | TRUE
34 | bus_MV_668_0_node_158 | 20 | n |  | TRUE
35 | bus_MV_668_0_node_60 | 20 | n |  | TRUE
36 | bus_MV_668_0_node_24 | 20 | n |  | TRUE
37 | bus_MV_668_0_node_58 | 20 | n |  | TRUE
38 | bus_MV_668_0_node_55 | 20 | n |  | TRUE
39 | bus_MV_668_0_node_13 | 20 | n |  | TRUE
40 | bus_MV_668_0_node_14 | 20 | n |  | TRUE
41 | bus_MV_668_0_node_15 | 20 | n |  | TRUE
42 | bus_MV_668_0_node_16 | 20 | n |  | TRUE
43 | bus_MV_668_0_node_17 | 20 | n |  | TRUE
44 | bus_MV_668_0_node_22 | 20 | n |  | TRUE
45 | bus_MV_668_0_node_165 | 20 | n |  | TRUE
46 | bus_MV_668_0_node_18 | 20 | n |  | TRUE
47 | bus_MV_668_0_node_78 | 20 | n |  | TRUE
48 | bus_MV_668_0_node_20 | 20 | n |  | TRUE
49 | bus_MV_668_0_node_56 | 20 | n |  | TRUE
50 | bus_MV_668_0_node_19 | 20 | n |  | TRUE
51 | bus_MV_668_0_node_161 | 20 | n |  | TRUE
52 | bus_MV_668_0_node_43 | 20 | n |  | TRUE
53 | bus_MV_668_0_node_21 | 20 | n |  | TRUE
54 | bus_MV_668_0_node_42 | 20 | n |  | TRUE
55 | bus_MV_668_0_node_44 | 20 | n |  | TRUE
56 | bus_MV_668_0_node_121 | 20 | n |  | TRUE
57 | bus_MV_668_0_node_124 | 20 | n |  | TRUE
58 | bus_MV_668_0_node_23 | 20 | n |  | TRUE
59 | bus_MV_668_0_node_63 | 20 | n |  | TRUE
60 | bus_MV_668_0_node_159 | 20 | n |  | TRUE
61 | bus_MV_668_0_node_80 | 20 | n |  | TRUE
62 | bus_MV_668_0_node_79 | 20 | n |  | TRUE
63 | bus_MV_668_0_node_126 | 20 | n |  | TRUE
64 | bus_MV_668_0_node_114 | 20 | n |  | TRUE
65 | bus_MV_668_0_node_29 | 20 | n |  | TRUE
66 | bus_MV_668_0_node_122 | 20 | n |  | TRUE
67 | bus_MV_668_0_node_147 | 20 | n |  | TRUE
68 | bus_MV_668_0_node_120 | 20 | n |  | TRUE
69 | bus_MV_668_0_node_119 | 20 | n |  | TRUE
70 | bus_MV_668_0_node_123 | 20 | n |  | TRUE
71 | bus_MV_668_0_node_25 | 20 | n |  | TRUE
72 | bus_MV_668_0_node_26 | 20 | n |  | TRUE
73 | bus_MV_668_0_node_27 | 20 | n |  | TRUE
74 | bus_MV_668_0_node_28 | 20 | n |  | TRUE
75 | bus_MV_668_0_node_31 | 20 | n |  | TRUE
76 | bus_MV_668_0_node_30 | 20 | n |  | TRUE
77 | bus_MV_668_0_node_84 | 20 | n |  | TRUE
78 | bus_MV_668_0_node_131 | 20 | n |  | TRUE
79 | bus_MV_668_0_node_125 | 20 | n |  | TRUE
80 | bus_MV_668_0_node_83 | 20 | n |  | TRUE
81 | bus_MV_668_0_node_32 | 20 | n |  | TRUE
82 | bus_MV_668_0_node_33 | 20 | n |  | TRUE
83 | bus_MV_668_0_node_34 | 20 | n |  | TRUE
84 | bus_MV_668_0_node_35 | 20 | n |  | TRUE
85 | bus_MV_668_0_node_36 | 20 | n |  | TRUE
86 | bus_MV_668_0_node_37 | 20 | n |  | TRUE
87 | bus_MV_668_0_node_138 | 20 | n |  | TRUE
88 | bus_MV_668_0_node_132 | 20 | n |  | TRUE
89 | bus_MV_668_0_node_134 | 20 | n |  | TRUE
90 | bus_MV_668_0_node_38 | 20 | n |  | TRUE
91 | bus_MV_668_0_node_95 | 20 | n |  | TRUE
92 | bus_MV_668_0_node_100 | 20 | n |  | TRUE
93 | bus_MV_668_0_node_164 | 20 | n |  | TRUE
94 | bus_MV_668_0_node_39 | 20 | n |  | TRUE
95 | bus_MV_668_0_node_41 | 20 | n |  | TRUE
96 | bus_MV_668_0_node_150 | 20 | n |  | TRUE
97 | bus_MV_668_0_node_40 | 20 | n |  | TRUE
98 | bus_MV_668_0_node_170 | 20 | n |  | TRUE
99 | bus_MV_668_0_node_76 | 20 | n |  | TRUE
100 | bus_MV_668_0_node_141 | 20 | n |  | TRUE
101 | bus_MV_668_0_node_151 | 20 | n |  | TRUE
102 | bus_MV_668_0_node_68 | 20 | n |  | TRUE
103 | bus_MV_668_0_node_97 | 20 | n |  | TRUE
104 | bus_MV_668_0_node_90 | 20 | n |  | TRUE
105 | bus_MV_668_0_node_50 | 20 | n |  | TRUE
106 | bus_MV_668_0_node_71 | 20 | n |  | TRUE
107 | bus_MV_668_0_node_75 | 20 | n |  | TRUE
108 | bus_MV_668_0_node_69 | 20 | n |  | TRUE
109 | bus_MV_668_0_node_148 | 20 | n |  | TRUE
110 | bus_MV_668_0_node_66 | 20 | n |  | TRUE
111 | bus_MV_668_0_node_149 | 20 | n |  | TRUE
112 | bus_MV_668_0_node_154 | 20 | n |  | TRUE
113 | bus_MV_668_0_node_81 | 20 | n |  | TRUE
114 | bus_MV_668_0_node_110 | 20 | n |  | TRUE
115 | bus_MV_668_0_node_112 | 20 | n |  | TRUE
116 | bus_MV_668_0_node_127 | 20 | n |  | TRUE
117 | bus_MV_668_0_node_45 | 20 | n |  | TRUE
118 | bus_MV_668_0_node_46 | 20 | n |  | TRUE
119 | bus_MV_668_0_node_47 | 20 | n |  | TRUE
120 | bus_MV_668_0_node_48 | 20 | n |  | TRUE
121 | bus_MV_668_0_node_137 | 20 | n |  | TRUE
122 | bus_MV_668_0_node_49 | 20 | n |  | TRUE
123 | bus_MV_668_0_node_51 | 20 | n |  | TRUE
124 | bus_MV_668_0_node_140 | 20 | n |  | TRUE
125 | bus_MV_668_0_node_139 | 20 | n |  | TRUE
126 | bus_MV_668_0_node_101 | 20 | n |  | TRUE
127 | bus_MV_668_0_node_99 | 20 | n |  | TRUE
128 | bus_MV_668_0_node_133 | 20 | n |  | TRUE
129 | bus_MV_668_0_node_136 | 20 | n |  | TRUE
130 | bus_MV_668_0_node_102 | 20 | n |  | TRUE
131 | bus_MV_668_0_node_53 | 20 | n |  | TRUE
132 | bus_MV_668_0_node_54 | 20 | n |  | TRUE
133 | bus_MV_668_0_node_168 | 20 | n |  | TRUE
134 | bus_MV_668_0_node_59 | 20 | n |  | TRUE
135 | bus_MV_668_0_node_65 | 20 | n |  | TRUE
136 | bus_MV_668_0_node_67 | 20 | n |  | TRUE
137 | bus_MV_668_0_node_77 | 20 | n |  | TRUE
138 | bus_MV_668_0_node_70 | 20 | n |  | TRUE
139 | bus_MV_668_0_node_73 | 20 | n |  | TRUE
140 | bus_MV_668_0_node_153 | 20 | n |  | TRUE
141 | bus_MV_668_0_node_74 | 20 | n |  | TRUE
142 | bus_MV_668_0_node_152 | 20 | n |  | TRUE
143 | bus_MV_668_0_node_82 | 20 | n |  | TRUE
144 | bus_MV_668_0_node_85 | 20 | n |  | TRUE
145 | bus_MV_668_0_node_111 | 20 | n |  | TRUE
146 | bus_MV_668_0_node_86 | 20 | n |  | TRUE
147 | bus_MV_668_0_node_87 | 20 | n |  | TRUE
148 | bus_MV_668_0_node_88 | 20 | n |  | TRUE
149 | bus_MV_668_0_node_89 | 20 | n |  | TRUE
150 | bus_MV_668_0_node_91 | 20 | n |  | TRUE
151 | bus_MV_668_0_node_98 | 20 | n |  | TRUE
152 | bus_MV_668_0_node_92 | 20 | n |  | TRUE
153 | bus_MV_668_0_node_93 | 20 | n |  | TRUE
154 | bus_MV_668_0_node_106 | 20 | n |  | TRUE
155 | bus_MV_668_0_node_94 | 20 | n |  | TRUE
156 | bus_MV_668_0_node_107 | 20 | n |  | TRUE
157 | bus_MV_668_0_node_109 | 20 | n |  | TRUE
158 | bus_MV_668_0_node_108 | 20 | n |  | TRUE
159 | bus_MV_668_0_node_115 | 20 | n |  | TRUE
160 | bus_MV_668_0_node_113 | 20 | n |  | TRUE
161 | bus_MV_668_0_node_166 | 20 | n |  | TRUE
162 | bus_MV_668_0_node_96 | 20 | n |  | TRUE
163 | bus_MV_668_0_node_156 | 20 | n |  | TRUE
164 | bus_MV_668_0_node_118 | 20 | n |  | TRUE
165 | bus_MV_668_0_node_162 | 20 | n |  | TRUE
166 | bus_MV_668_0_node_128 | 20 | n |  | TRUE
167 | bus_MV_668_0_node_129 | 20 | n |  | TRUE
168 | bus_MV_668_0_node_130 | 20 | n |  | TRUE
169 | bus_MV_668_0_node_163 | 20 | n |  | TRUE
170 | bus_MV_668_0_node_135 | 20 | n |  | TRUE
171 | bus_HV_668_0_node_94 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_668_0_load_0 | 0 | 0.29421 | 0.14249 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_668_0_load_116 | 4 | 0.082827 | 0.040115 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_668_0_load_169 | 6 | 0.1015 | 0.049158 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_668_0_load_160 | 9 | 0.39804 | 0.19278 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_668_0_load_52 | 11 | 0.39493 | 0.19127 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_668_0_load_171 | 13 | 0.14236 | 0.068948 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_668_0_load_167 | 15 | 0.096873 | 0.046918 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_668_0_load_172 | 17 | 0.31231 | 0.15126 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_668_0_load_142 | 19 | 1.2459 | 0.60343 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_668_0_load_6 | 20 | 0.35019 | 0.1696 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_668_0_load_64 | 26 | 0.21097 | 0.10218 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_668_0_load_105 | 28 | 0.074573 | 0.036117 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_668_0_load_104 | 30 | 0.099564 | 0.048221 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_668_0_load_57 | 31 | 0.32513 | 0.15747 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_668_0_load_103 | 32 | 0.11068 | 0.053603 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_668_0_load_158 | 34 | 0.17794 | 0.086178 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_668_0_load_60 | 35 | 0.17776 | 0.086091 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_668_0_load_13 | 39 | 0.3995 | 0.19349 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_668_0_load_165 | 45 | 0.1853 | 0.089747 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_668_0_load_78 | 47 | 0.19863 | 0.096202 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_668_0_load_56 | 49 | 0.33502 | 0.16226 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_668_0_load_161 | 51 | 0.17464 | 0.084584 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_668_0_load_42 | 54 | 0.37196 | 0.18015 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_668_0_load_124 | 57 | 0.073378 | 0.035538 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_668_0_load_63 | 59 | 0.1665 | 0.080638 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_668_0_load_159 | 60 | 0.28706 | 0.13903 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_668_0_load_79 | 62 | 0.077897 | 0.037727 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_668_0_load_126 | 63 | 0.22294 | 0.10798 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_668_0_load_147 | 67 | 0.094071 | 0.045561 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_668_0_load_119 | 69 | 0.11879 | 0.057535 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_668_0_load_123 | 70 | 0.10641 | 0.051538 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_668_0_load_25 | 71 | 0.3047 | 0.14757 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_668_0_load_31 | 75 | 0.11738 | 0.056848 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_668_0_load_84 | 77 | 0.12364 | 0.05988 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_668_0_load_131 | 78 | 0.078247 | 0.037897 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_668_0_load_125 | 79 | 0.26108 | 0.12645 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_668_0_load_32 | 81 | 0.25463 | 0.12332 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_668_0_load_138 | 87 | 0.092748 | 0.04492 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_668_0_load_132 | 88 | 0.11526 | 0.055823 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_668_0_load_134 | 89 | 0.099812 | 0.048341 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_668_0_load_100 | 92 | 1.2664 | 0.61335 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_668_0_load_164 | 93 | 0.095477 | 0.046242 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_668_0_load_150 | 96 | 0.20886 | 0.10116 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_668_0_load_170 | 98 | 0.16816 | 0.081442 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_668_0_load_141 | 100 | 0.49088 | 0.23775 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_668_0_load_151 | 101 | 0.11342 | 0.054933 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_668_0_load_90 | 104 | 0.96129 | 0.46557 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_668_0_load_69 | 108 | 0.27142 | 0.13146 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_668_0_load_148 | 109 | 0.32267 | 0.15628 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_668_0_load_149 | 111 | 0.32075 | 0.15535 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_668_0_load_154 | 112 | 0.080149 | 0.038818 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_668_0_load_110 | 114 | 0.082014 | 0.039721 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_668_0_load_112 | 115 | 0.069288 | 0.033558 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_668_0_load_127 | 116 | 0.099584 | 0.048231 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_668_0_load_45 | 117 | 0.16826 | 0.08149 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_668_0_load_137 | 121 | 0.2301 | 0.11144 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_668_0_load_140 | 124 | 0.1258 | 0.06093 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_668_0_load_139 | 125 | 0.17904 | 0.086715 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_668_0_load_99 | 127 | 0.11478 | 0.055591 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_668_0_load_133 | 128 | 0.19219 | 0.093081 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_668_0_load_136 | 129 | 0.11581 | 0.056088 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_668_0_load_102 | 130 | 0.16002 | 0.077502 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_668_0_load_53 | 131 | 0.20678 | 0.10015 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_668_0_load_168 | 133 | 0.14011 | 0.067859 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_668_0_load_65 | 135 | 0.37423 | 0.18125 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_668_0_load_77 | 137 | 0.2658 | 0.12873 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_668_0_load_153 | 140 | 0.1306 | 0.063253 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_668_0_load_74 | 141 | 0.20618 | 0.099856 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_668_0_load_152 | 142 | 0.081585 | 0.039513 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_668_0_load_82 | 143 | 0.28394 | 0.13752 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_668_0_load_111 | 145 | 0.12319 | 0.059662 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_668_0_load_87 | 147 | 0.14659 | 0.070995 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_668_0_load_88 | 148 | 1.4858 | 0.71959 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_668_0_load_98 | 151 | 0.097689 | 0.047313 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_668_0_load_106 | 154 | 0.10322 | 0.049991 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_668_0_load_107 | 156 | 0.58913 | 0.28533 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_668_0_load_108 | 158 | 0.22883 | 0.11083 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_668_0_load_113 | 160 | 0.10072 | 0.048781 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_668_0_load_166 | 161 | 0.26404 | 0.12788 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_668_0_load_96 | 162 | 0.090379 | 0.043772 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_668_0_load_156 | 163 | 0.20456 | 0.099071 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_668_0_load_162 | 165 | 0.2438 | 0.11808 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_668_0_load_129 | 167 | 0.14892 | 0.072123 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_668_0_load_163 | 169 | 0.36711 | 0.1778 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_668_0_load_135 | 170 | 0.11424 | 0.055327 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 155 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_668_0_line_0 |  | 0 | 1 | 0.004102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_668_0_line_1 |  | 1 | 2 | 0.25588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_668_0_line_2 |  | 2 | 8 | 0.3132 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_668_0_line_3 |  | 2 | 9 | 0.015429 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_668_0_line_4 |  | 2 | 3 | 0.14564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_668_0_line_5 |  | 2 | 5 | 0.31313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_668_0_line_6 |  | 3 | 4 | 0.052029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_668_0_line_7 |  | 4 | 14 | 0.046609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_668_0_line_8 |  | 5 | 6 | 0.020732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_668_0_line_9 |  | 5 | 7 | 0.01482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_668_0_line_10 |  | 7 | 15 | 0.021906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_668_0_line_11 |  | 7 | 16 | 0.18049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_668_0_line_12 |  | 8 | 17 | 0.017163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_668_0_line_13 |  | 8 | 18 | 0.42735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_668_0_line_14 |  | 10 | 11 | 0.045327 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_668_0_line_15 |  | 10 | 12 | 0.15268 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_668_0_line_16 |  | 10 | 13 | 0.24216 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_668_0_line_17 |  | 12 | 19 | 0.048114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_668_0_line_18 |  | 13 | 18 | 0.015115 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_668_0_line_19 |  | 14 | 164 | 0.234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_668_0_line_20 |  | 16 | 163 | 0.037244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_668_0_line_21 |  | 16 | 64 | 0.27278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_668_0_line_22 |  | 20 | 21 | 0.019711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_668_0_line_23 |  | 21 | 22 | 0.35477 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_668_0_line_24 |  | 21 | 23 | 0.40143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_668_0_line_25 |  | 22 | 29 | 0.53641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_668_0_line_26 |  | 22 | 30 | 0.049914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_668_0_line_27 |  | 23 | 32 | 0.036855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_668_0_line_28 |  | 23 | 27 | 0.32269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_668_0_line_29 |  | 24 | 25 | 0.19295 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_668_0_line_30 |  | 24 | 26 | 0.032158 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_668_0_line_31 |  | 25 | 31 | 0.015083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_668_0_line_32 |  | 27 | 28 | 0.056799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_668_0_line_33 |  | 29 | 35 | 0.005684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_668_0_line_34 |  | 29 | 33 | 0.81207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_668_0_line_35 |  | 30 | 36 | 0.027153 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_668_0_line_36 |  | 31 | 37 | 0.10543 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_668_0_line_37 |  | 32 | 38 | 0.048503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_668_0_line_38 |  | 33 | 34 | 0.1856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_668_0_line_39 |  | 36 | 58 | 0.56026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_668_0_line_40 |  | 37 | 134 | 0.23882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_668_0_line_41 |  | 38 | 133 | 0.08989 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_668_0_line_42 |  | 38 | 132 | 0.073581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_668_0_line_43 |  | 39 | 40 | 0.01156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_668_0_line_44 |  | 39 | 41 | 0.026858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_668_0_line_45 |  | 40 | 42 | 0.31662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_668_0_line_46 |  | 40 | 43 | 0.33002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_668_0_line_47 |  | 41 | 44 | 0.32538 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_668_0_line_48 |  | 42 | 45 | 0.071893 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_668_0_line_49 |  | 43 | 46 | 0.18396 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_668_0_line_50 |  | 43 | 47 | 0.044782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_668_0_line_51 |  | 44 | 58 | 0.25449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_668_0_line_52 |  | 44 | 59 | 0.016537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_668_0_line_53 |  | 46 | 48 | 0.7462 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_668_0_line_54 |  | 46 | 49 | 0.004337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_668_0_line_55 |  | 48 | 53 | 0.27635 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_668_0_line_56 |  | 48 | 54 | 0.00432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_668_0_line_57 |  | 48 | 50 | 0.65734 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
58 | MV_668_0_line_58 |  | 50 | 51 | 0.005739 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_668_0_line_59 |  | 50 | 52 | 0.20248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_668_0_line_60 |  | 51 | 64 | 0.008537 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
61 | MV_668_0_line_61 |  | 52 | 61 | 0.081873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_668_0_line_62 |  | 52 | 62 | 0.07476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_668_0_line_63 |  | 53 | 55 | 0.49547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_668_0_line_64 |  | 53 | 56 | 0.060664 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_668_0_line_65 |  | 53 | 57 | 0.071746 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_668_0_line_66 |  | 54 | 65 | 0.025298 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_668_0_line_67 |  | 55 | 63 | 0.042619 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_668_0_line_68 |  | 56 | 70 | 0.03203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_668_0_line_69 |  | 56 | 66 | 0.31448 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_668_0_line_70 |  | 58 | 60 | 0.034506 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_668_0_line_71 |  | 61 | 113 | 0.30161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_668_0_line_72 |  | 61 | 114 | 0.077814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_668_0_line_73 |  | 63 | 116 | 0.017103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_668_0_line_74 |  | 64 | 159 | 0.12932 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
75 | MV_668_0_line_75 |  | 65 | 76 | 0.13947 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_668_0_line_76 |  | 66 | 67 | 0.035737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_668_0_line_77 |  | 66 | 68 | 0.48789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_668_0_line_78 |  | 68 | 69 | 0.037381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_668_0_line_79 |  | 71 | 72 | 0.11356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_668_0_line_80 |  | 72 | 73 | 0.012339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_668_0_line_81 |  | 72 | 74 | 0.18085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_668_0_line_82 |  | 73 | 75 | 0.11739 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_668_0_line_83 |  | 74 | 76 | 0.12268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_668_0_line_84 |  | 74 | 77 | 0.031252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_668_0_line_85 |  | 75 | 79 | 0.041834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_668_0_line_86 |  | 76 | 78 | 0.025535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_668_0_line_87 |  | 77 | 80 | 0.0084089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_668_0_line_88 |  | 80 | 144 | 0.26445 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_668_0_line_89 |  | 80 | 143 | 0.022332 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_668_0_line_90 |  | 81 | 82 | 0.024703 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_668_0_line_91 |  | 82 | 83 | 0.013844 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_668_0_line_92 |  | 82 | 84 | 0.040402 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_668_0_line_93 |  | 82 | 85 | 0.0463 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_668_0_line_94 |  | 83 | 86 | 0.26341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_668_0_line_95 |  | 83 | 87 | 0.08515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_668_0_line_96 |  | 84 | 88 | 0.069726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_668_0_line_97 |  | 85 | 89 | 0.013882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_668_0_line_98 |  | 86 | 90 | 0.69196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_668_0_line_99 |  | 86 | 91 | 0.020002 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
100 | MV_668_0_line_100 |  | 86 | 92 | 0.089765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_668_0_line_101 |  | 90 | 93 | 0.006556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_668_0_line_102 |  | 90 | 94 | 0.57763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_668_0_line_103 |  | 91 | 103 | 0.0085263 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_668_0_line_104 |  | 91 | 104 | 0.061286 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
105 | MV_668_0_line_105 |  | 92 | 105 | 0.036064 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_668_0_line_106 |  | 94 | 95 | 0.020916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_668_0_line_107 |  | 94 | 96 | 0.06693 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_668_0_line_108 |  | 95 | 100 | 0.062944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_668_0_line_109 |  | 95 | 97 | 0.17571 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_668_0_line_110 |  | 96 | 111 | 0.083681 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_668_0_line_111 |  | 97 | 98 | 0.02038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_668_0_line_112 |  | 97 | 99 | 0.3313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_668_0_line_113 |  | 98 | 112 | 0.12201 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_668_0_line_114 |  | 99 | 101 | 0.032896 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_668_0_line_115 |  | 99 | 102 | 0.68257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_668_0_line_116 |  | 101 | 142 | 0.0055704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_668_0_line_117 |  | 102 | 109 | 0.0094097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_668_0_line_118 |  | 102 | 110 | 0.27001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_668_0_line_119 |  | 103 | 162 | 0.040255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_668_0_line_120 |  | 104 | 149 | 0.047165 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
121 | MV_668_0_line_121 |  | 105 | 126 | 0.075585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_668_0_line_122 |  | 105 | 127 | 0.037971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_668_0_line_123 |  | 105 | 118 | 0.2454 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_668_0_line_124 |  | 106 | 107 | 0.01981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_668_0_line_125 |  | 106 | 108 | 0.026893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_668_0_line_126 |  | 107 | 140 | 0.069622 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_668_0_line_127 |  | 108 | 138 | 0.09173 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_668_0_line_128 |  | 110 | 136 | 0.59039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_668_0_line_129 |  | 110 | 135 | 0.014205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_668_0_line_130 |  | 112 | 139 | 0.051852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_668_0_line_131 |  | 113 | 115 | 0.05172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_668_0_line_132 |  | 116 | 166 | 0.034564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_668_0_line_133 |  | 117 | 118 | 0.15088 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
134 | MV_668_0_line_134 |  | 118 | 119 | 0.47052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_668_0_line_135 |  | 119 | 120 | 0.17567 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_668_0_line_136 |  | 119 | 121 | 0.048253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_668_0_line_137 |  | 120 | 122 | 0.1149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_668_0_line_138 |  | 120 | 123 | 0.25761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_668_0_line_139 |  | 120 | 124 | 0.11569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_668_0_line_140 |  | 121 | 129 | 0.047362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_668_0_line_141 |  | 122 | 125 | 0.036612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_668_0_line_142 |  | 123 | 128 | 0.066154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_668_0_line_143 |  | 126 | 130 | 0.027269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_668_0_line_144 |  | 129 | 170 | 0.038579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_668_0_line_145 |  | 131 | 132 | 0.003315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_668_0_line_146 |  | 133 | 134 | 0.058331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_668_0_line_147 |  | 136 | 137 | 0.14874 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
148 | MV_668_0_line_148 |  | 138 | 139 | 0.042141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_668_0_line_149 |  | 140 | 141 | 0.088873 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
150 | MV_668_0_line_150 |  | 144 | 145 | 0.12418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_668_0_line_151 |  | 144 | 146 | 0.29341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_668_0_line_152 |  | 146 | 147 | 0.036908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_668_0_line_153 |  | 148 | 149 | 0.0050835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_668_0_line_154 |  | 149 | 150 | 0.0087603 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
155 | MV_668_0_line_155 |  | 150 | 151 | 0.081891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_668_0_line_156 |  | 150 | 152 | 0.070881 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
157 | MV_668_0_line_157 |  | 152 | 153 | 0.13347 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
158 | MV_668_0_line_158 |  | 152 | 154 | 0.018544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_668_0_line_159 |  | 153 | 155 | 0.18701 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
160 | MV_668_0_line_160 |  | 153 | 156 | 0.033776 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_668_0_line_161 |  | 155 | 157 | 0.0712 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
162 | MV_668_0_line_162 |  | 155 | 158 | 0.026201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_668_0_line_163 |  | 157 | 159 | 0.15283 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
164 | MV_668_0_line_164 |  | 157 | 160 | 0.0275 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_668_0_line_165 |  | 158 | 161 | 0.093307 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
166 | MV_668_0_line_166 |  | 164 | 165 | 0.006155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_668_0_line_167 |  | 166 | 167 | 0.059354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_668_0_line_168 |  | 166 | 168 | 0.077869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_668_0_line_169 |  | 168 | 169 | 0.004485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_668_0_trafo_94 | 25 MVA 110/20 kV | 171 | 155 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2494563.3041 | 1120463.909
1 | 2494559.3745 | 1120465.1227
2 | 2494543.9475 | 1120636.5903
3 | 2494678.6395 | 1120623.2345
4 | 2494692.0121 | 1120672.9677
5 | 2494800.9397 | 1120626.7191
6 | 2494820.2023 | 1120618.9124
7 | 2494806.4264 | 1120640.488
8 | 2494266.6765 | 1120782.2362
9 | 2494533.2933 | 1120647.7499
10 | 2494197.8683 | 1120370.2868
11 | 2494235.1351 | 1120344.4851
12 | 2494160.7914 | 1120518.3971
13 | 2494236.4291 | 1120609.3544
14 | 2494700.2832 | 1120717.9959
15 | 2494826.7848 | 1120632.2509
16 | 2494948.8076 | 1120697.038
17 | 2494250.95 | 1120789.2156
18 | 2494248.2252 | 1120618.0648
19 | 2494147.1921 | 1120553.4109
20 | 2495334.581 | 1121505.1972
21 | 2495345.8279 | 1121489.07
22 | 2495368.6632 | 1121283.5883
23 | 2495115.7558 | 1121610.3116
24 | 2495100.1731 | 1121395.2892
25 | 2495005.1544 | 1121519.6956
26 | 2495076.662 | 1121373.3498
27 | 2495293.6621 | 1121711.8706
28 | 2495330.5591 | 1121668.688
29 | 2495590.7725 | 1121085.4007
30 | 2495332.3223 | 1121249.3726
31 | 2494990.0331 | 1121520.1473
32 | 2495140.33 | 1121637.1136
33 | 2495869.1441 | 1121528.3599
34 | 2495821.3441 | 1121660.9232
35 | 2495596.4722 | 1121085.28
36 | 2495312.5527 | 1121230.7592
37 | 2494987.1044 | 1121625.5321
38 | 2495132.5247 | 1121682.5779
39 | 2495153.6554 | 1120943.0843
40 | 2495161.5422 | 1120951.1638
41 | 2495136.9147 | 1120964.1214
42 | 2495395.1903 | 1121092.4854
43 | 2495393.0104 | 1120938.9141
44 | 2494934.0823 | 1121174.3875
45 | 2495450.7976 | 1121138.0527
46 | 2495449.0254 | 1120810.3969
47 | 2495427.4426 | 1120967.5473
48 | 2495404.533 | 1120263.6401
49 | 2495451.7054 | 1120806.9817
50 | 2495107.7775 | 1120522.9674
51 | 2495103.271 | 1120519.3989
52 | 2495208.2386 | 1120604.122
53 | 2495552.3722 | 1120329.5492
54 | 2495403.2501 | 1120259.5152
55 | 2495498.6788 | 1120026.8395
56 | 2495595.6482 | 1120333.6712
57 | 2495511.4667 | 1120388.4913
58 | 2495107.4745 | 1121182.5491
59 | 2494945.964 | 1121185.9217
60 | 2495130.8584 | 1121157.1162
61 | 2495168.7211 | 1120661.3323
62 | 2495264.6435 | 1120652.8575
63 | 2495460.8692 | 1120007.5716
64 | 2495098.0879 | 1120526.1931
65 | 2495385.2264 | 1120254.7461
66 | 2495665.025 | 1120518.1469
67 | 2495630.2322 | 1120523.4951
68 | 2495625.1189 | 1120217.5775
69 | 2495590.629 | 1120231.9932
70 | 2495599.5009 | 1120302.5293
71 | 2495155.4038 | 1120232.9727
72 | 2495232.4415 | 1120316.4081
73 | 2495227.1094 | 1120327.5409
74 | 2495290.921 | 1120188.3358
75 | 2495144.9373 | 1120302.8654
76 | 2495353.2832 | 1120194.338
77 | 2495270.1763 | 1120164.9619
78 | 2495336.9826 | 1120174.683
79 | 2495117.6748 | 1120271.1351
80 | 2495264.5946 | 1120158.6728
81 | 2494708.4846 | 1120044.7005
82 | 2494696.716 | 1120022.9804
83 | 2494696.2675 | 1120012.2925
84 | 2494665.8137 | 1120031.1793
85 | 2494665.6617 | 1120007.4001
86 | 2494828.804 | 1120052.0895
87 | 2494762.6157 | 1119959.0749
88 | 2494602.2661 | 1120059.2508
89 | 2494658.6521 | 1119995.4809
90 | 2495075.528 | 1119738.6596
91 | 2494845.9341 | 1120054.2263
92 | 2494778.1256 | 1120126.1804
93 | 2495072.7853 | 1119732.7034
94 | 2495340.5981 | 1119747.4059
95 | 2495356.3442 | 1119755.1495
96 | 2495295.7935 | 1119697.6846
97 | 2495483.3567 | 1119675.3803
98 | 2495480.6077 | 1119690.9043
99 | 2495595.4574 | 1119489.8704
100 | 2495403.0238 | 1119797.3743
101 | 2495570.5313 | 1119494.7183
102 | 2495193.4289 | 1119519.0197
103 | 2494853.386 | 1120050.083
104 | 2494875.8163 | 1120107.7338
105 | 2494757.765 | 1120155.9472
106 | 2495756.2415 | 1119667.7549
107 | 2495767.6469 | 1119683.813
108 | 2495736.9952 | 1119686.5875
109 | 2495200.4627 | 1119525.2703
110 | 2494981.3188 | 1119439.9149
111 | 2495282.0094 | 1119615.1467
112 | 2495597.2046 | 1119726.8579
113 | 2495042.89 | 1120778.3674
114 | 2495207.6351 | 1120712.5481
115 | 2495075.7905 | 1120738.4608
116 | 2495447.4796 | 1119996.9308
117 | 2494492.0847 | 1120221.8406
118 | 2494605.1479 | 1120321.7443
119 | 2494370.6776 | 1120080.525
120 | 2494268.3951 | 1119981.9824
121 | 2494415.2768 | 1120062.1066
122 | 2494214.006 | 1119934.8255
123 | 2494368.2767 | 1120042.0534
124 | 2494375.3476 | 1119937.8832
125 | 2494247.8064 | 1119920.7563
126 | 2494801.6362 | 1120217.212
127 | 2494735.5268 | 1120186.7247
128 | 2494425.032 | 1120034.0686
129 | 2494459.0524 | 1120044.0284
130 | 2494818.6176 | 1120238.28
131 | 2495166.3654 | 1121715.2452
132 | 2495163.0423 | 1121715.3585
133 | 2495048.4859 | 1121714.4786
134 | 2495036.7974 | 1121763.7352
135 | 2494967.1064 | 1119440.5621
136 | 2494765.9173 | 1119266.5033
137 | 2494617.3636 | 1119259.0071
138 | 2495670.5919 | 1119749.8729
139 | 2495643.5632 | 1119734.0624
140 | 2495801.4725 | 1119744.6661
141 | 2495749.1215 | 1119816.4834
142 | 2495566.3521 | 1119498.4011
143 | 2495250.2561 | 1120141.5514
144 | 2495058.1198 | 1120087.2397
145 | 2495014.7209 | 1119974.3566
146 | 2495272.1446 | 1120096.5024
147 | 2495295.7052 | 1120124.9113
148 | 2494901.2919 | 1120153.3503
149 | 2494898.8131 | 1120148.9121
150 | 2494906.4872 | 1120144.6872
151 | 2494968.3883 | 1120137.3359
152 | 2494937.4555 | 1120194.4587
153 | 2494997.1912 | 1120279.7757
154 | 2494948.219 | 1120209.5588
155 | 2494940.209 | 1120408.3474
156 | 2495024.4755 | 1120259.8665
157 | 2494991.0231 | 1120427.9663
158 | 2494919.9735 | 1120424.9909
159 | 2495008.2252 | 1120487.1721
160 | 2495012.2298 | 1120410.4577
161 | 2494892.4788 | 1120514.1555
162 | 2494873.0895 | 1120085.1863
163 | 2494943.2012 | 1120723.8525
164 | 2494722.6396 | 1120886.9258
165 | 2494717.925 | 1120890.8993
166 | 2495420.4195 | 1119975.4261
167 | 2495380.6153 | 1120019.5537
168 | 2495391.3364 | 1119941.6631
169 | 2495389.0184 | 1119945.5056
170 | 2494494.7103 | 1120029.3026
171 | 2494940.209 | 1120408.3474

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99541 | 0.023856 | 0.29421 | 0.14249
1 | 0.99541 | 0.023841 | 0 | 0
2 | 0.99551 | 0.022984 | 0 | 0
3 | 0.99545 | 0.023467 | 0 | 0
4 | 0.99543 | 0.023647 | 0.082827 | 0.040115
5 | 0.99675 | 0.011885 | 0 | 0
6 | 0.99675 | 0.01191 | 0.1015 | 0.049158
7 | 0.99681 | 0.011347 | 0 | 0
8 | 0.99423 | 0.014611 | 0 | 0
9 | 0.9955 | 0.022909 | 0.39804 | 0.19278
10 | 0.99245 | 0.019087 | 0 | 0
11 | 0.99241 | 0.018868 | 0.39493 | 0.19127
12 | 0.99208 | 0.016736 | 0 | 0
13 | 0.99322 | 0.02399 | 0.14236 | 0.068948
14 | 0.99541 | 0.023766 | 0 | 0
15 | 0.99681 | 0.011372 | 0.096873 | 0.046918
16 | 0.99758 | 0.0046159 | 0 | 0
17 | 0.99422 | 0.014676 | 0.31231 | 0.15126
18 | 0.99326 | 0.023665 | 0 | 0
19 | 0.992 | 0.017463 | 1.2459 | 0.60343
20 | 0.9873 | 0.034185 | 0.35019 | 0.1696
21 | 0.98731 | 0.0341 | 0 | 0
22 | 0.98795 | 0.02882 | 0 | 0
23 | 0.98676 | 0.038599 | 0 | 0
24 | 0.98617 | 0.040198 | 0 | 0
25 | 0.98622 | 0.039726 | 0 | 0
26 | 0.98615 | 0.040113 | 0.21097 | 0.10218
27 | 0.98673 | 0.038787 | 0 | 0
28 | 0.98672 | 0.038837 | 0.074573 | 0.036117
29 | 0.98771 | 0.030122 | 0 | 0
30 | 0.98806 | 0.027992 | 0.099564 | 0.048221
31 | 0.98622 | 0.039691 | 0.32513 | 0.15747
32 | 0.98671 | 0.039012 | 0.11068 | 0.053603
33 | 0.98753 | 0.031163 | 0 | 0
34 | 0.98749 | 0.031542 | 0.17794 | 0.086178
35 | 0.98771 | 0.030134 | 0.17776 | 0.086091
36 | 0.98813 | 0.027511 | 0 | 0
37 | 0.98633 | 0.040439 | 0 | 0
38 | 0.98666 | 0.039493 | 0 | 0
39 | 0.99121 | 0.0051298 | 0.3995 | 0.19349
40 | 0.99125 | 0.0048277 | 0 | 0
41 | 0.99113 | 0.005702 | 0 | 0
42 | 0.99118 | 0.0054641 | 0 | 0
43 | 0.99248 | -0.0042849 | 0 | 0
44 | 0.99017 | 0.012729 | 0 | 0
45 | 0.99115 | 0.0053 | 0.1853 | 0.089747
46 | 0.9932 | -0.0097134 | 0 | 0
47 | 0.99246 | -0.0041784 | 0.19863 | 0.096202
48 | 0.99648 | -0.034136 | 0 | 0
49 | 0.9932 | -0.0096958 | 0.33502 | 0.16226
50 | 0.99877 | -0.0062695 | 0 | 0
51 | 0.99878 | -0.0062008 | 0.17464 | 0.084584
52 | 0.99871 | -0.0059252 | 0 | 0
53 | 0.99605 | -0.030837 | 0 | 0
54 | 0.99647 | -0.034052 | 0.37196 | 0.18015
55 | 0.99552 | -0.026189 | 0 | 0
56 | 0.99602 | -0.03069 | 0 | 0
57 | 0.99604 | -0.030778 | 0.073378 | 0.035538
58 | 0.98947 | 0.017836 | 0 | 0
59 | 0.99016 | 0.012762 | 0.1665 | 0.080638
60 | 0.98945 | 0.017956 | 0.28706 | 0.13903
61 | 0.9987 | -0.0058354 | 0 | 0
62 | 0.9987 | -0.0058596 | 0.077897 | 0.037727
63 | 0.99547 | -0.025771 | 0.22294 | 0.10798
64 | 0.9988 | -0.0060968 | 0 | 0
65 | 0.99642 | -0.033673 | 0 | 0
66 | 0.99594 | -0.030227 | 0 | 0
67 | 0.99594 | -0.030187 | 0.094071 | 0.045561
68 | 0.99587 | -0.029736 | 0 | 0
69 | 0.99586 | -0.029684 | 0.11879 | 0.057535
70 | 0.99602 | -0.03065 | 0.10641 | 0.051538
71 | 0.99575 | -0.028002 | 0.3047 | 0.14757
72 | 0.9958 | -0.028409 | 0 | 0
73 | 0.99579 | -0.028356 | 0 | 0
74 | 0.99596 | -0.029796 | 0 | 0
75 | 0.99574 | -0.027838 | 0.11738 | 0.056848
76 | 0.99617 | -0.031565 | 0 | 0
77 | 0.99593 | -0.029578 | 0.12364 | 0.05988
78 | 0.99616 | -0.031541 | 0.078247 | 0.037897
79 | 0.99572 | -0.027708 | 0.26108 | 0.12645
80 | 0.99592 | -0.029531 | 0 | 0
81 | 0.99826 | -0.0056909 | 0.25463 | 0.12332
82 | 0.99827 | -0.0056145 | 0 | 0
83 | 0.99828 | -0.0056889 | 0 | 0
84 | 0.99827 | -0.0055642 | 0 | 0
85 | 0.99827 | -0.0055617 | 0 | 0
86 | 0.99847 | -0.007306 | 0 | 0
87 | 0.99827 | -0.0055996 | 0.092748 | 0.04492
88 | 0.99826 | -0.0054714 | 0.11526 | 0.055823
89 | 0.99826 | -0.0055452 | 0.099812 | 0.048341
90 | 0.99571 | 0.015159 | 0 | 0
91 | 0.99854 | -0.0065203 | 0 | 0
92 | 0.99816 | -0.0046842 | 1.2664 | 0.61335
93 | 0.99571 | 0.015166 | 0.095477 | 0.046242
94 | 0.99348 | 0.033904 | 0 | 0
95 | 0.99341 | 0.034462 | 0 | 0
96 | 0.99343 | 0.03433 | 0.20886 | 0.10116
97 | 0.99296 | 0.038147 | 0 | 0
98 | 0.99294 | 0.038352 | 0.16816 | 0.081442
99 | 0.99247 | 0.041909 | 0 | 0
100 | 0.99337 | 0.034833 | 0.49088 | 0.23775
101 | 0.99246 | 0.041986 | 0.11342 | 0.054933
102 | 0.99163 | 0.048618 | 0 | 0
103 | 0.99854 | -0.0065116 | 0 | 0
104 | 0.99867 | -0.0059176 | 0.96129 | 0.46557
105 | 0.9981 | -0.0041755 | 0 | 0
106 | 0.99258 | 0.037335 | 0 | 0
107 | 0.99257 | 0.037413 | 0 | 0
108 | 0.99259 | 0.037229 | 0.27142 | 0.13146
109 | 0.99163 | 0.048655 | 0.32267 | 0.15628
110 | 0.99141 | 0.050415 | 0 | 0
111 | 0.99338 | 0.034001 | 0.32075 | 0.15535
112 | 0.99277 | 0.037267 | 0.080149 | 0.038818
113 | 0.99867 | -0.0056777 | 0 | 0
114 | 0.99869 | -0.0057635 | 0.082014 | 0.039721
115 | 0.99867 | -0.0056367 | 0.069288 | 0.033558
116 | 0.99546 | -0.025649 | 0.099584 | 0.048231
117 | 0.9977 | -0.0017269 | 0.16826 | 0.08149
118 | 0.99775 | -0.0014176 | 0 | 0
119 | 0.99718 | 0.003185 | 0 | 0
120 | 0.99707 | 0.0040542 | 0 | 0
121 | 0.99715 | 0.0034441 | 0.2301 | 0.11144
122 | 0.99704 | 0.0042853 | 0 | 0
123 | 0.99701 | 0.0045736 | 0 | 0
124 | 0.99705 | 0.0042192 | 0.1258 | 0.06093
125 | 0.99704 | 0.0043632 | 0.17904 | 0.086715
126 | 0.99808 | -0.0040378 | 0 | 0
127 | 0.99809 | -0.0041243 | 0.11478 | 0.055591
128 | 0.99699 | 0.0047233 | 0.19219 | 0.093081
129 | 0.99714 | 0.0035707 | 0.11581 | 0.056088
130 | 0.99808 | -0.0039859 | 0.16002 | 0.077502
131 | 0.98664 | 0.039684 | 0.20678 | 0.10015
132 | 0.98664 | 0.039675 | 0 | 0
133 | 0.98654 | 0.038644 | 0.14011 | 0.067859
134 | 0.9865 | 0.038986 | 0 | 0
135 | 0.99141 | 0.050479 | 0.37423 | 0.18125
136 | 0.99121 | 0.052053 | 0 | 0
137 | 0.99114 | 0.051566 | 0.2658 | 0.12873
138 | 0.9927 | 0.037936 | 0 | 0
139 | 0.99273 | 0.037635 | 0 | 0
140 | 0.99254 | 0.037694 | 0.1306 | 0.063253
141 | 0.9925 | 0.037469 | 0.20618 | 0.099856
142 | 0.99246 | 0.041991 | 0.081585 | 0.039513
143 | 0.99591 | -0.029455 | 0.28394 | 0.13752
144 | 0.99583 | -0.028906 | 0 | 0
145 | 0.99581 | -0.028734 | 0.12319 | 0.059662
146 | 0.99578 | -0.02847 | 0 | 0
147 | 0.99577 | -0.028405 | 0.14659 | 0.070995
148 | 0.99877 | -0.0053081 | 1.4858 | 0.71959
149 | 0.99878 | -0.0053987 | 0 | 0
150 | 0.9988 | -0.0052869 | 0 | 0
151 | 0.99879 | -0.0051961 | 0.097689 | 0.047313
152 | 0.99901 | -0.00437 | 0 | 0
153 | 0.99941 | -0.0026149 | 0 | 0
154 | 0.99901 | -0.0043473 | 0.10322 | 0.049991
155 | 1 | 0 | -20.8122 | -9.5435
156 | 0.99938 | -0.0023774 | 0.58913 | 0.28533
157 | 0.99976 | -0.0012439 | 0 | 0
158 | 0.99998 | 0.0001538 | 0.22883 | 0.11083
159 | 0.99924 | -0.0038805 | 0 | 0
160 | 0.99975 | -0.0012113 | 0.10072 | 0.048781
161 | 0.99994 | -0.00014438 | 0.26404 | 0.12788
162 | 0.99853 | -0.0064692 | 0.090379 | 0.043772
163 | 0.99757 | 0.0047064 | 0.20456 | 0.099071
164 | 0.99534 | 0.024411 | 0 | 0
165 | 0.99534 | 0.024429 | 0.2438 | 0.11808
166 | 0.99544 | -0.025442 | 0 | 0
167 | 0.99543 | -0.025338 | 0.14892 | 0.072123
168 | 0.9954 | -0.025102 | 0 | 0
169 | 0.9954 | -0.025082 | 0.36711 | 0.1778
170 | 0.99713 | 0.0036226 | 0.11424 | 0.055327
171 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.29421 | -0.14249 | 0.29421 | 0.14239 | 4.9211e-07 | -9.6897e-05 | 0.0094802 | 0.009479 | 0.0094802 | 0.99541 | 0.023856 | 0.99541 | 0.023841 | 4.3092
1 | -0.29421 | -0.14239 | 0.29424 | 0.13635 | 3.0448e-05 | -0.006045 | 0.009479 | 0.0094039 | 0.009479 | 0.99541 | 0.023841 | 0.99551 | 0.022984 | 4.3086
2 | 2.1018 | 1.0053 | -2.0993 | -1.0041 | 0.0025473 | 0.0012255 | 0.067561 | 0.067566 | 0.067566 | 0.99551 | 0.022984 | 0.99423 | 0.014611 | 32.1741
3 | 0.39805 | 0.19276 | -0.39804 | -0.19278 | 4.5214e-06 | -1.5422e-05 | 0.012825 | 0.012825 | 0.012825 | 0.99551 | 0.022984 | 0.9955 | 0.022909 | 6.1071
4 | 0.32668 | 0.14675 | -0.32666 | -0.15019 | 2.1051e-05 | -0.0034396 | 0.010385 | 0.010426 | 0.010426 | 0.99551 | 0.022984 | 0.99545 | 0.023467 | 4.7391
5 | -3.1208 | -1.4812 | 3.125 | 1.475 | 0.0041907 | -0.0061755 | 0.10017 | 0.10008 | 0.10017 | 0.99551 | 0.022984 | 0.99675 | 0.011885 | 45.5323
6 | 0.32666 | 0.15019 | -0.32665 | -0.15141 | 7.5612e-06 | -0.0012287 | 0.010426 | 0.010441 | 0.010441 | 0.99545 | 0.023467 | 0.99543 | 0.023647 | 4.7459
7 | 0.24382 | 0.1113 | -0.24382 | -0.1124 | 3.7657e-06 | -0.0011016 | 0.0077727 | 0.007786 | 0.007786 | 0.99543 | 0.023647 | 0.99541 | 0.023766 | 3.5391
8 | 0.1015 | 0.048666 | -0.1015 | -0.049158 | 2.947e-07 | -0.0004917 | 0.00326 | 0.0032662 | 0.0032662 | 0.99675 | 0.011885 | 0.99675 | 0.01191 | 1.4846
9 | -3.2265 | -1.5237 | 3.2267 | 1.5234 | 0.00021127 | -0.0002889 | 0.10334 | 0.10333 | 0.10334 | 0.99675 | 0.011885 | 0.99681 | 0.011347 | 46.9723
10 | 0.096873 | 0.046398 | -0.096873 | -0.046918 | 2.8356e-07 | -0.00051962 | 0.0031106 | 0.0031171 | 0.0031171 | 0.99681 | 0.011347 | 0.99681 | 0.011372 | 1.4169
11 | -3.3236 | -1.5698 | 3.3263 | 1.5663 | 0.0027288 | -0.0034759 | 0.10645 | 0.10639 | 0.10645 | 0.99681 | 0.011347 | 0.99758 | 0.0046159 | 48.3842
12 | 0.31232 | 0.15086 | -0.31231 | -0.15126 | 2.3249e-06 | -0.00040438 | 0.010071 | 0.010076 | 0.010076 | 0.99423 | 0.014611 | 0.99422 | 0.014676 | 4.5799
13 | 1.787 | 0.85323 | -1.7851 | -0.86275 | 0.0018901 | -0.0095155 | 0.057495 | 0.057622 | 0.057622 | 0.99423 | 0.014611 | 0.99326 | 0.023665 | 26.1918
14 | 0.39494 | 0.19123 | -0.39493 | -0.19127 | 1.3157e-05 | -4.5054e-05 | 0.012764 | 0.012764 | 0.012764 | 0.99245 | 0.019087 | 0.99241 | 0.018868 | 6.0782
15 | 1.2465 | 0.60243 | -1.246 | -0.60233 | 0.00044115 | 9.6861e-05 | 0.040269 | 0.040271 | 0.040271 | 0.99245 | 0.019087 | 0.99208 | 0.016736 | 19.1768
16 | -1.6414 | -0.79366 | 1.6426 | 0.79413 | 0.0012134 | 0.00047505 | 0.053033 | 0.053029 | 0.053033 | 0.99245 | 0.019087 | 0.99322 | 0.02399 | 25.2536
17 | 1.246 | 0.60233 | -1.2459 | -0.60343 | 0.00010421 | -0.0010996 | 0.040271 | 0.040286 | 0.040286 | 0.99208 | 0.016736 | 0.992 | 0.017463 | 18.3117
18 | -1.785 | -0.86308 | 1.7851 | 0.86275 | 6.7004e-05 | -0.00033615 | 0.057626 | 0.057622 | 0.057626 | 0.99322 | 0.02399 | 0.99326 | 0.023665 | 26.1938
19 | 0.24382 | 0.1124 | -0.2438 | -0.11793 | 1.9103e-05 | -0.0055297 | 0.007786 | 0.0078546 | 0.0078546 | 0.99541 | 0.023766 | 0.99534 | 0.024411 | 3.5703
20 | 0.20456 | 0.098186 | -0.20456 | -0.099071 | 2.1472e-06 | -0.00088429 | 0.006566 | 0.0065771 | 0.0065771 | 0.99758 | 0.0046159 | 0.99757 | 0.0047064 | 2.9896
21 | -3.5308 | -1.6645 | 3.5355 | 1.6594 | 0.0046432 | -0.005112 | 0.11296 | 0.11288 | 0.11296 | 0.99758 | 0.0046159 | 0.9988 | -0.0060968 | 51.3446
22 | -0.35019 | -0.1696 | 0.35019 | 0.16915 | 3.4041e-06 | -0.00045774 | 0.011377 | 0.011371 | 0.011377 | 0.9873 | 0.034185 | 0.98731 | 0.0341 | 5.1713
23 | -1.4194 | -0.65293 | 1.4204 | 0.64496 | 0.00098622 | -0.0079696 | 0.045683 | 0.045582 | 0.045683 | 0.98731 | 0.0341 | 0.98795 | 0.02882 | 20.7649
24 | 1.0693 | 0.48379 | -1.0686 | -0.49294 | 0.00063311 | -0.0091498 | 0.034315 | 0.034428 | 0.034428 | 0.98731 | 0.0341 | 0.98676 | 0.038599 | 15.6491
25 | 0.35582 | 0.13645 | -0.35573 | -0.14892 | 8.9859e-05 | -0.012471 | 0.011135 | 0.011271 | 0.011271 | 0.98795 | 0.02882 | 0.98771 | 0.030122 | 5.1232
26 | -1.7763 | -0.78141 | 1.7765 | 0.78031 | 0.00021418 | -0.0010998 | 0.056702 | 0.056688 | 0.056702 | 0.98795 | 0.02882 | 0.98806 | 0.027992 | 25.7734
27 | 0.99404 | 0.46564 | -0.99399 | -0.46648 | 5.0755e-05 | -0.0008417 | 0.032113 | 0.032124 | 0.032124 | 0.98676 | 0.038599 | 0.98671 | 0.039012 | 14.6017
28 | 0.074575 | 0.027296 | -0.074573 | -0.034797 | 2.4059e-06 | -0.007501 | 0.0023232 | 0.0024075 | 0.0024075 | 0.98676 | 0.038599 | 0.98673 | 0.038787 | 1.0943
29 | -0.21097 | -0.10214 | 0.21098 | 0.097664 | 1.2027e-05 | -0.0044771 | 0.0068614 | 0.0068052 | 0.0068614 | 0.98617 | 0.040198 | 0.98622 | 0.039726 | 3.1188
30 | 0.21097 | 0.10214 | -0.21097 | -0.10218 | 2.6975e-06 | -3.5645e-05 | 0.0068614 | 0.0068618 | 0.0068618 | 0.98617 | 0.040198 | 0.98615 | 0.040113 | 3.2675
31 | -0.21098 | -0.097664 | 0.21098 | 0.097314 | 9.3193e-07 | -0.00034999 | 0.0068052 | 0.0068009 | 0.0068052 | 0.98622 | 0.039726 | 0.98622 | 0.039691 | 3.0933
32 | 0.074573 | 0.034797 | -0.074573 | -0.036117 | 4.4251e-07 | -0.0013202 | 0.0024075 | 0.0024241 | 0.0024241 | 0.98673 | 0.038787 | 0.98672 | 0.038837 | 1.1019
33 | 0.17776 | 0.085959 | -0.17776 | -0.086091 | 2.528e-07 | -0.00013232 | 0.0057708 | 0.0057725 | 0.0057725 | 0.98771 | 0.030122 | 0.98771 | 0.030134 | 2.6238
34 | 0.17798 | 0.062957 | -0.17794 | -0.081859 | 3.419e-05 | -0.018902 | 0.0055176 | 0.0057257 | 0.0057257 | 0.98771 | 0.030122 | 0.98753 | 0.031163 | 2.6026
35 | -1.876 | -0.82853 | 1.8762 | 0.82794 | 0.00013013 | -0.00059437 | 0.059918 | 0.05991 | 0.059918 | 0.98806 | 0.027992 | 0.98813 | 0.027511 | 27.2354
36 | -0.53611 | -0.25478 | 0.53617 | 0.25469 | 5.6696e-05 | -8.6914e-05 | 0.017374 | 0.017373 | 0.017374 | 0.98622 | 0.039691 | 0.98633 | 0.040439 | 8.2735
37 | 0.88332 | 0.41288 | -0.88326 | -0.41399 | 5.2717e-05 | -0.0011118 | 0.028526 | 0.02854 | 0.02854 | 0.98671 | 0.039012 | 0.98666 | 0.039493 | 12.9728
38 | 0.17794 | 0.081859 | -0.17794 | -0.086178 | 8.1989e-06 | -0.004319 | 0.0057257 | 0.0057796 | 0.0057796 | 0.98753 | 0.031163 | 0.98749 | 0.031542 | 2.6271
39 | -1.8762 | -0.82794 | 1.8788 | 0.81565 | 0.0026777 | -0.012285 | 0.05991 | 0.059757 | 0.05991 | 0.98813 | 0.027511 | 0.98947 | 0.017836 | 27.232
40 | -0.53617 | -0.25469 | 0.53626 | 0.24917 | 9.5842e-05 | -0.0055198 | 0.017373 | 0.017304 | 0.017373 | 0.98633 | 0.040439 | 0.9865 | 0.038986 | 7.8967
41 | 0.67647 | 0.31563 | -0.6764 | -0.31568 | 7.6401e-05 | -5.6598e-05 | 0.021841 | 0.021842 | 0.021842 | 0.98666 | 0.039493 | 0.98654 | 0.038644 | 10.4009
42 | 0.20679 | 0.098364 | -0.20678 | -0.10007 | 4.4235e-06 | -0.0017089 | 0.0066998 | 0.0067215 | 0.0067215 | 0.98666 | 0.039493 | 0.98664 | 0.039675 | 3.0552
43 | -2.7361 | -1.2147 | 2.7362 | 1.2144 | 0.0001173 | -0.00023639 | 0.087184 | 0.087181 | 0.087184 | 0.99121 | 0.0051298 | 0.99125 | 0.0048277 | 39.6293
44 | 2.3366 | 1.0212 | -2.3364 | -1.0217 | 0.00019777 | -0.00057133 | 0.074265 | 0.074273 | 0.074273 | 0.99121 | 0.0051298 | 0.99113 | 0.005702 | 33.7603
45 | 0.18532 | 0.082243 | -0.18531 | -0.089666 | 1.4961e-05 | -0.007423 | 0.0059046 | 0.0059957 | 0.0059957 | 0.99125 | 0.0048277 | 0.99118 | 0.0054641 | 2.7253
46 | -2.9216 | -1.2967 | 2.9254 | 1.29 | 0.0038138 | -0.0066205 | 0.093086 | 0.092995 | 0.093086 | 0.99125 | 0.0048277 | 0.99248 | -0.0042849 | 42.3118
47 | 2.3364 | 1.0217 | -2.334 | -1.0287 | 0.0023991 | -0.0069125 | 0.074273 | 0.074362 | 0.074362 | 0.99113 | 0.005702 | 0.99017 | 0.012729 | 33.8009
48 | 0.18531 | 0.089666 | -0.1853 | -0.089747 | 4.6054e-06 | -8.1431e-05 | 0.0059957 | 0.0059967 | 0.0059967 | 0.99118 | 0.0054641 | 0.99115 | 0.0053 | 2.8556
49 | -3.124 | -1.3852 | 3.1264 | 1.3816 | 0.0024251 | -0.0036101 | 0.099398 | 0.099347 | 0.099398 | 0.99248 | -0.0042849 | 0.9932 | -0.0097134 | 45.1809
50 | 0.19863 | 0.095149 | -0.19863 | -0.096202 | 2.4586e-06 | -0.0010524 | 0.0064062 | 0.0064195 | 0.0064195 | 0.99248 | -0.0042849 | 0.99246 | -0.0041784 | 2.918
51 | 2.1675 | 0.9484 | -2.1659 | -0.95388 | 0.001618 | -0.0054731 | 0.068977 | 0.069047 | 0.069047 | 0.99017 | 0.012729 | 0.98947 | 0.017836 | 31.3848
52 | 0.1665 | 0.080251 | -0.1665 | -0.080638 | 6.4161e-07 | -0.00038692 | 0.0053885 | 0.0053934 | 0.0053934 | 0.99017 | 0.012729 | 0.99016 | 0.012762 | 2.4516
53 | -3.4615 | -1.5437 | 3.4735 | 1.5297 | 0.012066 | -0.014054 | 0.11016 | 0.10995 | 0.11016 | 0.9932 | -0.0097134 | 0.99648 | -0.034136 | 50.0723
54 | 0.33502 | 0.16216 | -0.33502 | -0.16226 | 6.7768e-07 | -0.00010195 | 0.010818 | 0.010819 | 0.010819 | 0.9932 | -0.0097134 | 0.9932 | -0.0096958 | 4.9179
55 | 1.2324 | 0.54816 | -1.2318 | -0.55454 | 0.00056437 | -0.0063814 | 0.039074 | 0.039151 | 0.039151 | 0.99648 | -0.034136 | 0.99605 | -0.030837 | 17.796
56 | 1.8117 | 0.84023 | -1.8117 | -0.84032 | 1.9304e-05 | -9.6692e-05 | 0.057854 | 0.057856 | 0.057856 | 0.99648 | -0.034136 | 0.99647 | -0.034052 | 26.298
57 | -6.5176 | -2.9181 | 6.5312 | 2.9055 | 0.01357 | -0.012582 | 0.20687 | 0.20661 | 0.20687 | 0.99648 | -0.034136 | 0.99877 | -0.0062695 | 57.1471
58 | -6.7604 | -2.9977 | 6.7605 | 2.9974 | 8.1017e-05 | -0.00031409 | 0.21374 | 0.21374 | 0.21374 | 0.99877 | -0.0062695 | 0.99878 | -0.0062008 | 33.5022
59 | 0.22922 | 0.092193 | -0.22921 | -0.097011 | 1.3885e-05 | -0.004818 | 0.0071409 | 0.0071941 | 0.0071941 | 0.99877 | -0.0062695 | 0.99871 | -0.0059252 | 3.2701
60 | -6.9351 | -3.0819 | 6.9353 | 3.0815 | 0.00012691 | -0.00046363 | 0.21935 | 0.21934 | 0.21935 | 0.99878 | -0.0062008 | 0.9988 | -0.0060968 | 34.3802
61 | 0.15131 | 0.061064 | -0.15131 | -0.063013 | 2.4421e-06 | -0.001949 | 0.0047163 | 0.0047376 | 0.0047376 | 0.99871 | -0.0059252 | 0.9987 | -0.0058354 | 2.1535
62 | 0.077898 | 0.035947 | -0.077897 | -0.037727 | 6.1914e-07 | -0.0017802 | 0.0024798 | 0.0025018 | 0.0025018 | 0.99871 | -0.0059252 | 0.9987 | -0.0058596 | 1.1372
63 | 0.83911 | 0.38898 | -0.83864 | -0.40057 | 0.00047782 | -0.011589 | 0.026805 | 0.02695 | 0.02695 | 0.99605 | -0.030837 | 0.99552 | -0.026189 | 12.25
64 | 0.31931 | 0.13171 | -0.31931 | -0.13315 | 8.129e-06 | -0.0014345 | 0.010011 | 0.010027 | 0.010027 | 0.99605 | -0.030837 | 0.99602 | -0.03069 | 4.5576
65 | 0.073378 | 0.033839 | -0.073378 | -0.035538 | 5.2999e-07 | -0.0016993 | 0.0023419 | 0.0023629 | 0.0023629 | 0.99605 | -0.030837 | 0.99604 | -0.030778 | 1.0741
66 | 1.4397 | 0.66017 | -1.4397 | -0.66075 | 7.1117e-05 | -0.00057864 | 0.045885 | 0.045892 | 0.045892 | 0.99647 | -0.034052 | 0.99642 | -0.033673 | 20.8601
67 | 0.83864 | 0.40057 | -0.83859 | -0.40157 | 4.1344e-05 | -0.00099618 | 0.02695 | 0.026963 | 0.026963 | 0.99552 | -0.026189 | 0.99547 | -0.025771 | 12.2557
68 | 0.10641 | 0.050779 | -0.10641 | -0.051538 | 5.0073e-07 | -0.00075852 | 0.0034173 | 0.0034268 | 0.0034268 | 0.99602 | -0.03069 | 0.99602 | -0.03065 | 1.5576
69 | 0.21289 | 0.08237 | -0.21288 | -0.089813 | 1.8598e-05 | -0.0074427 | 0.006616 | 0.0066969 | 0.0066969 | 0.99602 | -0.03069 | 0.99594 | -0.030227 | 3.0441
70 | 0.28707 | 0.13823 | -0.28706 | -0.13903 | 3.9847e-06 | -0.00080541 | 0.0092955 | 0.0093057 | 0.0093057 | 0.98947 | 0.017836 | 0.98945 | 0.017956 | 4.2299
71 | 0.069291 | 0.025145 | -0.069289 | -0.032326 | 1.893e-06 | -0.0071818 | 0.0021307 | 0.0022101 | 0.0022101 | 0.9987 | -0.0058354 | 0.99867 | -0.0056777 | 1.0046
72 | 0.082015 | 0.037868 | -0.082014 | -0.039721 | 7.1445e-07 | -0.0018528 | 0.0026112 | 0.0026341 | 0.0026341 | 0.9987 | -0.0058354 | 0.99869 | -0.0057635 | 1.1973
73 | 0.61565 | 0.29359 | -0.61564 | -0.29399 | 8.9348e-06 | -0.00040201 | 0.019779 | 0.019784 | 0.019784 | 0.99547 | -0.025771 | 0.99546 | -0.025649 | 8.9929
74 | -10.4707 | -4.7409 | 10.4751 | 4.7352 | 0.0044086 | -0.005627 | 0.3322 | 0.3321 | 0.3322 | 0.9988 | -0.0060968 | 0.99924 | -0.0038805 | 52.0692
75 | 1.4397 | 0.66075 | -1.4393 | -0.66394 | 0.00039249 | -0.003189 | 0.045892 | 0.045932 | 0.045932 | 0.99642 | -0.033673 | 0.99617 | -0.031565 | 20.8783
76 | 0.094071 | 0.044714 | -0.094071 | -0.045561 | 4.3637e-07 | -0.00084622 | 0.003019 | 0.0030296 | 0.0030296 | 0.99594 | -0.030227 | 0.99594 | -0.030187 | 1.3771
77 | 0.1188 | 0.045099 | -0.11879 | -0.05665 | 9.1399e-06 | -0.011551 | 0.0036833 | 0.003815 | 0.003815 | 0.99594 | -0.030227 | 0.99587 | -0.029736 | 1.7341
78 | 0.11879 | 0.05665 | -0.11879 | -0.057535 | 7.2844e-07 | -0.00088494 | 0.003815 | 0.0038262 | 0.0038262 | 0.99587 | -0.029736 | 0.99586 | -0.029684 | 1.7392
79 | -0.3047 | -0.14757 | 0.30471 | 0.14489 | 1.4554e-05 | -0.0026842 | 0.0098148 | 0.0097811 | 0.0098148 | 0.99575 | -0.028002 | 0.9958 | -0.028409 | 4.4613
80 | 0.37848 | 0.17924 | -0.37848 | -0.17953 | 2.4285e-06 | -0.00029141 | 0.01214 | 0.012144 | 0.012144 | 0.9958 | -0.028409 | 0.99579 | -0.028356 | 5.5199
81 | -0.68319 | -0.32413 | 0.68331 | 0.31988 | 0.00011574 | -0.004248 | 0.021921 | 0.021868 | 0.021921 | 0.9958 | -0.028409 | 0.99596 | -0.029796 | 9.9642
82 | 0.37848 | 0.17953 | -0.37846 | -0.1823 | 2.3177e-05 | -0.0027723 | 0.012144 | 0.012179 | 0.012179 | 0.99579 | -0.028356 | 0.99574 | -0.027838 | 5.5357
83 | -1.3607 | -0.62946 | 1.361 | 0.62665 | 0.00030903 | -0.0028145 | 0.043456 | 0.043421 | 0.043456 | 0.99596 | -0.029796 | 0.99617 | -0.031565 | 19.7526
84 | 0.67742 | 0.30958 | -0.6774 | -0.31032 | 1.9452e-05 | -0.00073436 | 0.021588 | 0.021597 | 0.021597 | 0.99596 | -0.029796 | 0.99593 | -0.029578 | 9.8168
85 | 0.26108 | 0.12546 | -0.26108 | -0.12645 | 3.9442e-06 | -0.00098914 | 0.0083976 | 0.0084101 | 0.0084101 | 0.99574 | -0.027838 | 0.99572 | -0.027708 | 3.8228
86 | 0.078247 | 0.037292 | -0.078247 | -0.037897 | 2.1573e-07 | -0.00060494 | 0.0025118 | 0.0025194 | 0.0025194 | 0.99617 | -0.031565 | 0.99616 | -0.031541 | 1.1452
87 | 0.55376 | 0.25044 | -0.55376 | -0.25064 | 3.4842e-06 | -0.0001981 | 0.017616 | 0.017619 | 0.017619 | 0.99593 | -0.029578 | 0.99592 | -0.029531 | 8.0084
88 | 0.26981 | 0.11365 | -0.26978 | -0.1199 | 2.5637e-05 | -0.0062544 | 0.0084861 | 0.0085582 | 0.0085582 | 0.99592 | -0.029531 | 0.99583 | -0.028906 | 3.8901
89 | 0.28395 | 0.13699 | -0.28394 | -0.13752 | 2.4914e-06 | -0.00052813 | 0.0091382 | 0.0091449 | 0.0091449 | 0.99592 | -0.029531 | 0.99591 | -0.029455 | 4.1568
90 | -0.25463 | -0.12332 | 0.25464 | 0.1233 | 2.9461e-06 | -2.7544e-05 | 0.0081816 | 0.0081812 | 0.0081816 | 0.99826 | -0.0056909 | 0.99827 | -0.0056145 | 3.896
91 | -0.46971 | -0.22341 | 0.46972 | 0.22308 | 4.18e-06 | -0.00032816 | 0.015041 | 0.015037 | 0.015041 | 0.99827 | -0.0056145 | 0.99828 | -0.0056889 | 6.8368
92 | 0.11526 | 0.053204 | -0.11526 | -0.054165 | 7.292e-07 | -0.00096108 | 0.0036711 | 0.0036828 | 0.0036828 | 0.99827 | -0.0056145 | 0.99827 | -0.0055642 | 1.674
93 | 0.099813 | 0.04691 | -0.099813 | -0.048011 | 6.3138e-07 | -0.0011015 | 0.0031892 | 0.0032029 | 0.0032029 | 0.99827 | -0.0056145 | 0.99827 | -0.0055617 | 1.4559
94 | -0.56247 | -0.26598 | 0.56258 | 0.25974 | 0.00011335 | -0.0062353 | 0.017992 | 0.017915 | 0.017992 | 0.99828 | -0.0056889 | 0.99847 | -0.007306 | 8.1781
95 | 0.092749 | 0.042894 | -0.092748 | -0.04492 | 1.001e-06 | -0.0020258 | 0.002955 | 0.00298 | 0.00298 | 0.99828 | -0.0056889 | 0.99827 | -0.0055996 | 1.3546
96 | 0.11526 | 0.054165 | -0.11526 | -0.055823 | 1.2696e-06 | -0.0016586 | 0.0036828 | 0.0037035 | 0.0037035 | 0.99827 | -0.0055642 | 0.99826 | -0.0054714 | 1.6834
97 | 0.099813 | 0.048011 | -0.099812 | -0.048341 | 1.9035e-07 | -0.00033023 | 0.0032029 | 0.0032071 | 0.0032071 | 0.99827 | -0.0055617 | 0.99826 | -0.0055452 | 1.4578
98 | 3.1499 | 1.4325 | -3.1407 | -1.4462 | 0.0092643 | -0.013677 | 0.10005 | 0.10024 | 0.10024 | 0.99847 | -0.007306 | 0.99571 | 0.015159 | 45.565
99 | -6.3812 | -2.9394 | 6.3816 | 2.9391 | 0.0003986 | -0.00039448 | 0.20313 | 0.20312 | 0.20313 | 0.99847 | -0.007306 | 0.99854 | -0.0065203 | 56.112
100 | 2.6687 | 1.2472 | -2.6679 | -1.2491 | 0.00086951 | -0.0018781 | 0.085168 | 0.085194 | 0.085194 | 0.99847 | -0.007306 | 0.99816 | -0.0046842 | 38.7245
101 | 0.095477 | 0.046086 | -0.095477 | -0.046242 | 8.273e-08 | -0.00015517 | 0.0030737 | 0.0030756 | 0.0030756 | 0.99571 | 0.015159 | 0.99571 | 0.015166 | 1.398
102 | 3.0452 | 1.4001 | -3.0379 | -1.4116 | 0.0072935 | -0.011479 | 0.09717 | 0.097336 | 0.097336 | 0.99571 | 0.015159 | 0.99348 | 0.033904 | 44.2436
103 | 0.090379 | 0.042611 | -0.090379 | -0.042814 | 9.507e-08 | -0.00020295 | 0.0028887 | 0.0028912 | 0.0028912 | 0.99854 | -0.0065203 | 0.99854 | -0.0065116 | 1.3142
104 | -6.472 | -2.9817 | 6.4728 | 2.9783 | 0.00080349 | -0.0033875 | 0.20601 | 0.20596 | 0.20601 | 0.99854 | -0.0065203 | 0.99867 | -0.0059176 | 32.2893
105 | 1.4014 | 0.63574 | -1.4014 | -0.63657 | 9.5388e-05 | -0.00082956 | 0.044506 | 0.044516 | 0.044516 | 0.99816 | -0.0046842 | 0.9981 | -0.0041755 | 20.2347
106 | 2.5082 | 1.1567 | -2.5081 | -1.1572 | 0.00017988 | -0.0004395 | 0.080259 | 0.080265 | 0.080265 | 0.99348 | 0.033904 | 0.99341 | 0.034462 | 36.4841
107 | 0.52965 | 0.25484 | -0.52963 | -0.25641 | 2.6093e-05 | -0.0015694 | 0.017079 | 0.017099 | 0.017099 | 0.99348 | 0.033904 | 0.99343 | 0.03433 | 7.7722
108 | 0.4909 | 0.23627 | -0.49088 | -0.23775 | 2.1086e-05 | -0.0014768 | 0.015831 | 0.01585 | 0.01585 | 0.99341 | 0.034462 | 0.99337 | 0.034833 | 7.2046
109 | 2.0172 | 0.92089 | -2.0162 | -0.92474 | 0.00097469 | -0.0038491 | 0.064436 | 0.064486 | 0.064486 | 0.99341 | 0.034462 | 0.99296 | 0.038147 | 29.3119
110 | 0.32076 | 0.15526 | -0.32075 | -0.15535 | 1.599e-05 | -8.857e-05 | 0.010355 | 0.010357 | 0.010357 | 0.99343 | 0.03433 | 0.99338 | 0.034001 | 4.9317
111 | 0.85677 | 0.40918 | -0.85675 | -0.40965 | 2.0735e-05 | -0.0004736 | 0.027603 | 0.027609 | 0.027609 | 0.99296 | 0.038147 | 0.99294 | 0.038352 | 12.5496
112 | 1.1594 | 0.51556 | -1.1588 | -0.52317 | 0.00060337 | -0.0076164 | 0.036889 | 0.036982 | 0.036982 | 0.99296 | 0.038147 | 0.99247 | 0.041909 | 16.8098
113 | 0.68859 | 0.32821 | -0.68849 | -0.32829 | 0.00010693 | -7.661e-05 | 0.022177 | 0.022179 | 0.022179 | 0.99294 | 0.038352 | 0.99277 | 0.037267 | 10.5614
114 | 0.19501 | 0.093542 | -0.19501 | -0.094315 | 1.7407e-06 | -0.00077311 | 0.0062909 | 0.0063007 | 0.0063007 | 0.99247 | 0.041909 | 0.99246 | 0.041986 | 2.864
115 | 0.9638 | 0.42963 | -0.96293 | -0.44541 | 0.00086379 | -0.015783 | 0.030693 | 0.030886 | 0.030886 | 0.99247 | 0.041909 | 0.99163 | 0.048618 | 14.0389
116 | 0.081585 | 0.039382 | -0.081585 | -0.039513 | 5.1657e-08 | -0.00013099 | 0.0026351 | 0.0026367 | 0.0026367 | 0.99246 | 0.041986 | 0.99246 | 0.041991 | 1.1985
117 | 0.32267 | 0.15606 | -0.32267 | -0.15628 | 1.368e-06 | -0.00022052 | 0.010434 | 0.010437 | 0.010437 | 0.99163 | 0.048618 | 0.99163 | 0.048655 | 4.7441
118 | 0.64026 | 0.28936 | -0.64011 | -0.29565 | 0.00015137 | -0.0062931 | 0.020454 | 0.02053 | 0.02053 | 0.99163 | 0.048618 | 0.99141 | 0.050415 | 9.332
119 | 0.090379 | 0.042814 | -0.090379 | -0.043772 | 4.5107e-07 | -0.00095818 | 0.0028912 | 0.0029032 | 0.0029032 | 0.99854 | -0.0065116 | 0.99853 | -0.0064692 | 1.3196
120 | -7.4341 | -3.4438 | 7.4349 | 3.4414 | 0.00081729 | -0.0024957 | 0.23683 | 0.23679 | 0.23683 | 0.99867 | -0.0059176 | 0.99878 | -0.0053987 | 37.1205
121 | 0.16003 | 0.075057 | -0.16002 | -0.076854 | 2.6485e-06 | -0.001797 | 0.0051121 | 0.0051344 | 0.0051344 | 0.9981 | -0.0041755 | 0.99808 | -0.0040378 | 2.3338
122 | 0.11478 | 0.054688 | -0.11478 | -0.055591 | 6.876e-07 | -0.00090295 | 0.0036773 | 0.0036887 | 0.0036887 | 0.9981 | -0.0041755 | 0.99809 | -0.0041243 | 1.6767
123 | 1.1265 | 0.50683 | -1.1261 | -0.51254 | 0.000419 | -0.0057106 | 0.035728 | 0.035798 | 0.035798 | 0.9981 | -0.0041755 | 0.99775 | -0.0014176 | 16.2716
124 | 0.3368 | 0.16091 | -0.3368 | -0.16137 | 3.1183e-06 | -0.00046506 | 0.010856 | 0.010862 | 0.010862 | 0.99258 | 0.037335 | 0.99257 | 0.037413 | 4.9371
125 | -0.3368 | -0.16091 | 0.3368 | 0.16028 | 4.2279e-06 | -0.00063136 | 0.010856 | 0.010848 | 0.010856 | 0.99258 | 0.037335 | 0.99259 | 0.037229 | 4.9344
126 | 0.3368 | 0.16137 | -0.33679 | -0.16301 | 1.0986e-05 | -0.0016344 | 0.010862 | 0.010882 | 0.010882 | 0.99257 | 0.037413 | 0.99254 | 0.037694 | 4.9465
127 | -0.60823 | -0.29173 | 0.60829 | 0.29167 | 6.29e-05 | -6.8504e-05 | 0.019619 | 0.019617 | 0.019619 | 0.99259 | 0.037229 | 0.9927 | 0.037936 | 9.3422
128 | 0.26588 | 0.11474 | -0.26582 | -0.12857 | 5.713e-05 | -0.013835 | 0.0084319 | 0.0085997 | 0.0085997 | 0.99141 | 0.050415 | 0.99121 | 0.052053 | 3.909
129 | 0.37423 | 0.18091 | -0.37423 | -0.18125 | 2.7789e-06 | -0.00033253 | 0.012103 | 0.012107 | 0.012107 | 0.99141 | 0.050415 | 0.99141 | 0.050479 | 5.5034
130 | 0.60834 | 0.28947 | -0.60831 | -0.29068 | 2.6585e-05 | -0.0012123 | 0.01959 | 0.019605 | 0.019605 | 0.99277 | 0.037267 | 0.99273 | 0.037635 | 8.9113
131 | 0.069289 | 0.032326 | -0.069288 | -0.033558 | 3.3958e-07 | -0.0012315 | 0.0022101 | 0.0022254 | 0.0022254 | 0.99867 | -0.0056777 | 0.99867 | -0.0056367 | 1.0115
132 | 0.51606 | 0.24576 | -0.51605 | -0.24658 | 1.2686e-05 | -0.000814 | 0.016576 | 0.016586 | 0.016586 | 0.99546 | -0.025649 | 0.99544 | -0.025442 | 7.539
133 | -0.16826 | -0.08149 | 0.16826 | 0.081315 | 7.8622e-06 | -0.00017438 | 0.0054092 | 0.005407 | 0.0054092 | 0.9977 | -0.0017269 | 0.99775 | -0.0014176 | 2.5758
134 | 0.95786 | 0.43122 | -0.95728 | -0.44223 | 0.00058276 | -0.011004 | 0.030392 | 0.030527 | 0.030527 | 0.99775 | -0.0014176 | 0.99718 | 0.003185 | 13.8757
135 | 0.49712 | 0.22255 | -0.49706 | -0.22671 | 5.8489e-05 | -0.0041529 | 0.015768 | 0.015817 | 0.015817 | 0.99718 | 0.003185 | 0.99707 | 0.0040542 | 7.1897
136 | 0.46016 | 0.21968 | -0.46014 | -0.22082 | 1.405e-05 | -0.0011414 | 0.014761 | 0.014776 | 0.014776 | 0.99718 | 0.003185 | 0.99715 | 0.0034441 | 6.7162
137 | 0.17905 | 0.08312 | -0.17905 | -0.085846 | 5.0399e-06 | -0.0027258 | 0.0057153 | 0.005749 | 0.005749 | 0.99707 | 0.0040542 | 0.99704 | 0.0042853 | 2.6132
138 | 0.1922 | 0.085402 | -0.19219 | -0.091512 | 1.2906e-05 | -0.0061106 | 0.0060894 | 0.0061634 | 0.0061634 | 0.99707 | 0.0040542 | 0.99701 | 0.0045736 | 2.8015
139 | 0.12581 | 0.058184 | -0.1258 | -0.06093 | 2.5082e-06 | -0.0027452 | 0.0040131 | 0.0040471 | 0.0040471 | 0.99707 | 0.0040542 | 0.99705 | 0.0042192 | 1.8396
140 | 0.23005 | 0.10938 | -0.23004 | -0.1105 | 3.4449e-06 | -0.0011233 | 0.0073743 | 0.0073883 | 0.0073883 | 0.99715 | 0.0034441 | 0.99714 | 0.0035707 | 3.3583
141 | 0.17905 | 0.085846 | -0.17904 | -0.086715 | 1.6185e-06 | -0.00086849 | 0.005749 | 0.0057599 | 0.0057599 | 0.99704 | 0.0042853 | 0.99704 | 0.0043632 | 2.6181
142 | 0.19219 | 0.091512 | -0.19219 | -0.093081 | 3.3655e-06 | -0.001569 | 0.0061634 | 0.0061831 | 0.0061831 | 0.99701 | 0.0045736 | 0.99699 | 0.0047233 | 2.8105
143 | 0.16002 | 0.076854 | -0.16002 | -0.077502 | 9.6123e-07 | -0.0006483 | 0.0051344 | 0.0051426 | 0.0051426 | 0.99808 | -0.0040378 | 0.99808 | -0.0039859 | 2.3375
144 | 0.11424 | 0.054411 | -0.11424 | -0.055327 | 6.9326e-07 | -0.00091564 | 0.0036632 | 0.0036746 | 0.0036746 | 0.99714 | 0.0035707 | 0.99713 | 0.0036226 | 1.6703
145 | -0.20678 | -0.10015 | 0.20678 | 0.10007 | 1.9997e-07 | -7.6989e-05 | 0.0067224 | 0.0067215 | 0.0067224 | 0.98664 | 0.039684 | 0.98664 | 0.039675 | 3.0557
146 | 0.53629 | 0.24782 | -0.53626 | -0.24917 | 2.3294e-05 | -0.0013485 | 0.017287 | 0.017304 | 0.017304 | 0.98654 | 0.038644 | 0.9865 | 0.038986 | 7.8653
147 | 0.26582 | 0.12857 | -0.2658 | -0.12873 | 1.9604e-05 | -0.00016217 | 0.0085997 | 0.0086019 | 0.0086019 | 0.99121 | 0.052053 | 0.99114 | 0.051566 | 4.0961
148 | -0.60829 | -0.29167 | 0.60831 | 0.29068 | 2.1637e-05 | -0.00098515 | 0.019617 | 0.019605 | 0.019617 | 0.9927 | 0.037936 | 0.99273 | 0.037635 | 8.9169
149 | 0.20618 | 0.099756 | -0.20618 | -0.099856 | 7.0286e-06 | -0.00010011 | 0.0066618 | 0.0066631 | 0.0066631 | 0.99254 | 0.037694 | 0.9925 | 0.037469 | 3.1729
150 | 0.12319 | 0.056722 | -0.12319 | -0.059662 | 2.5858e-06 | -0.0029394 | 0.0039314 | 0.0039678 | 0.0039678 | 0.99583 | -0.028906 | 0.99581 | -0.028734 | 1.8035
151 | 0.1466 | 0.063177 | -0.14659 | -0.070122 | 8.5358e-06 | -0.0069442 | 0.0046274 | 0.0047107 | 0.0047107 | 0.99583 | -0.028906 | 0.99578 | -0.02847 | 2.1412
152 | 0.14659 | 0.070122 | -0.14659 | -0.070995 | 1.0959e-06 | -0.00087345 | 0.0047107 | 0.0047217 | 0.0047217 | 0.99578 | -0.02847 | 0.99577 | -0.028405 | 2.1462
153 | -1.4858 | -0.71959 | 1.4858 | 0.71947 | 1.545e-05 | -0.00011649 | 0.047715 | 0.047713 | 0.047715 | 0.99877 | -0.0053081 | 0.99878 | -0.0053987 | 21.6885
154 | -8.9207 | -4.1608 | 8.9209 | 4.1604 | 0.00021909 | -0.00042572 | 0.2845 | 0.28449 | 0.2845 | 0.99878 | -0.0053987 | 0.9988 | -0.0052869 | 44.5925
155 | 0.09769 | 0.045363 | -0.097689 | -0.047313 | 1.0676e-06 | -0.0019502 | 0.003113 | 0.0031372 | 0.0031372 | 0.9988 | -0.0052869 | 0.99879 | -0.0051961 | 1.426
156 | -9.0186 | -4.2058 | 9.0204 | 4.2023 | 0.0018114 | -0.0034239 | 0.28761 | 0.28755 | 0.28761 | 0.9988 | -0.0052869 | 0.99901 | -0.00437 | 45.0793
157 | -9.1236 | -4.2519 | 9.1271 | 4.2455 | 0.0034878 | -0.0064089 | 0.29086 | 0.29076 | 0.29086 | 0.99901 | -0.00437 | 0.99941 | -0.0026149 | 45.5894
158 | 0.10322 | 0.049549 | -0.10322 | -0.049991 | 2.7143e-07 | -0.00044179 | 0.0033085 | 0.003314 | 0.003314 | 0.99901 | -0.00437 | 0.99901 | -0.0043473 | 1.5064
159 | -9.7163 | -4.53 | 9.7218 | 4.5214 | 0.0055384 | -0.0086248 | 0.30965 | 0.30951 | 0.30965 | 0.99941 | -0.0026149 | 1 | 0 | 48.5351
160 | 0.58915 | 0.28453 | -0.58913 | -0.28533 | 1.6112e-05 | -0.00080068 | 0.018898 | 0.018908 | 0.018908 | 0.99941 | -0.0026149 | 0.99938 | -0.0023774 | 8.5946
161 | 10.5835 | 4.7736 | -10.5811 | -4.7767 | 0.0024718 | -0.0030807 | 0.33516 | 0.33521 | 0.33521 | 1 | 0 | 0.99976 | -0.0012439 | 52.5413
162 | 0.49289 | 0.23798 | -0.49288 | -0.2386 | 8.7364e-06 | -0.00062297 | 0.0158 | 0.015808 | 0.015808 | 1 | 0 | 0.99998 | 0.0001538 | 7.1854
163 | 10.4804 | 4.7286 | -10.4751 | -4.7352 | 0.0052067 | -0.0066609 | 0.33199 | 0.3321 | 0.3321 | 0.99976 | -0.0012439 | 0.99924 | -0.0038805 | 52.054
164 | 0.10072 | 0.048125 | -0.10072 | -0.048781 | 3.8238e-07 | -0.00065617 | 0.0032232 | 0.0032314 | 0.0032314 | 0.99976 | -0.0012439 | 0.99975 | -0.0012113 | 1.4688
165 | 0.26405 | 0.12778 | -0.26404 | -0.12788 | 1.1923e-05 | -0.00010391 | 0.0084681 | 0.0084695 | 0.0084695 | 0.99998 | 0.0001538 | 0.99994 | -0.00014438 | 4.0331
166 | 0.2438 | 0.11793 | -0.2438 | -0.11808 | 5.0703e-07 | -0.00014544 | 0.0078546 | 0.0078564 | 0.0078564 | 0.99534 | 0.024411 | 0.99534 | 0.024429 | 3.5711
167 | 0.14892 | 0.07072 | -0.14892 | -0.072123 | 1.8177e-06 | -0.0014037 | 0.0047808 | 0.0047984 | 0.0047984 | 0.99544 | -0.025442 | 0.99543 | -0.025338 | 2.1811
168 | 0.36713 | 0.17586 | -0.36711 | -0.17769 | 1.4515e-05 | -0.0018379 | 0.011805 | 0.011828 | 0.011828 | 0.99544 | -0.025442 | 0.9954 | -0.025102 | 5.3765
169 | 0.36711 | 0.17769 | -0.36711 | -0.1778 | 8.3782e-07 | -0.00010585 | 0.011828 | 0.01183 | 0.01183 | 0.9954 | -0.025102 | 0.9954 | -0.025082 | 5.3771

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 20.8122 | 9.5435

## res_load
| p_mw | q_mvar
0 | 0.29421 | 0.14249
1 | 0.082827 | 0.040115
2 | 0.1015 | 0.049158
3 | 0.39804 | 0.19278
4 | 0.39493 | 0.19127
5 | 0.14236 | 0.068948
6 | 0.096873 | 0.046918
7 | 0.31231 | 0.15126
8 | 1.2459 | 0.60343
9 | 0.35019 | 0.1696
10 | 0.21097 | 0.10218
11 | 0.074573 | 0.036117
12 | 0.099564 | 0.048221
13 | 0.32513 | 0.15747
14 | 0.11068 | 0.053603
15 | 0.17794 | 0.086178
16 | 0.17776 | 0.086091
17 | 0.3995 | 0.19349
18 | 0.1853 | 0.089747
19 | 0.19863 | 0.096202
20 | 0.33502 | 0.16226
21 | 0.17464 | 0.084584
22 | 0.37196 | 0.18015
23 | 0.073378 | 0.035538
24 | 0.1665 | 0.080638
25 | 0.28706 | 0.13903
26 | 0.077897 | 0.037727
27 | 0.22294 | 0.10798
28 | 0.094071 | 0.045561
29 | 0.11879 | 0.057535
30 | 0.10641 | 0.051538
31 | 0.3047 | 0.14757
32 | 0.11738 | 0.056848
33 | 0.12364 | 0.05988
34 | 0.078247 | 0.037897
35 | 0.26108 | 0.12645
36 | 0.25463 | 0.12332
37 | 0.092748 | 0.04492
38 | 0.11526 | 0.055823
39 | 0.099812 | 0.048341
40 | 1.2664 | 0.61335
41 | 0.095477 | 0.046242
42 | 0.20886 | 0.10116
43 | 0.16816 | 0.081442
44 | 0.49088 | 0.23775
45 | 0.11342 | 0.054933
46 | 0.96129 | 0.46557
47 | 0.27142 | 0.13146
48 | 0.32267 | 0.15628
49 | 0.32075 | 0.15535
50 | 0.080149 | 0.038818
51 | 0.082014 | 0.039721
52 | 0.069288 | 0.033558
53 | 0.099584 | 0.048231
54 | 0.16826 | 0.08149
55 | 0.2301 | 0.11144
56 | 0.1258 | 0.06093
57 | 0.17904 | 0.086715
58 | 0.11478 | 0.055591
59 | 0.19219 | 0.093081
60 | 0.11581 | 0.056088
61 | 0.16002 | 0.077502
62 | 0.20678 | 0.10015
63 | 0.14011 | 0.067859
64 | 0.37423 | 0.18125
65 | 0.2658 | 0.12873
66 | 0.1306 | 0.063253
67 | 0.20618 | 0.099856
68 | 0.081585 | 0.039513
69 | 0.28394 | 0.13752
70 | 0.12319 | 0.059662
71 | 0.14659 | 0.070995
72 | 1.4858 | 0.71959
73 | 0.097689 | 0.047313
74 | 0.10322 | 0.049991
75 | 0.58913 | 0.28533
76 | 0.22883 | 0.11083
77 | 0.10072 | 0.048781
78 | 0.26404 | 0.12788
79 | 0.090379 | 0.043772
80 | 0.20456 | 0.099071
81 | 0.2438 | 0.11808
82 | 0.14892 | 0.072123
83 | 0.36711 | 0.1778
84 | 0.11424 | 0.055327

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1