## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_72_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_72_0_node_118 | 20 | n |  | TRUE
2 | bus_MV_72_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_72_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_72_0_node_22 | 20 | n |  | TRUE
5 | bus_MV_72_0_node_123 | 20 | n |  | TRUE
6 | bus_MV_72_0_node_3 | 20 | n |  | TRUE
7 | bus_MV_72_0_node_162 | 20 | n |  | TRUE
8 | bus_MV_72_0_node_6 | 20 | n |  | TRUE
9 | bus_MV_72_0_node_5 | 20 | n |  | TRUE
10 | bus_MV_72_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_72_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_72_0_node_133 | 20 | n |  | TRUE
13 | bus_MV_72_0_node_9 | 20 | n |  | TRUE
14 | bus_MV_72_0_node_10 | 20 | n |  | TRUE
15 | bus_MV_72_0_node_11 | 20 | n |  | TRUE
16 | bus_MV_72_0_node_12 | 20 | n |  | TRUE
17 | bus_MV_72_0_node_26 | 20 | n |  | TRUE
18 | bus_MV_72_0_node_161 | 20 | n |  | TRUE
19 | bus_MV_72_0_node_13 | 20 | n |  | TRUE
20 | bus_MV_72_0_node_160 | 20 | n |  | TRUE
21 | bus_MV_72_0_node_135 | 20 | n |  | TRUE
22 | bus_MV_72_0_node_14 | 20 | n |  | TRUE
23 | bus_MV_72_0_node_158 | 20 | n |  | TRUE
24 | bus_MV_72_0_node_17 | 20 | n |  | TRUE
25 | bus_MV_72_0_node_19 | 20 | n |  | TRUE
26 | bus_MV_72_0_node_20 | 20 | n |  | TRUE
27 | bus_MV_72_0_node_18 | 20 | n |  | TRUE
28 | bus_MV_72_0_node_21 | 20 | n |  | TRUE
29 | bus_MV_72_0_node_120 | 20 | n |  | TRUE
30 | bus_MV_72_0_node_23 | 20 | n |  | TRUE
31 | bus_MV_72_0_node_132 | 20 | n |  | TRUE
32 | bus_MV_72_0_node_124 | 20 | n |  | TRUE
33 | bus_MV_72_0_node_125 | 20 | n |  | TRUE
34 | bus_MV_72_0_node_24 | 20 | n |  | TRUE
35 | bus_MV_72_0_node_117 | 20 | n |  | TRUE
36 | bus_MV_72_0_node_25 | 20 | n |  | TRUE
37 | bus_MV_72_0_node_27 | 20 | n |  | TRUE
38 | bus_MV_72_0_node_28 | 20 | n |  | TRUE
39 | bus_MV_72_0_node_48 | 20 | n |  | TRUE
40 | bus_MV_72_0_node_128 | 20 | n |  | TRUE
41 | bus_MV_72_0_node_127 | 20 | n |  | TRUE
42 | bus_MV_72_0_node_159 | 20 | n |  | TRUE
43 | bus_MV_72_0_node_61 | 20 | n |  | TRUE
44 | bus_MV_72_0_node_134 | 20 | n |  | TRUE
45 | bus_MV_72_0_node_63 | 20 | n |  | TRUE
46 | bus_MV_72_0_node_131 | 20 | n |  | TRUE
47 | bus_MV_72_0_node_164 | 20 | n |  | TRUE
48 | bus_MV_72_0_node_119 | 20 | n |  | TRUE
49 | bus_MV_72_0_node_129 | 20 | n |  | TRUE
50 | bus_MV_72_0_node_130 | 20 | n |  | TRUE
51 | bus_MV_72_0_node_60 | 20 | n |  | TRUE
52 | bus_MV_72_0_node_62 | 20 | n |  | TRUE
53 | bus_MV_72_0_node_146 | 20 | n |  | TRUE
54 | bus_MV_72_0_node_114 | 20 | n |  | TRUE
55 | bus_MV_72_0_node_115 | 20 | n |  | TRUE
56 | bus_MV_72_0_node_116 | 20 | n |  | TRUE
57 | bus_MV_72_0_node_121 | 20 | n |  | TRUE
58 | bus_MV_72_0_node_126 | 20 | n |  | TRUE
59 | bus_MV_72_0_node_122 | 20 | n |  | TRUE
60 | bus_HV_72_0_node_127 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_72_0_load_0 | 0 | 0.22234 | 0.10768 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_72_0_load_123 | 5 | 0.075738 | 0.036682 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_72_0_load_162 | 7 | 0.1776 | 0.086017 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_72_0_load_5 | 9 | 0.1481 | 0.071728 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_72_0_load_133 | 12 | 0.077026 | 0.037306 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_72_0_load_9 | 13 | 0.35926 | 0.174 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_72_0_load_161 | 18 | 0.26199 | 0.12689 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_72_0_load_160 | 20 | 0.1135 | 0.05497 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_72_0_load_14 | 22 | 0.1746 | 0.084561 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_72_0_load_158 | 23 | 0.097361 | 0.047154 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_72_0_load_17 | 24 | 0.37312 | 0.18071 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_72_0_load_19 | 25 | 0.15574 | 0.075427 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_72_0_load_18 | 27 | 0.28121 | 0.1362 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_72_0_load_21 | 28 | 0.13734 | 0.066519 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_72_0_load_132 | 31 | 0.71864 | 0.34805 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_72_0_load_124 | 32 | 0.2404 | 0.11643 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_72_0_load_125 | 33 | 0.32748 | 0.15861 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_72_0_load_24 | 34 | 0.17394 | 0.084242 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_72_0_load_25 | 36 | 0.33445 | 0.16198 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_72_0_load_27 | 37 | 0.10506 | 0.050883 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_72_0_load_128 | 40 | 0.089327 | 0.043263 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_72_0_load_127 | 41 | 0.069085 | 0.033459 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_72_0_load_159 | 42 | 0.23136 | 0.11205 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_72_0_load_134 | 44 | 0.14452 | 0.069994 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_72_0_load_164 | 47 | 0.1863 | 0.090227 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_72_0_load_129 | 49 | 0.13087 | 0.063384 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_72_0_load_60 | 51 | 0.25403 | 0.12303 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_72_0_load_146 | 53 | 0.10242 | 0.049606 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_72_0_load_114 | 54 | 0.070445 | 0.034118 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_72_0_load_126 | 58 | 0.37056 | 0.17947 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_72_0_load_122 | 59 | 1.8553 | 0.89855 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_72_0_line_0 |  | 0 | 1 | 0.1101 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_72_0_line_1 |  | 0 | 2 | 0.11251 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_72_0_line_2 |  | 1 | 58 | 0.10452 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
3 | MV_72_0_line_3 |  | 1 | 35 | 0.10059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_72_0_line_4 |  | 1 | 55 | 0.31262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_72_0_line_5 |  | 2 | 3 | 0.094338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_72_0_line_6 |  | 3 | 4 | 0.13444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_72_0_line_7 |  | 3 | 5 | 0.040905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_72_0_line_8 |  | 4 | 32 | 0.048286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_72_0_line_9 |  | 4 | 26 | 0.051782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_72_0_line_10 |  | 6 | 7 | 0.074694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_72_0_line_11 |  | 6 | 8 | 0.2397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_72_0_line_12 |  | 7 | 46 | 0.089127 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_72_0_line_13 |  | 8 | 9 | 0.074173 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_72_0_line_14 |  | 9 | 10 | 0.073729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_72_0_line_15 |  | 10 | 11 | 0.056011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_72_0_line_16 |  | 11 | 12 | 0.10245 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_72_0_line_17 |  | 12 | 15 | 0.10425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_72_0_line_18 |  | 13 | 14 | 0.054947 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_72_0_line_19 |  | 14 | 15 | 0.073837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_72_0_line_20 |  | 14 | 16 | 0.32669 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_72_0_line_21 |  | 15 | 17 | 0.062765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_72_0_line_22 |  | 16 | 18 | 0.016583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_72_0_line_23 |  | 16 | 19 | 0.2051 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_72_0_line_24 |  | 17 | 36 | 0.009476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_72_0_line_25 |  | 19 | 20 | 0.097624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_72_0_line_26 |  | 19 | 21 | 0.54043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_72_0_line_27 |  | 21 | 45 | 0.20704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_72_0_line_28 |  | 21 | 23 | 0.070768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_72_0_line_29 |  | 22 | 23 | 0.042623 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_72_0_line_30 |  | 24 | 25 | 0.034731 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_72_0_line_31 |  | 24 | 26 | 0.036024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_72_0_line_32 |  | 25 | 29 | 0.14622 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_72_0_line_33 |  | 26 | 30 | 0.014983 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_72_0_line_34 |  | 27 | 28 | 0.01632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_72_0_line_35 |  | 28 | 31 | 0.11979 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_72_0_line_36 |  | 29 | 31 | 0.086366 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_72_0_line_37 |  | 30 | 33 | 0.042201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_72_0_line_38 |  | 34 | 35 | 0.25567 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_72_0_line_39 |  | 35 | 49 | 0.057645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_72_0_line_40 |  | 37 | 38 | 0.090147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_72_0_line_41 |  | 38 | 39 | 2.3558 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_72_0_line_42 |  | 39 | 47 | 0.033687 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_72_0_line_43 |  | 40 | 41 | 0.049009 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_72_0_line_44 |  | 41 | 58 | 0.069109 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
45 | MV_72_0_line_45 |  | 42 | 43 | 0.34661 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_72_0_line_46 |  | 43 | 45 | 0.23606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_72_0_line_47 |  | 43 | 52 | 0.12236 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_72_0_line_48 |  | 44 | 45 | 0.06919 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_72_0_line_49 |  | 46 | 50 | 0.10799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_72_0_line_50 |  | 47 | 48 | 0.039198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_72_0_line_51 |  | 48 | 55 | 1.4975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_72_0_line_52 |  | 49 | 50 | 0.099023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_72_0_line_53 |  | 51 | 52 | 0.040252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_72_0_line_54 |  | 51 | 53 | 1.2919 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_72_0_line_55 |  | 54 | 55 | 0.032965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_72_0_line_56 |  | 54 | 56 | 0.035198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_72_0_line_57 |  | 56 | 57 | 0.11458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_72_0_line_58 |  | 57 | 59 | 0.25446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_72_0_trafo_127 | 25 MVA 110/20 kV | 60 | 41 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2715087.3659 | 1106061.5075
1 | 2714996.3687 | 1105999.5188
2 | 2715085.7342 | 1106174.008
3 | 2715121.9738 | 1106256.2841
4 | 2715179.6132 | 1106377.7373
5 | 2715085.5516 | 1106274.9021
6 | 2714601.3104 | 1105914.9681
7 | 2714672.76 | 1105892.5579
8 | 2714566.2364 | 1105687.753
9 | 2714580.3601 | 1105614.9372
10 | 2714576.2807 | 1105541.3551
11 | 2714538.7814 | 1105499.7639
12 | 2714443.1841 | 1105462.9268
13 | 2714321.5971 | 1105407.808
14 | 2714313.6866 | 1105353.4336
15 | 2714376.0317 | 1105383.3725
16 | 2714264.6895 | 1105127.7816
17 | 2714431.4329 | 1105371.6976
18 | 2714248.2349 | 1105126.9269
19 | 2714191.5686 | 1105061.45
20 | 2714245.676 | 1105002.3504
21 | 2714529.4896 | 1104881.4387
22 | 2714507.6702 | 1104990.9898
23 | 2714524.9924 | 1104952.0459
24 | 2715218.2908 | 1106456.5873
25 | 2715249.4294 | 1106441.2051
26 | 2715202.3356 | 1106424.2888
27 | 2715293.1605 | 1106610.631
28 | 2715300.1487 | 1106625.3792
29 | 2715386.9823 | 1106490.7968
30 | 2715188.8596 | 1106430.9153
31 | 2715408.4289 | 1106574.1481
32 | 2715136.8397 | 1106400.143
33 | 2715150.9835 | 1106449.5241
34 | 2714694.5183 | 1106181.1678
35 | 2714910.8693 | 1106044.9302
36 | 2714438.3264 | 1105378.2208
37 | 2718196.4882 | 1106494.65
38 | 2718130.293 | 1106447.4401
39 | 2715816.9159 | 1106892.4572
40 | 2714898.9775 | 1105799.3227
41 | 2714920.504 | 1105843.3514
42 | 2714209.5443 | 1104370.7455
43 | 2714452.8367 | 1104617.6265
44 | 2714519.6204 | 1104752.5884
45 | 2714588.6008 | 1104757.9709
46 | 2714761.81 | 1105888.8606
47 | 2715790.652 | 1106913.0478
48 | 2715769.6812 | 1106881.2262
49 | 2714884.8759 | 1105993.4788
50 | 2714840.3429 | 1105905.0345
51 | 2714468.8001 | 1104487.1062
52 | 2714430.0282 | 1104497.4156
53 | 2715374.253 | 1103565.6763
54 | 2715220.5367 | 1105950.4343
55 | 2715230.0731 | 1105922.61
56 | 2715188.7701 | 1105965.5884
57 | 2715124.8099 | 1105903.0661
58 | 2714950.902 | 1105905.4163
59 | 2715014.7107 | 1105673.751
60 | 2714920.504 | 1105843.3514

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99894 | -0.010573 | 0.22234 | 0.10768
1 | 0.99948 | -0.0070532 | 0 | 0
2 | 0.99844 | -0.013869 | 0 | 0
3 | 0.99816 | -0.011334 | 0 | 0
4 | 0.99778 | -0.0078095 | 0 | 0
5 | 0.99815 | -0.011298 | 0.075738 | 0.036682
6 | 0.99764 | 0.0013415 | 0 | 0
7 | 0.99786 | -0.00043427 | 0.1776 | 0.086017
8 | 0.99694 | 0.0071029 | 0 | 0
9 | 0.99661 | 0.0046776 | 0.1481 | 0.071728
10 | 0.99641 | 0.0063378 | 0 | 0
11 | 0.99626 | 0.007605 | 0 | 0
12 | 0.99583 | 0.0044654 | 0.077026 | 0.037306
13 | 0.99536 | 0.0078339 | 0.35926 | 0.174
14 | 0.99539 | 0.0080748 | 0 | 0
15 | 0.99556 | 0.0067418 | 0 | 0
16 | 0.99482 | 0.01266 | 0 | 0
17 | 0.99553 | 0.0069913 | 0 | 0
18 | 0.99482 | 0.012712 | 0.26199 | 0.12689
19 | 0.99453 | 0.014979 | 0 | 0
20 | 0.99452 | 0.015106 | 0.1135 | 0.05497
21 | 0.99384 | 0.020742 | 0 | 0
22 | 0.9938 | 0.02088 | 0.1746 | 0.084561
23 | 0.99381 | 0.020971 | 0.097361 | 0.047154
24 | 0.99757 | -0.0058771 | 0.37312 | 0.18071
25 | 0.99751 | -0.005344 | 0.15574 | 0.075427
26 | 0.99764 | -0.0065897 | 0 | 0
27 | 0.99696 | -0.0067838 | 0.28121 | 0.1362
28 | 0.99697 | -0.0068389 | 0.13734 | 0.066519
29 | 0.99719 | -0.007398 | 0 | 0
30 | 0.99764 | -0.0065318 | 0 | 0
31 | 0.99706 | -0.0062247 | 0.71864 | 0.34805
32 | 0.99776 | -0.0076718 | 0.2404 | 0.11643
33 | 0.99762 | -0.006367 | 0.32748 | 0.15861
34 | 0.99904 | -0.0046838 | 0.17394 | 0.084242
35 | 0.99912 | -0.0041421 | 0 | 0
36 | 0.99553 | 0.0070295 | 0.33445 | 0.16198
37 | 0.99755 | -0.0004339 | 0.10506 | 0.050883
38 | 0.99756 | -0.00054157 | 0 | 0
39 | 0.99804 | 0.0031753 | 0 | 0
40 | 0.99999 | 5.0548e-05 | 0.089327 | 0.043263
41 | 1 | 0 | -8.0293 | -3.7361
42 | 0.99331 | 0.023015 | 0.23136 | 0.11205
43 | 0.99347 | 0.024003 | 0 | 0
44 | 0.99363 | 0.022527 | 0.14452 | 0.069994
45 | 0.99365 | 0.02241 | 0 | 0
46 | 0.99828 | 0.0027277 | 0 | 0
47 | 0.99804 | 0.0031442 | 0.1863 | 0.090227
48 | 0.99806 | 0.0030226 | 0 | 0
49 | 0.99893 | -0.0025851 | 0.13087 | 0.063384
50 | 0.99862 | -5.2801e-05 | 0 | 0
51 | 0.99337 | 0.023611 | 0.25403 | 0.12303
52 | 0.99338 | 0.023443 | 0 | 0
53 | 0.99311 | 0.021906 | 0.10242 | 0.049606
54 | 0.99852 | 0.00086913 | 0.070445 | 0.034118
55 | 0.9986 | 0.00012854 | 0 | 0
56 | 0.99844 | 0.0016321 | 0 | 0
57 | 0.99817 | 0.0041297 | 0 | 0
58 | 0.99982 | -0.00079288 | 0.37056 | 0.17947
59 | 0.99756 | 0.0097527 | 1.8553 | 0.89855
60 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -2.5358 | -1.2132 | 2.5371 | 1.2139 | 0.0012945 | 0.00067962 | 0.081234 | 0.081233 | 0.081234 | 0.99894 | -0.010573 | 0.99948 | -0.0070532 | 38.683
1 | 2.3134 | 1.1055 | -2.3123 | -1.105 | 0.0011006 | 0.00055541 | 0.074095 | 0.074097 | 0.074097 | 0.99894 | -0.010573 | 0.99844 | -0.013869 | 35.2843
2 | -7.5518 | -3.5095 | 7.554 | 3.5076 | 0.0022124 | -0.0019588 | 0.24052 | 0.24047 | 0.24052 | 0.99948 | -0.0070532 | 0.99982 | -0.00079288 | 57.1303
3 | 2.7933 | 1.2807 | -2.7922 | -1.2828 | 0.0010582 | -0.0020845 | 0.088753 | 0.088782 | 0.088782 | 0.99948 | -0.0070532 | 0.99912 | -0.0041421 | 40.3554
4 | 2.2214 | 1.0149 | -2.2194 | -1.0218 | 0.0020793 | -0.006833 | 0.07054 | 0.07063 | 0.07063 | 0.99948 | -0.0070532 | 0.9986 | 0.00012854 | 32.1046
5 | 2.3123 | 1.105 | -2.3117 | -1.107 | 0.00069172 | -0.0020396 | 0.074097 | 0.074125 | 0.074125 | 0.99844 | -0.013869 | 0.99816 | -0.011334 | 33.6932
6 | 2.2359 | 1.0713 | -2.235 | -1.0742 | 0.00092326 | -0.0029229 | 0.071704 | 0.071744 | 0.071744 | 0.99816 | -0.011334 | 0.99778 | -0.0078095 | 32.6107
7 | 0.075738 | 0.035709 | -0.075738 | -0.036682 | 3.2184e-07 | -0.00097296 | 0.0024217 | 0.0024338 | 0.0024338 | 0.99816 | -0.011334 | 0.99815 | -0.011298 | 1.1063
8 | 0.24041 | 0.11529 | -0.2404 | -0.11643 | 3.8429e-06 | -0.0011466 | 0.0077138 | 0.0077282 | 0.0077282 | 0.99778 | -0.0078095 | 0.99776 | -0.0076718 | 3.5128
9 | 1.9946 | 0.95893 | -1.9943 | -0.96007 | 0.00028348 | -0.0011466 | 0.06403 | 0.064045 | 0.064045 | 0.99778 | -0.0078095 | 0.99764 | -0.0065897 | 29.1114
10 | -2.306 | -1.0562 | 2.3065 | 1.0546 | 0.00053696 | -0.0016161 | 0.073392 | 0.073371 | 0.073392 | 0.99764 | 0.0013415 | 0.99786 | -0.00043427 | 33.3601
11 | 2.306 | 1.0562 | -2.3043 | -1.0614 | 0.0017253 | -0.0051804 | 0.073392 | 0.073461 | 0.073461 | 0.99764 | 0.0013415 | 0.99694 | 0.0071029 | 33.3913
12 | -2.4841 | -1.1406 | 2.4851 | 1.1411 | 0.000993 | 0.000516 | 0.079078 | 0.079077 | 0.079078 | 0.99786 | -0.00043427 | 0.99828 | 0.0027277 | 37.6564
13 | 2.3043 | 1.0614 | -2.3036 | -1.061 | 0.00071318 | 0.00035874 | 0.073461 | 0.073462 | 0.073462 | 0.99694 | 0.0071029 | 0.99661 | 0.0046776 | 34.9819
14 | 2.1555 | 0.98931 | -2.155 | -0.99092 | 0.00046465 | -0.0016103 | 0.068697 | 0.068718 | 0.068718 | 0.99661 | 0.0046776 | 0.99641 | 0.0063378 | 31.2353
15 | 2.155 | 0.99092 | -2.1546 | -0.99214 | 0.00035318 | -0.0012228 | 0.068718 | 0.068734 | 0.068734 | 0.99641 | 0.0063378 | 0.99626 | 0.007605 | 31.2426
16 | 2.1546 | 0.99214 | -2.1538 | -0.99172 | 0.00086237 | 0.00041882 | 0.068734 | 0.068735 | 0.068735 | 0.99626 | 0.007605 | 0.99583 | 0.0044654 | 32.7311
17 | 2.0768 | 0.95441 | -2.0761 | -0.9567 | 0.00061123 | -0.0022865 | 0.066255 | 0.066285 | 0.066285 | 0.99583 | 0.0044654 | 0.99556 | 0.0067418 | 30.1294
18 | -0.35926 | -0.174 | 0.35928 | 0.17394 | 1.3121e-05 | -5.6772e-05 | 0.011577 | 0.011576 | 0.011577 | 0.99536 | 0.0078339 | 0.99539 | 0.0080748 | 5.5129
19 | -1.7414 | -0.79808 | 1.7417 | 0.79642 | 0.00030409 | -0.0016568 | 0.055553 | 0.055532 | 0.055553 | 0.99539 | 0.0080748 | 0.99556 | 0.0067418 | 25.2513
20 | 1.3821 | 0.62414 | -1.3813 | -0.63161 | 0.00084536 | -0.0074733 | 0.04398 | 0.044073 | 0.044073 | 0.99539 | 0.0080748 | 0.99482 | 0.01266 | 20.033
21 | 0.33446 | 0.16028 | -0.33445 | -0.16176 | 9.7076e-06 | -0.0014824 | 0.010754 | 0.010773 | 0.010773 | 0.99556 | 0.0067418 | 0.99553 | 0.0069913 | 4.8968
22 | 0.26199 | 0.1265 | -0.26199 | -0.12689 | 1.5787e-06 | -0.00039138 | 0.0084422 | 0.0084471 | 0.0084471 | 0.99482 | 0.01266 | 0.99482 | 0.012712 | 3.8396
23 | 1.1193 | 0.50511 | -1.1189 | -0.50986 | 0.00034821 | -0.0047416 | 0.035633 | 0.035691 | 0.035691 | 0.99482 | 0.01266 | 0.99453 | 0.014979 | 16.2231
24 | 0.33445 | 0.16176 | -0.33445 | -0.16198 | 1.4686e-06 | -0.0002238 | 0.010773 | 0.010776 | 0.010776 | 0.99553 | 0.0069913 | 0.99553 | 0.0070295 | 4.8981
25 | 0.1135 | 0.052665 | -0.1135 | -0.05497 | 1.7326e-06 | -0.0023049 | 0.0036319 | 0.0036606 | 0.0036606 | 0.99453 | 0.014979 | 0.99452 | 0.015106 | 1.6639
26 | 1.0054 | 0.45719 | -1.0047 | -0.46972 | 0.00074508 | -0.012533 | 0.032059 | 0.032214 | 0.032214 | 0.99453 | 0.014979 | 0.99384 | 0.020742 | 14.6427
27 | 0.7327 | 0.33972 | -0.73255 | -0.34456 | 0.00015249 | -0.0048364 | 0.023459 | 0.023519 | 0.023519 | 0.99384 | 0.020742 | 0.99365 | 0.02241 | 10.6903
28 | 0.27197 | 0.13 | -0.27196 | -0.13167 | 7.2601e-06 | -0.0016667 | 0.0087558 | 0.0087768 | 0.0087768 | 0.99384 | 0.020742 | 0.99381 | 0.020971 | 3.9894
29 | -0.1746 | -0.084561 | 0.1746 | 0.084512 | 2.4112e-06 | -4.8745e-05 | 0.0056351 | 0.0056345 | 0.0056351 | 0.9938 | 0.02088 | 0.99381 | 0.020971 | 2.6834
30 | 1.2936 | 0.62293 | -1.2935 | -0.62373 | 8.0054e-05 | -0.00080141 | 0.041547 | 0.041557 | 0.041557 | 0.99757 | -0.0058771 | 0.99751 | -0.005344 | 18.8897
31 | -1.6667 | -0.80364 | 1.6668 | 0.80282 | 0.00013785 | -0.00081512 | 0.053544 | 0.053533 | 0.053544 | 0.99757 | -0.0058771 | 0.99764 | -0.0065897 | 24.3382
32 | 1.1377 | 0.5483 | -1.1374 | -0.54826 | 0.00034804 | 4.437e-05 | 0.03655 | 0.036552 | 0.036552 | 0.99751 | -0.005344 | 0.99719 | -0.007398 | 17.4057
33 | 0.32749 | 0.15725 | -0.32749 | -0.1576 | 2.2112e-06 | -0.00035539 | 0.010512 | 0.010516 | 0.010516 | 0.99764 | -0.0065897 | 0.99764 | -0.0065318 | 4.7802
34 | -0.28121 | -0.1362 | 0.28122 | 0.13581 | 1.7825e-06 | -0.00038677 | 0.0090475 | 0.0090426 | 0.0090475 | 0.99696 | -0.0067838 | 0.99697 | -0.0068389 | 4.1125
35 | -0.41856 | -0.20233 | 0.4186 | 0.20221 | 3.8669e-05 | -0.00011793 | 0.013461 | 0.013459 | 0.013461 | 0.99697 | -0.0068389 | 0.99706 | -0.0062247 | 6.4101
36 | 1.1374 | 0.54826 | -1.1372 | -0.55026 | 0.00015415 | -0.0020045 | 0.036552 | 0.036578 | 0.036578 | 0.99719 | -0.007398 | 0.99706 | -0.0062247 | 16.6262
37 | 0.32749 | 0.1576 | -0.32748 | -0.15861 | 6.2381e-06 | -0.001001 | 0.010516 | 0.010529 | 0.010529 | 0.99764 | -0.0065318 | 0.99762 | -0.006367 | 4.7859
38 | -0.17394 | -0.084242 | 0.17395 | 0.083946 | 1.4197e-05 | -0.00029577 | 0.0055845 | 0.0055806 | 0.0055845 | 0.99904 | -0.0046838 | 0.99912 | -0.0041421 | 2.6593
39 | 2.6183 | 1.1989 | -2.6177 | -1.2001 | 0.00053284 | -0.0012156 | 0.083202 | 0.083219 | 0.083219 | 0.99912 | -0.0041421 | 0.99893 | -0.0025851 | 37.8268
40 | -0.10506 | -0.050883 | 0.10506 | 0.048741 | 1.3624e-06 | -0.0021415 | 0.003378 | 0.0033515 | 0.003378 | 0.99755 | -0.0004339 | 0.99756 | -0.00054157 | 1.5355
41 | -0.10506 | -0.048741 | 0.10511 | 0.04597 | 4.6674e-05 | -0.0027708 | 0.0033515 | 0.0033182 | 0.0033515 | 0.99756 | -0.00054157 | 0.99804 | 0.0031753 | 1.596
42 | -0.10511 | -0.04597 | 0.10511 | 0.045169 | 4.9379e-07 | -0.00080102 | 0.0033182 | 0.003309 | 0.0033182 | 0.99804 | 0.0031753 | 0.99804 | 0.0031442 | 1.5083
43 | -0.089327 | -0.043263 | 0.089327 | 0.042093 | 5.3437e-07 | -0.00117 | 0.0028652 | 0.0028506 | 0.0028652 | 0.99999 | 5.0548e-05 | 1 | 0 | 1.3024
44 | 7.9259 | 3.6835 | -7.9246 | -3.6871 | 0.0013597 | -0.0035759 | 0.2523 | 0.25236 | 0.25236 | 1 | 0 | 0.99982 | -0.00079288 | 39.5543
45 | -0.23136 | -0.11205 | 0.23139 | 0.11167 | 3.4444e-05 | -0.00038676 | 0.0074708 | 0.0074657 | 0.0074708 | 0.99331 | 0.023015 | 0.99347 | 0.024003 | 3.5575
46 | -0.58791 | -0.28173 | 0.58802 | 0.2762 | 0.00011267 | -0.0055303 | 0.018943 | 0.018874 | 0.018943 | 0.99347 | 0.024003 | 0.99365 | 0.02241 | 8.6106
47 | 0.35652 | 0.17006 | -0.35649 | -0.17019 | 2.8723e-05 | -0.00012616 | 0.011478 | 0.011479 | 0.011479 | 0.99347 | 0.024003 | 0.99338 | 0.023443 | 5.4664
48 | -0.14452 | -0.069994 | 0.14452 | 0.068364 | 2.0015e-06 | -0.0016305 | 0.0046652 | 0.0046447 | 0.0046652 | 0.99363 | 0.022527 | 0.99365 | 0.02241 | 2.1205
49 | -2.4851 | -1.1411 | 2.486 | 1.1388 | 0.00090116 | -0.0023031 | 0.079077 | 0.079046 | 0.079077 | 0.99828 | 0.0027277 | 0.99862 | -5.2801e-05 | 35.9441
50 | -0.2914 | -0.1354 | 0.29141 | 0.13447 | 4.5146e-06 | -0.00093091 | 0.009294 | 0.0092827 | 0.009294 | 0.99804 | 0.0031442 | 0.99806 | 0.0030226 | 4.2245
51 | -0.29141 | -0.13447 | 0.29157 | 0.098879 | 0.00016479 | -0.035587 | 0.0092827 | 0.0089003 | 0.0092827 | 0.99806 | 0.0030226 | 0.9986 | 0.00012854 | 4.2194
52 | 2.4869 | 1.1367 | -2.486 | -1.1388 | 0.0008257 | -0.0021136 | 0.079018 | 0.079046 | 0.079046 | 0.99893 | -0.0025851 | 0.99862 | -5.2801e-05 | 35.93
53 | -0.35648 | -0.17113 | 0.35649 | 0.17019 | 7.0886e-06 | -0.00094627 | 0.011491 | 0.011479 | 0.011491 | 0.99337 | 0.023611 | 0.99338 | 0.023443 | 5.2233
54 | 0.10245 | 0.048101 | -0.10242 | -0.049606 | 2.5042e-05 | -0.0015057 | 0.003289 | 0.0033081 | 0.0033081 | 0.99337 | 0.023611 | 0.99311 | 0.021906 | 1.5753
55 | -1.9276 | -0.92362 | 1.9278 | 0.92288 | 0.00016803 | -0.00073498 | 0.061795 | 0.061785 | 0.061795 | 0.99852 | 0.00086913 | 0.9986 | 0.00012854 | 28.0887
56 | 1.8572 | 0.8895 | -1.857 | -0.89029 | 0.00016656 | -0.00078843 | 0.059532 | 0.059543 | 0.059543 | 0.99852 | 0.00086913 | 0.99844 | 0.0016321 | 27.0649
57 | 1.857 | 0.89029 | -1.8565 | -0.89286 | 0.00054263 | -0.0025655 | 0.059543 | 0.059577 | 0.059577 | 0.99844 | 0.0016321 | 0.99817 | 0.0041297 | 27.0804
58 | 1.8565 | 0.89286 | -1.8553 | -0.89855 | 0.0012073 | -0.0056915 | 0.059577 | 0.059653 | 0.059653 | 0.99817 | 0.0041297 | 0.99756 | 0.0097527 | 27.115

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 8.0983 | 3.7695

## res_load
| p_mw | q_mvar
0 | 0.22234 | 0.10768
1 | 0.075738 | 0.036682
2 | 0.1776 | 0.086017
3 | 0.1481 | 0.071728
4 | 0.077026 | 0.037306
5 | 0.35926 | 0.174
6 | 0.26199 | 0.12689
7 | 0.1135 | 0.05497
8 | 0.1746 | 0.084561
9 | 0.097361 | 0.047154
10 | 0.37312 | 0.18071
11 | 0.15574 | 0.075427
12 | 0.28121 | 0.1362
13 | 0.13734 | 0.066519
14 | 0.71864 | 0.34805
15 | 0.2404 | 0.11643
16 | 0.32748 | 0.15861
17 | 0.17394 | 0.084242
18 | 0.33445 | 0.16198
19 | 0.10506 | 0.050883
20 | 0.089327 | 0.043263
21 | 0.069085 | 0.033459
22 | 0.23136 | 0.11205
23 | 0.14452 | 0.069994
24 | 0.1863 | 0.090227
25 | 0.13087 | 0.063384
26 | 0.25403 | 0.12303
27 | 0.10242 | 0.049606
28 | 0.070445 | 0.034118
29 | 0.37056 | 0.17947
30 | 1.8553 | 0.89855

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1