## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_72_2_node_148 | 20 | n |  | TRUE
1 | bus_MV_72_2_node_77 | 20 | n |  | TRUE
2 | bus_MV_72_2_node_149 | 20 | n |  | TRUE
3 | bus_MV_72_2_node_103 | 20 | n |  | TRUE
4 | bus_MV_72_2_node_150 | 20 | n |  | TRUE
5 | bus_MV_72_2_node_108 | 20 | n |  | TRUE
6 | bus_MV_72_2_node_113 | 20 | n |  | TRUE
7 | bus_MV_72_2_node_154 | 20 | n |  | TRUE
8 | bus_MV_72_2_node_88 | 20 | n |  | TRUE
9 | bus_MV_72_2_node_155 | 20 | n |  | TRUE
10 | bus_MV_72_2_node_86 | 20 | n |  | TRUE
11 | bus_MV_72_2_node_156 | 20 | n |  | TRUE
12 | bus_MV_72_2_node_102 | 20 | n |  | TRUE
13 | bus_MV_72_2_node_157 | 20 | n |  | TRUE
14 | bus_MV_72_2_node_167 | 20 | n |  | TRUE
15 | bus_MV_72_2_node_110 | 20 | n |  | TRUE
16 | bus_MV_72_2_node_168 | 20 | n |  | TRUE
17 | bus_MV_72_2_node_89 | 20 | n |  | TRUE
18 | bus_MV_72_2_node_169 | 20 | n |  | TRUE
19 | bus_MV_72_2_node_170 | 20 | n |  | TRUE
20 | bus_MV_72_2_node_101 | 20 | n |  | TRUE
21 | bus_MV_72_2_node_72 | 20 | n |  | TRUE
22 | bus_MV_72_2_node_73 | 20 | n |  | TRUE
23 | bus_MV_72_2_node_75 | 20 | n |  | TRUE
24 | bus_MV_72_2_node_76 | 20 | n |  | TRUE
25 | bus_MV_72_2_node_79 | 20 | n |  | TRUE
26 | bus_MV_72_2_node_96 | 20 | n |  | TRUE
27 | bus_MV_72_2_node_100 | 20 | n |  | TRUE
28 | bus_MV_72_2_node_111 | 20 | n |  | TRUE
29 | bus_MV_72_2_node_78 | 20 | n |  | TRUE
30 | bus_MV_72_2_node_80 | 20 | n |  | TRUE
31 | bus_MV_72_2_node_94 | 20 | n |  | TRUE
32 | bus_MV_72_2_node_82 | 20 | n |  | TRUE
33 | bus_MV_72_2_node_84 | 20 | n |  | TRUE
34 | bus_MV_72_2_node_85 | 20 | n |  | TRUE
35 | bus_MV_72_2_node_87 | 20 | n |  | TRUE
36 | bus_MV_72_2_node_92 | 20 | n |  | TRUE
37 | bus_MV_72_2_node_98 | 20 | n |  | TRUE
38 | bus_MV_72_2_node_90 | 20 | n |  | TRUE
39 | bus_MV_72_2_node_91 | 20 | n |  | TRUE
40 | bus_MV_72_2_node_93 | 20 | n |  | TRUE
41 | bus_MV_72_2_node_95 | 20 | n |  | TRUE
42 | bus_MV_72_2_node_97 | 20 | n |  | TRUE
43 | bus_MV_72_2_node_99 | 20 | n |  | TRUE
44 | bus_MV_72_2_node_105 | 20 | n |  | TRUE
45 | bus_MV_72_2_node_106 | 20 | n |  | TRUE
46 | bus_MV_72_2_node_107 | 20 | n |  | TRUE
47 | bus_MV_72_2_node_109 | 20 | n |  | TRUE
48 | bus_MV_72_2_node_112 | 20 | n |  | TRUE
49 | bus_HV_72_2_node_170 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_72_2_load_77 | 1 | 0.073279 | 0.03549 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_72_2_load_149 | 2 | 0.067515 | 0.032699 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_72_2_load_103 | 3 | 0.21636 | 0.10479 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_72_2_load_150 | 4 | 0.15063 | 0.072953 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_72_2_load_154 | 7 | 0.22294 | 0.10798 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_72_2_load_156 | 11 | 0.39777 | 0.19265 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_72_2_load_157 | 13 | 0.21832 | 0.10574 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_72_2_load_167 | 14 | 0.22061 | 0.10685 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_72_2_load_168 | 16 | 0.3436 | 0.16642 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_72_2_load_170 | 19 | 0.16806 | 0.081397 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_72_2_load_72 | 21 | 0.30343 | 0.14696 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_72_2_load_96 | 26 | 0.24323 | 0.1178 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_72_2_load_100 | 27 | 0.27733 | 0.13432 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_72_2_load_111 | 28 | 0.26922 | 0.13039 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_72_2_load_80 | 30 | 0.28137 | 0.13627 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_72_2_load_82 | 32 | 0.34084 | 0.16507 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_72_2_load_92 | 36 | 0.22928 | 0.11105 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_72_2_load_91 | 39 | 0.3086 | 0.14946 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_72_2_load_93 | 40 | 0.41384 | 0.20043 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_72_2_load_97 | 42 | 0.26387 | 0.1278 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_72_2_load_99 | 43 | 0.18471 | 0.089458 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_72_2_load_105 | 44 | 0.1176 | 0.056957 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_72_2_load_109 | 47 | 0.20387 | 0.098738 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_72_2_line_0 |  | 0 | 1 | 2.7248 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_72_2_line_1 |  | 0 | 2 | 0.41973 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_72_2_line_2 |  | 1 | 29 | 0.23773 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_72_2_line_3 |  | 2 | 3 | 1.7974 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_72_2_line_4 |  | 4 | 5 | 0.91119 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_72_2_line_5 |  | 4 | 6 | 0.005599 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_72_2_line_6 |  | 5 | 45 | 0.57177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_72_2_line_7 |  | 6 | 48 | 0.22251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_72_2_line_8 |  | 7 | 8 | 0.039186 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_72_2_line_9 |  | 8 | 37 | 0.25128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_72_2_line_10 |  | 8 | 33 | 1.0696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_72_2_line_11 |  | 8 | 35 | 0.44765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_72_2_line_12 |  | 9 | 10 | 0.30058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_72_2_line_13 |  | 9 | 11 | 0.050695 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_72_2_line_14 |  | 10 | 13 | 0.092871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_72_2_line_15 |  | 11 | 12 | 0.03462 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_72_2_line_16 |  | 12 | 20 | 0.56351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_72_2_line_17 |  | 14 | 15 | 0.026802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_72_2_line_18 |  | 15 | 43 | 0.63893 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_72_2_line_19 |  | 15 | 46 | 1.2795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_72_2_line_20 |  | 16 | 17 | 0.026921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_72_2_line_21 |  | 16 | 18 | 0.18273 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_72_2_line_22 |  | 17 | 38 | 0.078072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_72_2_line_23 |  | 17 | 34 | 0.11665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_72_2_line_24 |  | 18 | 19 | 0.003579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_72_2_line_25 |  | 19 | 20 | 0.39263 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_72_2_line_26 |  | 20 | 27 | 0.04823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_72_2_line_27 |  | 21 | 22 | 0.043585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_72_2_line_28 |  | 22 | 23 | 1.3455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_72_2_line_29 |  | 22 | 24 | 0.51456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_72_2_line_30 |  | 23 | 25 | 0.87677 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_72_2_line_31 |  | 23 | 26 | 0.011811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_72_2_line_32 |  | 23 | 27 | 0.3542 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_72_2_line_33 |  | 24 | 28 | 0.10588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_72_2_line_34 |  | 25 | 29 | 1.3615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_72_2_line_35 |  | 28 | 48 | 0.034107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_72_2_line_36 |  | 30 | 31 | 0.54931 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_72_2_line_37 |  | 31 | 41 | 0.81847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_72_2_line_38 |  | 31 | 40 | 0.011495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_72_2_line_39 |  | 32 | 33 | 0.13305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_72_2_line_40 |  | 32 | 34 | 0.18201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_72_2_line_41 |  | 35 | 36 | 0.03621 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_72_2_line_42 |  | 37 | 42 | 0.1501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_72_2_line_43 |  | 38 | 39 | 0.066528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_72_2_line_44 |  | 41 | 42 | 0.16357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_72_2_line_45 |  | 44 | 45 | 0.078389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_72_2_line_46 |  | 45 | 46 | 0.94768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_72_2_line_47 |  | 46 | 47 | 0.17265 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_72_2_trafo_170 | 25 MVA 110/20 kV | 49 | 19 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2708737.9035 | 1107383.3635
1 | 2706593.449 | 1109064.419
2 | 2708618.7615 | 1106993.2523
3 | 2707288.3615 | 1105784.7119
4 | 2703920.9761 | 1108665.3102
5 | 2703231.509 | 1108069.5713
6 | 2703922.7795 | 1108670.6111
7 | 2707200.1375 | 1110225.0838
8 | 2707208.0025 | 1110263.3142
9 | 2705852.8791 | 1110123.0136
10 | 2706113.8098 | 1110242.0494
11 | 2705809.6116 | 1110149.4314
12 | 2705818.9777 | 1110182.7607
13 | 2706101.5144 | 1110299.3379
14 | 2702699.1848 | 1107137.7113
15 | 2702673.4731 | 1107137.6318
16 | 2705998.5166 | 1109818.1601
17 | 2706008.8574 | 1109843.0235
18 | 2705823.7622 | 1109764.7524
19 | 2705821.3189 | 1109762.1303
20 | 2705442.1069 | 1109863.915
21 | 2704539.576 | 1108879.3186
22 | 2704502.1903 | 1108856.7823
23 | 2705435.999 | 1109463.5066
24 | 2704175.8734 | 1108723.2295
25 | 2706110.3249 | 1109735.4614
26 | 2705428.9124 | 1109454.044
27 | 2705434.8792 | 1109817.7041
28 | 2704101.8507 | 1108735.5892
29 | 2706384.1799 | 1109177.2078
30 | 2708363.5846 | 1111209.5981
31 | 2708370.947 | 1110660.3384
32 | 2706215.5297 | 1110020.5644
33 | 2706344.6404 | 1110004.1937
34 | 2706056.0996 | 1109933.7856
35 | 2706859.3643 | 1110294.9607
36 | 2706884.5282 | 1110320.9987
37 | 2707431.5937 | 1110347.4247
38 | 2706057.8881 | 1109885.0187
39 | 2706099.1567 | 1109832.9734
40 | 2708363.8044 | 1110651.316
41 | 2707676.2362 | 1110484.9074
42 | 2707532.6074 | 1110458.1754
43 | 2702315.1602 | 1106608.6325
44 | 2703301.8048 | 1107907.3195
45 | 2703292.8012 | 1107958.3544
46 | 2703158.1682 | 1107412.3599
47 | 2702986.5357 | 1107431.0679
48 | 2704074.0588 | 1108716.0999
49 | 2705821.3189 | 1109762.1303

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99371 | -0.045689 | 0 | 0
1 | 0.99518 | -0.033042 | 0.073279 | 0.03549
2 | 0.99356 | -0.044435 | 0.067515 | 0.032699
3 | 0.9928 | -0.049363 | 0.21636 | 0.10479
4 | 0.9927 | -0.014209 | 0.15063 | 0.072953
5 | 0.99146 | -0.027843 | 0 | 0
6 | 0.9927 | -0.014243 | 0 | 0
7 | 0.99626 | 0.014672 | 0.22294 | 0.10798
8 | 0.99627 | 0.014568 | 0 | 0
9 | 0.99733 | -0.018216 | 0 | 0
10 | 0.99724 | -0.017538 | 0 | 0
11 | 0.99735 | -0.018041 | 0.39777 | 0.19265
12 | 0.99739 | -0.017754 | 0 | 0
13 | 0.99722 | -0.0173 | 0.21832 | 0.10574
14 | 0.98954 | -0.015629 | 0.22061 | 0.10685
15 | 0.98955 | -0.0157 | 0 | 0
16 | 0.99915 | -0.0065839 | 0.3436 | 0.16642
17 | 0.99908 | -0.0060646 | 0 | 0
18 | 0.99999 | 8.365e-05 | 0 | 0
19 | 1 | 0 | -5.3874 | -2.3096
20 | 0.99783 | -0.021345 | 0 | 0
21 | 0.99386 | -0.020898 | 0.30343 | 0.14696
22 | 0.99388 | -0.021056 | 0 | 0
23 | 0.99634 | -0.035325 | 0 | 0
24 | 0.99314 | -0.016712 | 0 | 0
25 | 0.99595 | -0.034811 | 0 | 0
26 | 0.99633 | -0.03529 | 0.24323 | 0.1178
27 | 0.99769 | -0.020589 | 0.27733 | 0.13432
28 | 0.99298 | -0.015767 | 0.26922 | 0.13039
29 | 0.99534 | -0.031692 | 0 | 0
30 | 0.99462 | 0.024018 | 0.28137 | 0.13627
31 | 0.99492 | 0.02592 | 0 | 0
32 | 0.99842 | -0.001264 | 0.34084 | 0.16507
33 | 0.99818 | 0.00037583 | 0 | 0
34 | 0.99882 | -0.0042065 | 0 | 0
35 | 0.99614 | 0.015651 | 0 | 0
36 | 0.99613 | 0.01555 | 0.22928 | 0.11105
37 | 0.99597 | 0.016979 | 0 | 0
38 | 0.99905 | -0.0057883 | 0 | 0
39 | 0.99902 | -0.0055456 | 0.3086 | 0.14946
40 | 0.99491 | 0.025978 | 0.41384 | 0.20043
41 | 0.99564 | 0.019604 | 0 | 0
42 | 0.99579 | 0.018465 | 0.26387 | 0.1278
43 | 0.98932 | -0.017178 | 0.18471 | 0.089458
44 | 0.99093 | -0.024984 | 0.1176 | 0.056957
45 | 0.99094 | -0.025092 | 0 | 0
46 | 0.99021 | -0.020674 | 0 | 0
47 | 0.99014 | -0.021109 | 0.20387 | 0.098738
48 | 0.99295 | -0.01557 | 0 | 0
49 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.28408 | -0.12559 | 0.28447 | 0.12262 | 0.00039362 | -0.0029703 | 0.0090231 | 0.0089857 | 0.0090231 | 0.99371 | -0.045689 | 0.99518 | -0.033042 | 4.2967
1 | 0.28408 | 0.12559 | -0.28403 | -0.13547 | 4.622e-05 | -0.0098806 | 0.0090231 | 0.0091431 | 0.0091431 | 0.99371 | -0.045689 | 0.99356 | -0.044435 | 4.156
2 | -0.35775 | -0.15811 | 0.35781 | 0.15786 | 5.4507e-05 | -0.00024698 | 0.011346 | 0.011342 | 0.011346 | 0.99518 | -0.033042 | 0.99534 | -0.031692 | 5.4027
3 | 0.21652 | 0.10277 | -0.21636 | -0.10479 | 0.00015588 | -0.0020189 | 0.0069636 | 0.0069902 | 0.0069902 | 0.99356 | -0.044435 | 0.9928 | -0.049363 | 3.3287
4 | 0.72884 | 0.28287 | -0.728 | -0.28342 | 0.00083955 | -0.00054475 | 0.022735 | 0.022746 | 0.022746 | 0.9927 | -0.014209 | 0.99146 | -0.027843 | 10.8315
5 | -0.87947 | -0.35582 | 0.87947 | 0.35569 | 5.689e-06 | -0.00013005 | 0.027589 | 0.027587 | 0.027589 | 0.9927 | -0.014209 | 0.9927 | -0.014243 | 12.5403
6 | 0.728 | 0.28342 | -0.7276 | -0.29671 | 0.00039742 | -0.013294 | 0.022746 | 0.022891 | 0.022891 | 0.99146 | -0.027843 | 0.99094 | -0.025092 | 10.4049
7 | -0.87947 | -0.35569 | 0.8797 | 0.35052 | 0.0002256 | -0.0051697 | 0.027587 | 0.027531 | 0.027587 | 0.9927 | -0.014243 | 0.99295 | -0.01557 | 12.5397
8 | -0.22294 | -0.10798 | 0.22295 | 0.10705 | 2.6908e-06 | -0.00092784 | 0.0071778 | 0.0071661 | 0.0071778 | 0.99626 | 0.014672 | 0.99627 | 0.014568 | 3.2626
9 | 0.96032 | 0.43124 | -0.96001 | -0.4371 | 0.00031283 | -0.0058602 | 0.030503 | 0.030574 | 0.030574 | 0.99627 | 0.014568 | 0.99597 | 0.016979 | 13.8971
10 | -1.4126 | -0.6387 | 1.4154 | 0.61415 | 0.002862 | -0.024547 | 0.04492 | 0.044622 | 0.04492 | 0.99627 | 0.014568 | 0.99818 | 0.00037583 | 20.418
11 | 0.22931 | 0.10041 | -0.22928 | -0.111 | 3.1991e-05 | -0.010598 | 0.0072535 | 0.0073822 | 0.0073822 | 0.99627 | 0.014568 | 0.99614 | 0.015651 | 3.3555
12 | 0.21835 | 0.096402 | -0.21833 | -0.10353 | 1.9388e-05 | -0.007132 | 0.0069086 | 0.0069946 | 0.0069946 | 0.99733 | -0.018216 | 0.99724 | -0.017538 | 3.1794
13 | -0.21835 | -0.096402 | 0.21835 | 0.096345 | 4.3105e-06 | -5.7498e-05 | 0.0069086 | 0.0069079 | 0.0069086 | 0.99733 | -0.018216 | 0.99735 | -0.018041 | 3.2898
14 | 0.21833 | 0.10353 | -0.21832 | -0.10574 | 6.0896e-06 | -0.0022033 | 0.0069946 | 0.0070222 | 0.0070222 | 0.99724 | -0.017538 | 0.99722 | -0.0173 | 3.1919
15 | -0.61612 | -0.289 | 0.61615 | 0.28897 | 2.3932e-05 | -2.6122e-05 | 0.019698 | 0.019697 | 0.019698 | 0.99735 | -0.018041 | 0.99739 | -0.017754 | 9.3798
16 | -0.61615 | -0.28897 | 0.61644 | 0.27567 | 0.00028946 | -0.013304 | 0.019697 | 0.019536 | 0.019697 | 0.99739 | -0.017754 | 0.99783 | -0.021345 | 8.9532
17 | -0.22061 | -0.10685 | 0.22062 | 0.10622 | 1.8277e-06 | -0.00062608 | 0.007151 | 0.0071431 | 0.007151 | 0.98954 | -0.015629 | 0.98955 | -0.0157 | 3.2505
18 | 0.18475 | 0.088737 | -0.18471 | -0.089458 | 4.0759e-05 | -0.00072119 | 0.005979 | 0.0059884 | 0.0059884 | 0.98955 | -0.0157 | 0.98932 | -0.017178 | 2.8516
19 | -0.40536 | -0.19496 | 0.40565 | 0.16511 | 0.00028596 | -0.029849 | 0.013122 | 0.012768 | 0.013122 | 0.98955 | -0.0157 | 0.99021 | -0.020674 | 5.9646
20 | 2.0666 | 0.91484 | -2.0665 | -0.91543 | 0.00015326 | -0.00059617 | 0.065298 | 0.065305 | 0.065305 | 0.99915 | -0.0065839 | 0.99908 | -0.0060646 | 29.6843
21 | -2.4102 | -1.0813 | 2.4121 | 1.0822 | 0.0018965 | 0.00096993 | 0.076323 | 0.07632 | 0.076323 | 0.99915 | -0.0065839 | 0.99999 | 8.365e-05 | 36.3442
22 | 0.30862 | 0.14602 | -0.30861 | -0.14788 | 1.0167e-05 | -0.0018575 | 0.009865 | 0.0098881 | 0.0098881 | 0.99908 | -0.0060646 | 0.99905 | -0.0057883 | 4.4946
23 | 1.7579 | 0.76941 | -1.7574 | -0.77205 | 0.00047898 | -0.0026371 | 0.055444 | 0.055476 | 0.055476 | 0.99908 | -0.0060646 | 0.99882 | -0.0042065 | 25.2165
24 | -2.4121 | -1.0822 | 2.4122 | 1.0821 | 2.783e-05 | -7.7196e-05 | 0.07632 | 0.076319 | 0.07632 | 0.99999 | 8.365e-05 | 1 | 0 | 34.691
25 | 2.9613 | 1.217 | -2.9553 | -1.2137 | 0.0059759 | 0.0032754 | 0.092422 | 0.092427 | 0.092427 | 1 | 0 | 0.99783 | -0.021345 | 44.013
26 | 2.3389 | 0.93802 | -2.3385 | -0.93907 | 0.00034227 | -0.0010449 | 0.072903 | 0.072916 | 0.072916 | 0.99783 | -0.021345 | 0.99769 | -0.020589 | 33.1435
27 | -0.30343 | -0.14696 | 0.30344 | 0.14593 | 5.5724e-06 | -0.0010263 | 0.0097926 | 0.0097796 | 0.0097926 | 0.99386 | -0.020898 | 0.99388 | -0.021056 | 4.4512
28 | -1.4535 | -0.61175 | 1.4572 | 0.58105 | 0.0037393 | -0.030702 | 0.045803 | 0.045453 | 0.045803 | 0.99388 | -0.021056 | 0.99634 | -0.035325 | 20.8197
29 | 1.15 | 0.46582 | -1.1491 | -0.47768 | 0.00089551 | -0.011861 | 0.036039 | 0.036173 | 0.036173 | 0.99388 | -0.021056 | 0.99314 | -0.016712 | 16.4423
30 | 0.35817 | 0.10497 | -0.35803 | -0.1257 | 0.00013913 | -0.020732 | 0.010814 | 0.010999 | 0.010999 | 0.99634 | -0.035325 | 0.99595 | -0.034811 | 4.9994
31 | 0.24323 | 0.11752 | -0.24323 | -0.1178 | 9.6635e-07 | -0.00027965 | 0.0078268 | 0.0078304 | 0.0078304 | 0.99634 | -0.035325 | 0.99633 | -0.03529 | 3.5593
32 | -2.0586 | -0.80355 | 2.0612 | 0.80475 | 0.002587 | 0.0012001 | 0.064029 | 0.064024 | 0.064029 | 0.99634 | -0.035325 | 0.99769 | -0.020589 | 30.4898
33 | 1.1491 | 0.47768 | -1.149 | -0.48012 | 0.0001851 | -0.0024381 | 0.036173 | 0.036201 | 0.036201 | 0.99314 | -0.016712 | 0.99298 | -0.015767 | 16.455
34 | 0.35803 | 0.1257 | -0.35781 | -0.15786 | 0.00022646 | -0.032158 | 0.010999 | 0.011342 | 0.011342 | 0.99595 | -0.034811 | 0.99534 | -0.031692 | 5.1557
35 | 0.87973 | 0.34973 | -0.8797 | -0.35052 | 3.45e-05 | -0.00079269 | 0.027522 | 0.027531 | 0.027531 | 0.99298 | -0.015767 | 0.99295 | -0.01557 | 12.5139
36 | -0.28137 | -0.13627 | 0.28145 | 0.13567 | 8.0507e-05 | -0.00059849 | 0.0090738 | 0.0090656 | 0.0090738 | 0.99462 | 0.024018 | 0.99492 | 0.02592 | 4.3208
37 | -0.6953 | -0.33584 | 0.69584 | 0.31664 | 0.00054256 | -0.019197 | 0.022404 | 0.022166 | 0.022404 | 0.99492 | 0.02592 | 0.99564 | 0.019604 | 10.1837
38 | 0.41385 | 0.20016 | -0.41384 | -0.20043 | 2.731e-06 | -0.00027086 | 0.013338 | 0.013342 | 0.013342 | 0.99492 | 0.02592 | 0.99491 | 0.025978 | 6.0645
39 | 1.4158 | 0.61109 | -1.4154 | -0.61415 | 0.00035337 | -0.003061 | 0.044586 | 0.044622 | 0.044622 | 0.99842 | -0.001264 | 0.99818 | 0.00037583 | 20.2827
40 | -1.7566 | -0.77616 | 1.7574 | 0.77205 | 0.00074851 | -0.0041118 | 0.055527 | 0.055476 | 0.055527 | 0.99842 | -0.001264 | 0.99882 | -0.0042065 | 25.2394
41 | 0.22928 | 0.111 | -0.22928 | -0.11105 | 3.5162e-06 | -4.0692e-05 | 0.0073822 | 0.0073827 | 0.0073827 | 0.99614 | 0.015651 | 0.99613 | 0.01555 | 3.5156
42 | 0.96001 | 0.4371 | -0.95982 | -0.4406 | 0.00018757 | -0.0034987 | 0.030574 | 0.030616 | 0.030616 | 0.99597 | 0.016979 | 0.99579 | 0.018465 | 13.9166
43 | 0.30861 | 0.14788 | -0.3086 | -0.14946 | 8.7012e-06 | -0.0015828 | 0.0098881 | 0.009908 | 0.009908 | 0.99905 | -0.0057883 | 0.99902 | -0.0055456 | 4.5036
44 | -0.69584 | -0.31664 | 0.69594 | 0.3128 | 0.00010706 | -0.0038402 | 0.022166 | 0.022119 | 0.022166 | 0.99564 | 0.019604 | 0.99579 | 0.018465 | 10.0753
45 | -0.1176 | -0.056957 | 0.1176 | 0.055119 | 1.5071e-06 | -0.0018374 | 0.0038066 | 0.0037835 | 0.0038066 | 0.99093 | -0.024984 | 0.99094 | -0.025092 | 1.7303
46 | 0.61 | 0.24159 | -0.60953 | -0.26365 | 0.00046807 | -0.022063 | 0.019113 | 0.019361 | 0.019361 | 0.99094 | -0.025092 | 0.99021 | -0.020674 | 8.8003
47 | 0.20388 | 0.098544 | -0.20387 | -0.098738 | 1.3411e-05 | -0.00019368 | 0.0066016 | 0.0066042 | 0.0066042 | 0.99021 | -0.020674 | 0.99014 | -0.021109 | 3.1448

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 5.5555 | 2.391

## res_load
| p_mw | q_mvar
0 | 0.073279 | 0.03549
1 | 0.067515 | 0.032699
2 | 0.21636 | 0.10479
3 | 0.15063 | 0.072953
4 | 0.22294 | 0.10798
5 | 0.39777 | 0.19265
6 | 0.21832 | 0.10574
7 | 0.22061 | 0.10685
8 | 0.3436 | 0.16642
9 | 0.16806 | 0.081397
10 | 0.30343 | 0.14696
11 | 0.24323 | 0.1178
12 | 0.27733 | 0.13432
13 | 0.26922 | 0.13039
14 | 0.28137 | 0.13627
15 | 0.34084 | 0.16507
16 | 0.22928 | 0.11105
17 | 0.3086 | 0.14946
18 | 0.41384 | 0.20043
19 | 0.26387 | 0.1278
20 | 0.18471 | 0.089458
21 | 0.1176 | 0.056957
22 | 0.20387 | 0.098738

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1