## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_73_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_73_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_73_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_73_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_73_0_node_10 | 20 | n |  | TRUE
5 | bus_MV_73_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_73_0_node_17 | 20 | n |  | TRUE
7 | bus_MV_73_0_node_18 | 20 | n |  | TRUE
8 | bus_MV_73_0_node_11 | 20 | n |  | TRUE
9 | bus_MV_73_0_node_13 | 20 | n |  | TRUE
10 | bus_MV_73_0_node_14 | 20 | n |  | TRUE
11 | bus_MV_73_0_node_15 | 20 | n |  | TRUE
12 | bus_MV_73_0_node_16 | 20 | n |  | TRUE
13 | bus_MV_73_0_node_149 | 20 | n |  | TRUE
14 | bus_MV_73_0_node_163 | 20 | n |  | TRUE
15 | bus_MV_73_0_node_147 | 20 | n |  | TRUE
16 | bus_MV_73_0_node_148 | 20 | n |  | TRUE
17 | bus_MV_73_0_node_12 | 20 | n |  | TRUE
18 | bus_MV_73_0_node_153 | 20 | n |  | TRUE
19 | bus_MV_73_0_node_152 | 20 | n |  | TRUE
20 | bus_MV_73_0_node_124 | 20 | n |  | TRUE
21 | bus_MV_73_0_node_150 | 20 | n |  | TRUE
22 | bus_MV_73_0_node_140 | 20 | n |  | TRUE
23 | bus_MV_73_0_node_19 | 20 | n |  | TRUE
24 | bus_MV_73_0_node_20 | 20 | n |  | TRUE
25 | bus_MV_73_0_node_162 | 20 | n |  | TRUE
26 | bus_MV_73_0_node_22 | 20 | n |  | TRUE
27 | bus_MV_73_0_node_131 | 20 | n |  | TRUE
28 | bus_MV_73_0_node_21 | 20 | n |  | TRUE
29 | bus_MV_73_0_node_25 | 20 | n |  | TRUE
30 | bus_MV_73_0_node_24 | 20 | n |  | TRUE
31 | bus_MV_73_0_node_23 | 20 | n |  | TRUE
32 | bus_MV_73_0_node_26 | 20 | n |  | TRUE
33 | bus_MV_73_0_node_32 | 20 | n |  | TRUE
34 | bus_MV_73_0_node_34 | 20 | n |  | TRUE
35 | bus_MV_73_0_node_35 | 20 | n |  | TRUE
36 | bus_MV_73_0_node_30 | 20 | n |  | TRUE
37 | bus_MV_73_0_node_27 | 20 | n |  | TRUE
38 | bus_MV_73_0_node_28 | 20 | n |  | TRUE
39 | bus_MV_73_0_node_29 | 20 | n |  | TRUE
40 | bus_MV_73_0_node_113 | 20 | n |  | TRUE
41 | bus_MV_73_0_node_112 | 20 | n |  | TRUE
42 | bus_MV_73_0_node_125 | 20 | n |  | TRUE
43 | bus_MV_73_0_node_87 | 20 | n |  | TRUE
44 | bus_MV_73_0_node_85 | 20 | n |  | TRUE
45 | bus_MV_73_0_node_86 | 20 | n |  | TRUE
46 | bus_MV_73_0_node_89 | 20 | n |  | TRUE
47 | bus_MV_73_0_node_33 | 20 | n |  | TRUE
48 | bus_MV_73_0_node_44 | 20 | n |  | TRUE
49 | bus_MV_73_0_node_45 | 20 | n |  | TRUE
50 | bus_MV_73_0_node_36 | 20 | n |  | TRUE
51 | bus_MV_73_0_node_167 | 20 | n |  | TRUE
52 | bus_MV_73_0_node_39 | 20 | n |  | TRUE
53 | bus_MV_73_0_node_49 | 20 | n |  | TRUE
54 | bus_MV_73_0_node_43 | 20 | n |  | TRUE
55 | bus_MV_73_0_node_38 | 20 | n |  | TRUE
56 | bus_MV_73_0_node_47 | 20 | n |  | TRUE
57 | bus_MV_73_0_node_37 | 20 | n |  | TRUE
58 | bus_MV_73_0_node_40 | 20 | n |  | TRUE
59 | bus_MV_73_0_node_41 | 20 | n |  | TRUE
60 | bus_MV_73_0_node_130 | 20 | n |  | TRUE
61 | bus_MV_73_0_node_92 | 20 | n |  | TRUE
62 | bus_MV_73_0_node_93 | 20 | n |  | TRUE
63 | bus_MV_73_0_node_42 | 20 | n |  | TRUE
64 | bus_MV_73_0_node_134 | 20 | n |  | TRUE
65 | bus_MV_73_0_node_76 | 20 | n |  | TRUE
66 | bus_MV_73_0_node_46 | 20 | n |  | TRUE
67 | bus_MV_73_0_node_48 | 20 | n |  | TRUE
68 | bus_MV_73_0_node_50 | 20 | n |  | TRUE
69 | bus_MV_73_0_node_127 | 20 | n |  | TRUE
70 | bus_MV_73_0_node_126 | 20 | n |  | TRUE
71 | bus_MV_73_0_node_129 | 20 | n |  | TRUE
72 | bus_MV_73_0_node_128 | 20 | n |  | TRUE
73 | bus_MV_73_0_node_72 | 20 | n |  | TRUE
74 | bus_MV_73_0_node_74 | 20 | n |  | TRUE
75 | bus_MV_73_0_node_75 | 20 | n |  | TRUE
76 | bus_MV_73_0_node_77 | 20 | n |  | TRUE
77 | bus_MV_73_0_node_78 | 20 | n |  | TRUE
78 | bus_MV_73_0_node_73 | 20 | n |  | TRUE
79 | bus_MV_73_0_node_135 | 20 | n |  | TRUE
80 | bus_MV_73_0_node_136 | 20 | n |  | TRUE
81 | bus_MV_73_0_node_132 | 20 | n |  | TRUE
82 | bus_MV_73_0_node_79 | 20 | n |  | TRUE
83 | bus_MV_73_0_node_80 | 20 | n |  | TRUE
84 | bus_MV_73_0_node_81 | 20 | n |  | TRUE
85 | bus_MV_73_0_node_82 | 20 | n |  | TRUE
86 | bus_MV_73_0_node_83 | 20 | n |  | TRUE
87 | bus_MV_73_0_node_84 | 20 | n |  | TRUE
88 | bus_MV_73_0_node_145 | 20 | n |  | TRUE
89 | bus_MV_73_0_node_101 | 20 | n |  | TRUE
90 | bus_MV_73_0_node_90 | 20 | n |  | TRUE
91 | bus_MV_73_0_node_102 | 20 | n |  | TRUE
92 | bus_MV_73_0_node_99 | 20 | n |  | TRUE
93 | bus_MV_73_0_node_105 | 20 | n |  | TRUE
94 | bus_MV_73_0_node_156 | 20 | n |  | TRUE
95 | bus_MV_73_0_node_88 | 20 | n |  | TRUE
96 | bus_MV_73_0_node_91 | 20 | n |  | TRUE
97 | bus_MV_73_0_node_141 | 20 | n |  | TRUE
98 | bus_MV_73_0_node_139 | 20 | n |  | TRUE
99 | bus_MV_73_0_node_138 | 20 | n |  | TRUE
100 | bus_MV_73_0_node_94 | 20 | n |  | TRUE
101 | bus_MV_73_0_node_95 | 20 | n |  | TRUE
102 | bus_MV_73_0_node_96 | 20 | n |  | TRUE
103 | bus_MV_73_0_node_97 | 20 | n |  | TRUE
104 | bus_MV_73_0_node_98 | 20 | n |  | TRUE
105 | bus_MV_73_0_node_100 | 20 | n |  | TRUE
106 | bus_MV_73_0_node_137 | 20 | n |  | TRUE
107 | bus_MV_73_0_node_143 | 20 | n |  | TRUE
108 | bus_MV_73_0_node_142 | 20 | n |  | TRUE
109 | bus_MV_73_0_node_103 | 20 | n |  | TRUE
110 | bus_MV_73_0_node_144 | 20 | n |  | TRUE
111 | bus_MV_73_0_node_106 | 20 | n |  | TRUE
112 | bus_MV_73_0_node_107 | 20 | n |  | TRUE
113 | bus_MV_73_0_node_108 | 20 | n |  | TRUE
114 | bus_MV_73_0_node_165 | 20 | n |  | TRUE
115 | bus_MV_73_0_node_111 | 20 | n |  | TRUE
116 | bus_MV_73_0_node_109 | 20 | n |  | TRUE
117 | bus_MV_73_0_node_110 | 20 | n |  | TRUE
118 | bus_MV_73_0_node_166 | 20 | n |  | TRUE
119 | bus_MV_73_0_node_151 | 20 | n |  | TRUE
120 | bus_MV_73_0_node_133 | 20 | n |  | TRUE
121 | bus_HV_73_0_node_41 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_73_0_load_0 | 0 | 0.18492 | 0.089562 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_73_0_load_10 | 4 | 0.24819 | 0.1202 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_73_0_load_17 | 6 | 0.35251 | 0.17073 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_73_0_load_18 | 7 | 0.33184 | 0.16072 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_73_0_load_13 | 9 | 0.3024 | 0.14646 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_73_0_load_163 | 14 | 0.37642 | 0.18231 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_73_0_load_147 | 15 | 0.39296 | 0.19032 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_73_0_load_153 | 18 | 0.32141 | 0.15567 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_73_0_load_150 | 21 | 0.056281 | 0.027258 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_73_0_load_19 | 23 | 0.39638 | 0.19197 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_73_0_load_162 | 25 | 0.14609 | 0.070755 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_73_0_load_24 | 30 | 0.23247 | 0.11259 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_73_0_load_23 | 31 | 0.41297 | 0.20001 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_73_0_load_26 | 32 | 0.19511 | 0.094494 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_73_0_load_30 | 36 | 0.25102 | 0.12158 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_73_0_load_27 | 37 | 0.10337 | 0.050062 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_73_0_load_113 | 40 | 0.26201 | 0.1269 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_73_0_load_125 | 42 | 0.069984 | 0.033895 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_73_0_load_87 | 43 | 0.090935 | 0.044042 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_73_0_load_85 | 44 | 0.32023 | 0.15509 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_73_0_load_89 | 46 | 0.3127 | 0.15145 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_73_0_load_44 | 48 | 0.11557 | 0.055975 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_73_0_load_45 | 49 | 0.35374 | 0.17132 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_73_0_load_167 | 51 | 0.33576 | 0.16262 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_73_0_load_39 | 52 | 0.097359 | 0.047153 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_73_0_load_49 | 53 | 0.35997 | 0.17434 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_73_0_load_47 | 56 | 0.084055 | 0.04071 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_73_0_load_37 | 57 | 0.31756 | 0.1538 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_73_0_load_130 | 60 | 0.11654 | 0.056444 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_73_0_load_92 | 61 | 0.22082 | 0.10695 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_73_0_load_42 | 63 | 0.22594 | 0.10943 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_73_0_load_46 | 66 | 0.20368 | 0.098647 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_73_0_load_126 | 70 | 1.3696 | 0.66333 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_73_0_load_128 | 72 | 0.51898 | 0.25136 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_73_0_load_72 | 73 | 0.36385 | 0.17622 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_73_0_load_77 | 76 | 0.07366 | 0.035675 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_73_0_load_135 | 79 | 0.13136 | 0.06362 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_73_0_load_136 | 80 | 0.081972 | 0.039701 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_73_0_load_132 | 81 | 0.22203 | 0.10754 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_73_0_load_79 | 82 | 0.35719 | 0.17299 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_73_0_load_84 | 87 | 0.071478 | 0.034618 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_73_0_load_145 | 88 | 0.069338 | 0.033582 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_73_0_load_101 | 89 | 0.15397 | 0.074573 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_73_0_load_156 | 94 | 0.24793 | 0.12008 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_73_0_load_141 | 97 | 0.069443 | 0.033633 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_73_0_load_138 | 99 | 0.12892 | 0.062437 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_73_0_load_94 | 100 | 0.38821 | 0.18802 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_73_0_load_97 | 103 | 0.11732 | 0.05682 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_73_0_load_98 | 104 | 0.080229 | 0.038857 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_73_0_load_100 | 105 | 0.2657 | 0.12868 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_73_0_load_137 | 106 | 0.083859 | 0.040615 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_73_0_load_143 | 107 | 0.09633 | 0.046655 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_73_0_load_142 | 108 | 0.2248 | 0.10888 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_73_0_load_144 | 110 | 0.10503 | 0.05087 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_73_0_load_106 | 111 | 0.19144 | 0.092721 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_73_0_load_165 | 114 | 0.18745 | 0.090785 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_73_0_load_109 | 116 | 0.37066 | 0.17952 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_73_0_load_166 | 118 | 0.3974 | 0.19247 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_73_0_load_151 | 119 | 0.27819 | 0.13473 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_73_0_load_133 | 120 | 0.20877 | 0.10111 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_73_0_line_0 |  | 0 | 1 | 0.011226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_73_0_line_1 |  | 1 | 2 | 0.19733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_73_0_line_2 |  | 2 | 3 | 0.82488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_73_0_line_3 |  | 2 | 4 | 0.01978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_73_0_line_4 |  | 3 | 5 | 0.20527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_73_0_line_5 |  | 3 | 6 | 0.07896 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_73_0_line_6 |  | 4 | 8 | 0.074831 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_73_0_line_7 |  | 5 | 7 | 0.085242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_73_0_line_8 |  | 6 | 12 | 0.11314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_73_0_line_9 |  | 7 | 16 | 0.48084 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_73_0_line_10 |  | 8 | 17 | 0.087177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_73_0_line_11 |  | 9 | 10 | 0.041724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_73_0_line_12 |  | 10 | 11 | 0.10152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_73_0_line_13 |  | 10 | 12 | 0.10724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_73_0_line_14 |  | 11 | 13 | 0.37916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_73_0_line_15 |  | 11 | 14 | 0.012984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_73_0_line_16 |  | 13 | 15 | 0.013065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_73_0_line_17 |  | 16 | 21 | 0.12557 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_73_0_line_18 |  | 17 | 18 | 0.093291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_73_0_line_19 |  | 18 | 19 | 0.020335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_73_0_line_20 |  | 19 | 20 | 0.27033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_73_0_line_21 |  | 20 | 119 | 0.14955 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_73_0_line_22 |  | 21 | 22 | 0.64036 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_73_0_line_23 |  | 22 | 99 | 0.024009 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_73_0_line_24 |  | 23 | 24 | 0.14885 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
25 | MV_73_0_line_25 |  | 23 | 25 | 1.2091 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
26 | MV_73_0_line_26 |  | 24 | 26 | 0.60769 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_73_0_line_27 |  | 25 | 27 | 0.035746 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
28 | MV_73_0_line_28 |  | 26 | 31 | 0.02149 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_73_0_line_29 |  | 26 | 28 | 0.94771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_73_0_line_30 |  | 27 | 47 | 0.10801 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
31 | MV_73_0_line_31 |  | 28 | 29 | 0.94666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_73_0_line_32 |  | 28 | 30 | 0.10602 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_73_0_line_33 |  | 29 | 32 | 0.24899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_73_0_line_34 |  | 31 | 33 | 1.3537 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
35 | MV_73_0_line_35 |  | 33 | 34 | 0.30855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_73_0_line_36 |  | 33 | 35 | 0.17275 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
37 | MV_73_0_line_37 |  | 33 | 36 | 0.044691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_73_0_line_38 |  | 34 | 49 | 0.083424 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_73_0_line_39 |  | 35 | 50 | 0.44948 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
40 | MV_73_0_line_40 |  | 35 | 51 | 0.085083 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_73_0_line_41 |  | 37 | 38 | 0.1348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_73_0_line_42 |  | 38 | 39 | 0.022337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_73_0_line_43 |  | 39 | 42 | 0.023112 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_73_0_line_44 |  | 39 | 43 | 0.66806 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_73_0_line_45 |  | 40 | 41 | 0.049875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_73_0_line_46 |  | 41 | 115 | 0.47168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_73_0_line_47 |  | 41 | 117 | 0.27592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_73_0_line_48 |  | 43 | 44 | 0.012893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_73_0_line_49 |  | 44 | 95 | 0.03191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_73_0_line_50 |  | 44 | 45 | 0.0408 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_73_0_line_51 |  | 45 | 46 | 0.1559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_73_0_line_52 |  | 47 | 48 | 0.036335 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
53 | MV_73_0_line_53 |  | 48 | 54 | 0.080145 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_73_0_line_54 |  | 50 | 52 | 0.092516 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
55 | MV_73_0_line_55 |  | 50 | 53 | 0.054096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_73_0_line_56 |  | 52 | 55 | 0.048398 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
57 | MV_73_0_line_57 |  | 53 | 56 | 0.053013 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_73_0_line_58 |  | 54 | 64 | 0.31972 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
59 | MV_73_0_line_59 |  | 54 | 63 | 0.11712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_73_0_line_60 |  | 55 | 58 | 0.29272 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
61 | MV_73_0_line_61 |  | 55 | 57 | 0.032639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_73_0_line_62 |  | 58 | 59 | 0.34471 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
63 | MV_73_0_line_63 |  | 58 | 60 | 0.056706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_73_0_line_64 |  | 59 | 61 | 0.003567 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_73_0_line_65 |  | 61 | 62 | 0.064212 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
66 | MV_73_0_line_66 |  | 62 | 92 | 0.35841 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
67 | MV_73_0_line_67 |  | 62 | 93 | 0.31235 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_73_0_line_68 |  | 62 | 94 | 0.11906 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_73_0_line_69 |  | 64 | 65 | 0.12513 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
70 | MV_73_0_line_70 |  | 65 | 79 | 0.085857 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
71 | MV_73_0_line_71 |  | 65 | 78 | 1.0016 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
72 | MV_73_0_line_72 |  | 66 | 67 | 0.032001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_73_0_line_73 |  | 67 | 68 | 0.040689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_73_0_line_74 |  | 68 | 69 | 0.062403 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
75 | MV_73_0_line_75 |  | 68 | 70 | 0.056245 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
76 | MV_73_0_line_76 |  | 69 | 71 | 0.11126 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
77 | MV_73_0_line_77 |  | 69 | 72 | 0.092851 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
78 | MV_73_0_line_78 |  | 71 | 120 | 0.062939 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_73_0_line_79 |  | 71 | 81 | 0.30233 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
80 | MV_73_0_line_80 |  | 73 | 74 | 0.016863 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
81 | MV_73_0_line_81 |  | 73 | 75 | 0.016946 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
82 | MV_73_0_line_82 |  | 74 | 76 | 0.01573 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
83 | MV_73_0_line_83 |  | 75 | 77 | 0.017228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_73_0_line_84 |  | 76 | 78 | 0.038748 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
85 | MV_73_0_line_85 |  | 77 | 80 | 0.008126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_73_0_line_86 |  | 79 | 81 | 0.16848 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
87 | MV_73_0_line_87 |  | 82 | 83 | 0.009046 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_73_0_line_88 |  | 82 | 84 | 0.023068 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
89 | MV_73_0_line_89 |  | 83 | 85 | 0.023144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_73_0_line_90 |  | 83 | 86 | 0.13689 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
91 | MV_73_0_line_91 |  | 84 | 87 | 0.018631 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
92 | MV_73_0_line_92 |  | 85 | 88 | 0.015331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_73_0_line_93 |  | 86 | 89 | 0.039848 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
94 | MV_73_0_line_94 |  | 87 | 90 | 0.036524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_73_0_line_95 |  | 89 | 91 | 0.0043763 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
96 | MV_73_0_line_96 |  | 90 | 95 | 0.007197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_73_0_line_97 |  | 91 | 109 | 0.32616 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
98 | MV_73_0_line_98 |  | 92 | 107 | 0.058232 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
99 | MV_73_0_line_99 |  | 92 | 101 | 0.098019 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_73_0_line_100 |  | 93 | 111 | 0.059783 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_73_0_line_101 |  | 95 | 96 | 0.070646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_73_0_line_102 |  | 96 | 97 | 0.025725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_73_0_line_103 |  | 96 | 98 | 0.13963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_73_0_line_104 |  | 98 | 99 | 0.040464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_73_0_line_105 |  | 100 | 101 | 0.035777 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_73_0_line_106 |  | 100 | 102 | 0.060696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_73_0_line_107 |  | 100 | 103 | 0.18071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_73_0_line_108 |  | 101 | 104 | 0.057763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_73_0_line_109 |  | 102 | 105 | 0.12207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_73_0_line_110 |  | 103 | 106 | 0.15227 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_73_0_line_111 |  | 105 | 108 | 0.08492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_73_0_line_112 |  | 107 | 109 | 0.06008 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
113 | MV_73_0_line_113 |  | 109 | 110 | 0.043269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_73_0_line_114 |  | 111 | 112 | 0.059134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_73_0_line_115 |  | 112 | 113 | 0.22627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_73_0_line_116 |  | 113 | 114 | 0.098014 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_73_0_line_117 |  | 113 | 115 | 0.41535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_73_0_line_118 |  | 115 | 118 | 0.007768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_73_0_line_119 |  | 116 | 117 | 0.014095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_73_0_trafo_41 | 25 MVA 110/20 kV | 121 | 59 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2716395.5954 | 1101421.5731
1 | 2716395.7518 | 1101432.7949
2 | 2716551.2627 | 1101422.3696
3 | 2716632.9079 | 1102072.2247
4 | 2716567.7609 | 1101411.3897
5 | 2716489.0239 | 1102151.2174
6 | 2716666.2743 | 1102000.6611
7 | 2716561.3504 | 1102196.6693
8 | 2716642.5896 | 1101410.8591
9 | 2716869.9034 | 1101964.0063
10 | 2716871.7718 | 1102005.6596
11 | 2716972.0879 | 1101988.39
12 | 2716766.4253 | 1102025.7361
13 | 2716986.8846 | 1102340.738
14 | 2716971.1686 | 1101975.4412
15 | 2716990.046 | 1102353.4075
16 | 2716439.6591 | 1102661.8522
17 | 2716727.6885 | 1101391.9364
18 | 2716813.3982 | 1101357.3937
19 | 2716828.6747 | 1101343.9672
20 | 2716980.5904 | 1101132.6128
21 | 2716316.7779 | 1102636.0021
22 | 2715701.0569 | 1102460.0882
23 | 2713369.1946 | 1100540.6444
24 | 2713225.4721 | 1100501.9047
25 | 2714576.2958 | 1100610.5476
26 | 2713177.4367 | 1100750.8328
27 | 2714611.9163 | 1100606.4945
28 | 2712402.4771 | 1100676.0506
29 | 2711957.0408 | 1100671.7339
30 | 2712341.8256 | 1100589.0927
31 | 2713194.6223 | 1100763.7728
32 | 2711906.9239 | 1100459.3907
33 | 2714528.6368 | 1100993.7751
34 | 2714764.0708 | 1101087.7707
35 | 2714551.9032 | 1101147.4733
36 | 2714554.2655 | 1100967.7184
37 | 2715476.2074 | 1103409.0414
38 | 2715595.2778 | 1103369.8025
39 | 2715587.675 | 1103352.5127
40 | 2715062.0254 | 1102873.4281
41 | 2715024.141 | 1102841.2108
42 | 2715565.1115 | 1103352.8505
43 | 2715569.0712 | 1102684.7082
44 | 2715581.2431 | 1102680.4565
45 | 2715595.6624 | 1102718.6235
46 | 2715499.476 | 1102839.0196
47 | 2714719.9211 | 1100605.1432
48 | 2714755.7177 | 1100598.9121
49 | 2714711.7643 | 1101152.7602
50 | 2714888.5914 | 1101225.7068
51 | 2714543.0837 | 1101232.0976
52 | 2714935.0531 | 1101301.4681
53 | 2714936.9587 | 1101201.2051
54 | 2714834.5188 | 1100584.3274
55 | 2714945.5457 | 1101347.8781
56 | 2714912.5324 | 1101154.2028
57 | 2714915.1712 | 1101360.045
58 | 2714909.7736 | 1101499.6042
59 | 2715020.4406 | 1101824.6856
60 | 2714855.8979 | 1101517.2959
61 | 2715020.8457 | 1101828.229
62 | 2715028.4624 | 1101891.9498
63 | 2714858.617 | 1100698.8884
64 | 2715080.1242 | 1100379.6358
65 | 2715082.8905 | 1100501.2374
66 | 2714881.4113 | 1101017.6856
67 | 2714884.8081 | 1100985.8727
68 | 2714923.776 | 1100973.7904
69 | 2714983.6515 | 1100955.7223
70 | 2714940.1872 | 1101027.5881
71 | 2715054.6293 | 1101019.3426
72 | 2715005.4025 | 1101045.3837
73 | 2715642.0159 | 1100497.5295
74 | 2715650.9017 | 1100511.8751
75 | 2715625.4524 | 1100501.328
76 | 2715666.522 | 1100510.0212
77 | 2715628.2411 | 1100518.3259
78 | 2715678.0277 | 1100473.0206
79 | 2715084.3348 | 1100583.5206
80 | 2715620.5336 | 1100520.9001
81 | 2714992.1906 | 1100724.5672
82 | 2715496.3223 | 1102622.8574
83 | 2715489.3179 | 1102617.1648
84 | 2715517.7234 | 1102631.3369
85 | 2715501.312 | 1102597.3572
86 | 2715404.7272 | 1102509.5505
87 | 2715536.1233 | 1102634.1779
88 | 2715514.5568 | 1102590.3117
89 | 2715381.1814 | 1102477.4038
90 | 2715570.1495 | 1102647.2784
91 | 2715378.5793 | 1102473.8851
92 | 2715287.7759 | 1102139.3673
93 | 2714940.159 | 1102191.5589
94 | 2715038.3508 | 1102010.5952
95 | 2715577.1711 | 1102648.8131
96 | 2715618.5784 | 1102598.8006
97 | 2715595.6589 | 1102587.1178
98 | 2715637.0067 | 1102462.7035
99 | 2715677.0639 | 1102458.0409
100 | 2715409.8543 | 1102084.4039
101 | 2715377.1432 | 1102099.1036
102 | 2715470.6478 | 1102087.5838
103 | 2715471.7279 | 1102248.256
104 | 2715416.1763 | 1102141.3626
105 | 2715469.7739 | 1101966.0522
106 | 2715620.3126 | 1102281.5725
107 | 2715305.2303 | 1102194.9219
108 | 2715452.0071 | 1101883.246
109 | 2715323.2409 | 1102252.2393
110 | 2715362.5851 | 1102234.2319
111 | 2714938.2537 | 1102251.2966
112 | 2714908.7608 | 1102302.5844
113 | 2714741.8871 | 1102435.6529
114 | 2714722.9428 | 1102340.0971
115 | 2714780.5007 | 1102763.0595
116 | 2715072.1943 | 1102622.4174
117 | 2715075.5258 | 1102636.1121
118 | 2714778.3088 | 1102770.512
119 | 2717017.5188 | 1101277.5344
120 | 2715117.1192 | 1101011.838
121 | 2715020.4406 | 1101824.6856

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98724 | -0.10937 | 0.18492 | 0.089562
1 | 0.98725 | -0.10939 | 0 | 0
2 | 0.98729 | -0.10981 | 0 | 0
3 | 0.98838 | -0.11884 | 0 | 0
4 | 0.98727 | -0.10962 | 0.24819 | 0.1202
5 | 0.98903 | -0.12427 | 0 | 0
6 | 0.98816 | -0.12036 | 0.35251 | 0.17073
7 | 0.9893 | -0.1265 | 0.33184 | 0.16072
8 | 0.98718 | -0.11025 | 0 | 0
9 | 0.98784 | -0.11753 | 0.3024 | 0.14646
10 | 0.98786 | -0.11769 | 0 | 0
11 | 0.98776 | -0.1168 | 0 | 0
12 | 0.98801 | -0.119 | 0 | 0
13 | 0.98757 | -0.11509 | 0 | 0
14 | 0.98775 | -0.11674 | 0.37642 | 0.18231
15 | 0.98756 | -0.11503 | 0.39296 | 0.19032
16 | 0.9919 | -0.10739 | 0 | 0
17 | 0.98712 | -0.10966 | 0 | 0
18 | 0.98704 | -0.10902 | 0.32141 | 0.15567
19 | 0.98704 | -0.10896 | 0 | 0
20 | 0.98694 | -0.1081 | 0 | 0
21 | 0.99258 | -0.10241 | 0.056281 | 0.027258
22 | 0.99611 | -0.076672 | 0 | 0
23 | 0.99154 | -0.30045 | 0.39638 | 0.19197
24 | 0.99195 | -0.277 | 0 | 0
25 | 0.9886 | -0.4732 | 0.14609 | 0.070755
26 | 0.99275 | -0.27281 | 0 | 0
27 | 0.98856 | -0.47342 | 0 | 0
28 | 0.99225 | -0.2703 | 0 | 0
29 | 0.99201 | -0.2691 | 0 | 0
30 | 0.9922 | -0.2706 | 0.23247 | 0.11259
31 | 0.99278 | -0.27263 | 0.41297 | 0.20001
32 | 0.99195 | -0.26855 | 0.19511 | 0.094494
33 | 0.99715 | -0.015246 | 0 | 0
34 | 0.99701 | -0.014007 | 0 | 0
35 | 0.99746 | -0.013619 | 0 | 0
36 | 0.99714 | -0.015112 | 0.25102 | 0.12158
37 | 0.99687 | -0.086628 | 0.10337 | 0.050062
38 | 0.99689 | -0.086781 | 0 | 0
39 | 0.99689 | -0.086804 | 0 | 0
40 | 0.99751 | 0.0050264 | 0.26201 | 0.1269
41 | 0.99752 | 0.0048712 | 0 | 0
42 | 0.99689 | -0.086785 | 0.069984 | 0.033895
43 | 0.99712 | -0.085129 | 0.090935 | 0.044042
44 | 0.99712 | -0.085166 | 0.32023 | 0.15509
45 | 0.9971 | -0.085334 | 0 | 0
46 | 0.99703 | -0.084766 | 0.3127 | 0.15145
47 | 0.98844 | -0.47408 | 0 | 0
48 | 0.98839 | -0.4743 | 0.11557 | 0.055975
49 | 0.99696 | -0.014366 | 0.35374 | 0.17132
50 | 0.99831 | -0.0090829 | 0 | 0
51 | 0.99741 | -0.013966 | 0.33576 | 0.16262
52 | 0.9985 | -0.0080756 | 0.097359 | 0.047153
53 | 0.99828 | -0.0088011 | 0.35997 | 0.17434
54 | 0.98831 | -0.47477 | 0 | 0
55 | 0.9986 | -0.0075402 | 0 | 0
56 | 0.99828 | -0.0087497 | 0.084055 | 0.04071
57 | 0.99859 | -0.0074167 | 0.31756 | 0.1538
58 | 0.99924 | -0.0041464 | 0 | 0
59 | 1 | 0 | -14.7449 | -6.687
60 | 0.99923 | -0.0040696 | 0.11654 | 0.056444
61 | 0.99999 | -4.1731e-05 | 0.22082 | 0.10695
62 | 0.99983 | -0.00077458 | 0 | 0
63 | 0.98827 | -0.47446 | 0.22594 | 0.10943
64 | 0.98763 | -0.51452 | 0 | 0
65 | 0.9875 | -0.51521 | 0 | 0
66 | 0.98678 | -0.53327 | 0.20368 | 0.098647
67 | 0.98679 | -0.53335 | 0 | 0
68 | 0.9868 | -0.53345 | 0 | 0
69 | 0.98683 | -0.53332 | 0 | 0
70 | 0.98677 | -0.53354 | 1.3696 | 0.66333
71 | 0.98691 | -0.53302 | 0 | 0
72 | 0.98681 | -0.53339 | 0.51898 | 0.25136
73 | 0.98732 | -0.51714 | 0.36385 | 0.17622
74 | 0.98732 | -0.51713 | 0 | 0
75 | 0.98731 | -0.51715 | 0 | 0
76 | 0.98732 | -0.51713 | 0.07366 | 0.035675
77 | 0.98731 | -0.51713 | 0 | 0
78 | 0.98733 | -0.51635 | 0 | 0
79 | 0.98743 | -0.51553 | 0.13136 | 0.06362
80 | 0.98731 | -0.51712 | 0.081972 | 0.039701
81 | 0.98714 | -0.53204 | 0.22203 | 0.10754
82 | 0.99745 | -0.086765 | 0.35719 | 0.17299
83 | 0.99746 | -0.086707 | 0 | 0
84 | 0.99742 | -0.086901 | 0 | 0
85 | 0.99746 | -0.086689 | 0 | 0
86 | 0.99766 | -0.085817 | 0 | 0
87 | 0.99738 | -0.087358 | 0.071478 | 0.034618
88 | 0.99746 | -0.086676 | 0.069338 | 0.033582
89 | 0.99772 | -0.085554 | 0.15397 | 0.074573
90 | 0.99719 | -0.085799 | 0 | 0
91 | 0.99772 | -0.085525 | 0 | 0
92 | 0.9984 | -0.082396 | 0 | 0
93 | 0.99899 | -0.0071798 | 0 | 0
94 | 0.99977 | -0.0011321 | 0.24793 | 0.12008
95 | 0.99716 | -0.085491 | 0 | 0
96 | 0.99688 | -0.083185 | 0 | 0
97 | 0.99688 | -0.083164 | 0.069443 | 0.033633
98 | 0.99635 | -0.078712 | 0 | 0
99 | 0.9962 | -0.077409 | 0.12892 | 0.062437
100 | 0.9982 | -0.080682 | 0.38821 | 0.18802
101 | 0.99825 | -0.08112 | 0 | 0
102 | 0.99817 | -0.080347 | 0 | 0
103 | 0.99816 | -0.080273 | 0.11732 | 0.05682
104 | 0.99825 | -0.081067 | 0.080229 | 0.038857
105 | 0.99809 | -0.079655 | 0.2657 | 0.12868
106 | 0.99813 | -0.080429 | 0.083859 | 0.040615
107 | 0.99831 | -0.082828 | 0.09633 | 0.046655
108 | 0.99807 | -0.079431 | 0.2248 | 0.10888
109 | 0.99821 | -0.083263 | 0 | 0
110 | 0.99821 | -0.08321 | 0.10503 | 0.05087
111 | 0.99888 | -0.0063196 | 0.19144 | 0.092721
112 | 0.99879 | -0.0055989 | 0 | 0
113 | 0.99844 | -0.0027911 | 0 | 0
114 | 0.99842 | -0.0025779 | 0.18745 | 0.090785
115 | 0.9979 | 0.0016977 | 0 | 0
116 | 0.99739 | 0.0060999 | 0.37066 | 0.17952
117 | 0.99739 | 0.0060372 | 0 | 0
118 | 0.9979 | 0.0017348 | 0.3974 | 0.19247
119 | 0.98686 | -0.10862 | 0.27819 | 0.13473
120 | 0.98688 | -0.53318 | 0.20877 | 0.10111
121 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.18492 | -0.089562 | 0.18492 | 0.089301 | 5.4067e-07 | -0.00026108 | 0.006008 | 0.0060047 | 0.006008 | 0.98724 | -0.10937 | 0.98725 | -0.10939 | 2.7309
1 | -0.18492 | -0.089301 | 0.18493 | 0.084711 | 9.4076e-06 | -0.0045896 | 0.0060047 | 0.0059476 | 0.0060047 | 0.98725 | -0.10939 | 0.98729 | -0.10981 | 2.7294
2 | -1.0329 | -0.48372 | 1.0342 | 0.46487 | 0.0012161 | -0.018858 | 0.03335 | 0.033116 | 0.03335 | 0.98729 | -0.10981 | 0.98838 | -0.11884 | 15.159
3 | 0.84801 | 0.39901 | -0.84799 | -0.39947 | 1.9833e-05 | -0.00045445 | 0.027403 | 0.027408 | 0.027408 | 0.98729 | -0.10981 | 0.98727 | -0.10962 | 12.4583
4 | -2.4593 | -1.137 | 2.461 | 1.1327 | 0.0017147 | -0.0042823 | 0.079133 | 0.079074 | 0.079133 | 0.98838 | -0.11884 | 0.98903 | -0.12427 | 35.9694
5 | 1.4251 | 0.67215 | -1.4248 | -0.67206 | 0.00029796 | 9.4565e-05 | 0.04602 | 0.046021 | 0.046021 | 0.98838 | -0.11884 | 0.98816 | -0.12036 | 21.915
6 | 0.5998 | 0.27926 | -0.59975 | -0.27932 | 4.99e-05 | -5.581e-05 | 0.019346 | 0.019347 | 0.019347 | 0.98727 | -0.10962 | 0.98718 | -0.11025 | 9.2127
7 | -2.461 | -1.1327 | 2.4617 | 1.131 | 0.00071133 | -0.0017804 | 0.079074 | 0.07905 | 0.079074 | 0.98903 | -0.12427 | 0.9893 | -0.1265 | 35.9428
8 | 1.0723 | 0.50133 | -1.0721 | -0.50391 | 0.00018079 | -0.0025838 | 0.03458 | 0.034613 | 0.034613 | 0.98816 | -0.12036 | 0.98801 | -0.119 | 15.7331
9 | -2.7935 | -1.2917 | 2.8004 | 1.2954 | 0.0069091 | 0.0037643 | 0.089807 | 0.0898 | 0.089807 | 0.9893 | -0.1265 | 0.9919 | -0.10739 | 42.7652
10 | 0.59975 | 0.27932 | -0.5997 | -0.28133 | 4.3617e-05 | -0.0020154 | 0.019347 | 0.019372 | 0.019372 | 0.98718 | -0.11025 | 0.98712 | -0.10966 | 8.8053
11 | -0.3024 | -0.14646 | 0.30241 | 0.14549 | 5.3634e-06 | -0.00097056 | 0.0098189 | 0.0098065 | 0.0098189 | 0.98784 | -0.11753 | 0.98786 | -0.11769 | 4.4631
12 | 0.76955 | 0.36087 | -0.76946 | -0.36321 | 8.3707e-05 | -0.0023403 | 0.024838 | 0.024867 | 0.024867 | 0.98786 | -0.11769 | 0.98776 | -0.1168 | 11.3033
13 | -1.072 | -0.50636 | 1.0721 | 0.50391 | 0.00017168 | -0.0024482 | 0.034644 | 0.034613 | 0.034644 | 0.98786 | -0.11769 | 0.98801 | -0.119 | 15.7472
14 | 0.39304 | 0.18121 | -0.39296 | -0.19002 | 8.1685e-05 | -0.0088067 | 0.012649 | 0.012759 | 0.012759 | 0.98776 | -0.1168 | 0.98757 | -0.11509 | 5.7996
15 | 0.37642 | 0.18201 | -0.37642 | -0.18231 | 2.589e-06 | -0.0003017 | 0.012219 | 0.012223 | 0.012223 | 0.98776 | -0.1168 | 0.98775 | -0.11674 | 5.556
16 | 0.39296 | 0.19002 | -0.39296 | -0.19032 | 2.8403e-06 | -0.00030339 | 0.012759 | 0.012763 | 0.012763 | 0.98757 | -0.11509 | 0.98756 | -0.11503 | 5.8013
17 | -2.8004 | -1.2954 | 2.8023 | 1.2964 | 0.0018041 | 0.00098246 | 0.0898 | 0.089798 | 0.0898 | 0.9919 | -0.10739 | 0.99258 | -0.10241 | 42.7619
18 | 0.5997 | 0.28133 | -0.59965 | -0.28349 | 4.6802e-05 | -0.0021564 | 0.019372 | 0.019399 | 0.019399 | 0.98712 | -0.10966 | 0.98704 | -0.10902 | 8.8176
19 | 0.27824 | 0.12782 | -0.27824 | -0.12829 | 2.1785e-06 | -0.00047237 | 0.0089552 | 0.008961 | 0.008961 | 0.98704 | -0.10902 | 0.98704 | -0.10896 | 4.0732
20 | 0.27824 | 0.12829 | -0.27821 | -0.13457 | 2.9232e-05 | -0.006279 | 0.008961 | 0.0090395 | 0.0090395 | 0.98704 | -0.10896 | 0.98694 | -0.1081 | 4.1089
21 | 0.27821 | 0.13457 | -0.27819 | -0.13473 | 2.1778e-05 | -0.00016025 | 0.0090395 | 0.0090417 | 0.0090417 | 0.98694 | -0.1081 | 0.98686 | -0.10862 | 4.3056
22 | -2.8585 | -1.3237 | 2.8681 | 1.3289 | 0.0095755 | 0.005242 | 0.091617 | 0.091607 | 0.091617 | 0.99258 | -0.10241 | 0.99611 | -0.076672 | 43.627
23 | -2.8681 | -1.3289 | 2.8684 | 1.3284 | 0.00026896 | -0.00048906 | 0.091607 | 0.091601 | 0.091607 | 0.99611 | -0.076672 | 0.9962 | -0.077409 | 41.6397
24 | -4.0679 | -1.848 | 4.0688 | 1.8502 | 0.00089914 | 0.0022155 | 0.13008 | 0.13008 | 0.13008 | 0.99154 | -0.30045 | 0.99195 | -0.277 | 20.1672
25 | 3.6715 | 1.656 | -3.6656 | -1.6417 | 0.0059363 | 0.014325 | 0.11726 | 0.11728 | 0.11728 | 0.99154 | -0.30045 | 0.9886 | -0.4732 | 18.183
26 | -4.0688 | -1.8502 | 4.0719 | 1.8143 | 0.0031661 | -0.035817 | 0.13008 | 0.12963 | 0.13008 | 0.99195 | -0.277 | 0.99275 | -0.27281 | 20.3881
27 | 3.5195 | 1.5709 | -3.5193 | -1.573 | 0.00013993 | -0.0021162 | 0.11254 | 0.11257 | 0.11257 | 0.9886 | -0.4732 | 0.98856 | -0.47342 | 17.644
28 | -4.4998 | -1.971 | 4.5 | 1.9698 | 0.00013549 | -0.0012545 | 0.14285 | 0.14283 | 0.14285 | 0.99275 | -0.27281 | 0.99278 | -0.27263 | 22.3901
29 | 0.42787 | 0.15666 | -0.42764 | -0.17889 | 0.00022597 | -0.022222 | 0.013249 | 0.013486 | 0.013486 | 0.99275 | -0.27281 | 0.99225 | -0.2703 | 6.1301
30 | 3.5193 | 1.573 | -3.5189 | -1.5794 | 0.00042323 | -0.0063931 | 0.11257 | 0.11265 | 0.11265 | 0.98856 | -0.47342 | 0.98844 | -0.47408 | 17.6564
31 | 0.19517 | 0.066413 | -0.19512 | -0.088648 | 4.7175e-05 | -0.022234 | 0.0059977 | 0.0062364 | 0.0062364 | 0.99225 | -0.2703 | 0.99201 | -0.2691 | 2.8347
32 | 0.23248 | 0.11247 | -0.23247 | -0.11259 | 1.0666e-05 | -0.00011793 | 0.0075135 | 0.0075151 | 0.0075151 | 0.99225 | -0.2703 | 0.9922 | -0.2706 | 3.5786
33 | 0.19512 | 0.088648 | -0.19511 | -0.094494 | 1.3076e-05 | -0.005846 | 0.0062364 | 0.0063088 | 0.0063088 | 0.99201 | -0.2691 | 0.99195 | -0.26855 | 2.8676
34 | -4.9129 | -2.1698 | 4.9247 | 2.1996 | 0.011784 | 0.029837 | 0.15617 | 0.15614 | 0.15617 | 0.99278 | -0.27263 | 0.99715 | -0.015246 | 24.2119
35 | 0.35381 | 0.16393 | -0.35376 | -0.17124 | 5.2912e-05 | -0.0073084 | 0.011289 | 0.01138 | 0.01138 | 0.99715 | -0.015246 | 0.99701 | -0.014007 | 5.1725
36 | -5.5295 | -2.484 | 5.5312 | 2.4742 | 0.0016427 | -0.0098707 | 0.17549 | 0.17536 | 0.17549 | 0.99715 | -0.015246 | 0.99746 | -0.013619 | 27.5064
37 | 0.25103 | 0.12052 | -0.25102 | -0.12158 | 3.8836e-06 | -0.0010598 | 0.0080614 | 0.0080747 | 0.0080747 | 0.99715 | -0.015246 | 0.99714 | -0.015112 | 3.6703
38 | 0.35376 | 0.17124 | -0.35374 | -0.17132 | 1.925e-05 | -8.6935e-05 | 0.01138 | 0.011381 | 0.011381 | 0.99701 | -0.014007 | 0.99696 | -0.014366 | 5.4194
39 | -5.867 | -2.6367 | 5.8718 | 2.6113 | 0.0048044 | -0.025417 | 0.18615 | 0.18582 | 0.18615 | 0.99746 | -0.013619 | 0.99831 | -0.0090829 | 29.1779
40 | 0.33578 | 0.16253 | -0.33576 | -0.16262 | 1.7672e-05 | -8.9983e-05 | 0.010796 | 0.010798 | 0.010798 | 0.99746 | -0.013619 | 0.99741 | -0.013966 | 5.1417
41 | -0.10337 | -0.050062 | 0.10337 | 0.046865 | 1.9668e-06 | -0.0031978 | 0.0033259 | 0.0032865 | 0.0033259 | 0.99687 | -0.086628 | 0.99689 | -0.086781 | 1.5118
42 | -0.10337 | -0.046865 | 0.10337 | 0.046335 | 3.2147e-07 | -0.00052991 | 0.0032865 | 0.0032802 | 0.0032865 | 0.99689 | -0.086781 | 0.99689 | -0.086804 | 1.4939
43 | 0.069984 | 0.033346 | -0.069984 | -0.033895 | 1.5596e-07 | -0.00054836 | 0.0022448 | 0.0022517 | 0.0022517 | 0.99689 | -0.086804 | 0.99689 | -0.086785 | 1.0235
44 | -0.17335 | -0.079681 | 0.17339 | 0.078911 | 3.6268e-05 | -0.00077005 | 0.0055247 | 0.0055152 | 0.0055247 | 0.99689 | -0.086804 | 0.99712 | -0.085129 | 2.6308
45 | -0.26201 | -0.1269 | 0.26201 | 0.12571 | 4.7176e-06 | -0.0011835 | 0.0084249 | 0.00841 | 0.0084249 | 0.99751 | 0.0050264 | 0.99752 | 0.0048712 | 3.8295
46 | -0.63272 | -0.29836 | 0.63298 | 0.28722 | 0.00025632 | -0.011134 | 0.020244 | 0.020108 | 0.020244 | 0.99752 | 0.0048712 | 0.9979 | 0.0016977 | 9.2019
47 | 0.37071 | 0.17264 | -0.37066 | -0.17918 | 5.1942e-05 | -0.0065391 | 0.011834 | 0.011916 | 0.011916 | 0.99752 | 0.0048712 | 0.99739 | 0.0060372 | 5.4163
48 | -0.26432 | -0.12295 | 0.26432 | 0.12265 | 1.2255e-06 | -0.0003057 | 0.0084398 | 0.0084361 | 0.0084398 | 0.99712 | -0.085129 | 0.99712 | -0.085166 | 3.8363
49 | -0.89728 | -0.42545 | 0.89732 | 0.4247 | 3.5198e-05 | -0.00074709 | 0.028749 | 0.02874 | 0.028749 | 0.99712 | -0.085166 | 0.99716 | -0.085491 | 13.0679
50 | 0.31273 | 0.14771 | -0.31272 | -0.14775 | 7.2885e-06 | -4.3861e-05 | 0.010013 | 0.010013 | 0.010013 | 0.99712 | -0.085166 | 0.9971 | -0.085334 | 4.7683
51 | 0.31272 | 0.14775 | -0.3127 | -0.15145 | 2.0965e-05 | -0.0036943 | 0.010013 | 0.01006 | 0.01006 | 0.9971 | -0.085334 | 0.99703 | -0.084766 | 4.5726
52 | 3.5189 | 1.5794 | -3.5188 | -1.5816 | 0.00014251 | -0.0021502 | 0.11265 | 0.11267 | 0.11267 | 0.98844 | -0.47408 | 0.98839 | -0.4743 | 17.6606
53 | 3.4032 | 1.5256 | -3.4029 | -1.5303 | 0.00029399 | -0.0047535 | 0.10893 | 0.10898 | 0.10898 | 0.98839 | -0.4743 | 0.98831 | -0.47477 | 17.0822
54 | -6.3158 | -2.8238 | 6.317 | 2.8186 | 0.0011437 | -0.0051504 | 0.20005 | 0.19998 | 0.20005 | 0.99831 | -0.0090829 | 0.9985 | -0.0080756 | 31.3562
55 | 0.44404 | 0.21251 | -0.44403 | -0.21379 | 1.465e-05 | -0.0012829 | 0.014235 | 0.014251 | 0.014251 | 0.99831 | -0.0090829 | 0.99828 | -0.0088011 | 6.4776
56 | -6.4143 | -2.8658 | 6.4149 | 2.8631 | 0.00061684 | -0.0026848 | 0.20311 | 0.20307 | 0.20311 | 0.9985 | -0.0080756 | 0.9986 | -0.0075402 | 31.8354
57 | 0.084055 | 0.039448 | -0.084055 | -0.04071 | 5.1319e-07 | -0.0012612 | 0.002685 | 0.0027007 | 0.0027007 | 0.99828 | -0.0088011 | 0.99828 | -0.0087497 | 1.2276
58 | 3.177 | 1.4236 | -3.1758 | -1.4209 | 0.0011803 | 0.0027425 | 0.10169 | 0.10169 | 0.10169 | 0.98831 | -0.47477 | 0.98763 | -0.51452 | 15.7662
59 | 0.22595 | 0.1067 | -0.22594 | -0.10943 | 8.3681e-06 | -0.0027287 | 0.0072987 | 0.0073331 | 0.0073331 | 0.98831 | -0.47477 | 0.98827 | -0.47446 | 3.3332
60 | -6.7325 | -3.0161 | 6.7366 | 3.0001 | 0.0041096 | -0.016039 | 0.21326 | 0.21304 | 0.21326 | 0.9986 | -0.0075402 | 0.99924 | -0.0041464 | 33.4264
61 | 0.31757 | 0.15303 | -0.31756 | -0.1538 | 4.5292e-06 | -0.00077576 | 0.01019 | 0.0102 | 0.0102 | 0.9986 | -0.0075402 | 0.99859 | -0.0074167 | 4.6365
62 | -6.8532 | -3.0552 | 6.8582 | 3.0364 | 0.0049991 | -0.018827 | 0.21677 | 0.21651 | 0.21677 | 0.99924 | -0.0041464 | 1 | 0 | 33.9761
63 | 0.11654 | 0.055092 | -0.11654 | -0.056444 | 1.0547e-06 | -0.0013515 | 0.0037241 | 0.003741 | 0.003741 | 0.99924 | -0.0041464 | 0.99923 | -0.0040696 | 1.7004
64 | 7.8727 | 3.6401 | -7.8727 | -3.6403 | 6.91e-05 | -0.00018521 | 0.25038 | 0.25039 | 0.25039 | 1 | 0 | 0.99999 | -4.1731e-05 | 39.2455
65 | 7.6518 | 3.5334 | -7.6507 | -3.5367 | 0.0011748 | -0.0033723 | 0.2433 | 0.24335 | 0.24335 | 0.99999 | -4.1731e-05 | 0.99983 | -0.00077458 | 38.1432
66 | 5.991 | 2.7735 | -5.9864 | -2.7615 | 0.004649 | 0.012007 | 0.19061 | 0.19062 | 0.19062 | 0.99983 | -0.00077458 | 0.9984 | -0.082396 | 29.5531
67 | 1.4117 | 0.6433 | -1.4106 | -0.64297 | 0.0011167 | 0.000327 | 0.044792 | 0.044797 | 0.044797 | 0.99983 | -0.00077458 | 0.99899 | -0.0071798 | 21.3317
68 | 0.24794 | 0.11994 | -0.24793 | -0.12008 | 1.3417e-05 | -0.00013367 | 0.0079522 | 0.007954 | 0.007954 | 0.99983 | -0.00077458 | 0.99977 | -0.0011321 | 3.7876
69 | 3.1758 | 1.4209 | -3.1754 | -1.4283 | 0.0004002 | -0.0074423 | 0.10169 | 0.10178 | 0.10178 | 0.98763 | -0.51452 | 0.9875 | -0.51521 | 15.9536
70 | 2.6558 | 1.2417 | -2.6556 | -1.2469 | 0.00019501 | -0.0051503 | 0.085703 | 0.085769 | 0.085769 | 0.9875 | -0.51521 | 0.98743 | -0.51553 | 13.4434
71 | 0.51957 | 0.18662 | -0.51949 | -0.24793 | 8.3888e-05 | -0.061312 | 0.016139 | 0.01683 | 0.01683 | 0.9875 | -0.51521 | 0.98733 | -0.51635 | 2.6379
72 | -0.20368 | -0.098647 | 0.20368 | 0.097903 | 1.8699e-06 | -0.00074344 | 0.0066206 | 0.0066111 | 0.0066206 | 0.98678 | -0.53327 | 0.98679 | -0.53335 | 3.0094
73 | -0.20368 | -0.097903 | 0.20368 | 0.096958 | 2.3699e-06 | -0.0009453 | 0.0066111 | 0.0065992 | 0.0066111 | 0.98679 | -0.53335 | 0.9868 | -0.53345 | 3.0051
74 | -1.5733 | -0.75687 | 1.5734 | 0.75308 | 5.0253e-05 | -0.0037899 | 0.051074 | 0.051026 | 0.051074 | 0.9868 | -0.53345 | 0.98683 | -0.53332 | 8.0054
75 | 1.3696 | 0.65991 | -1.3696 | -0.66333 | 3.4412e-05 | -0.0034218 | 0.044475 | 0.044519 | 0.044519 | 0.9868 | -0.53345 | 0.98677 | -0.53354 | 6.9779
76 | -2.0924 | -0.99876 | 2.0925 | 0.99204 | 0.00015795 | -0.0067196 | 0.067823 | 0.067737 | 0.067823 | 0.98683 | -0.53332 | 0.98691 | -0.53302 | 10.6306
77 | 0.51899 | 0.24568 | -0.51898 | -0.25136 | 8.1294e-06 | -0.0056767 | 0.016797 | 0.016869 | 0.016869 | 0.98683 | -0.53332 | 0.98681 | -0.53339 | 2.644
78 | 0.20877 | 0.10104 | -0.20877 | -0.10111 | 5.162e-06 | -6.9947e-05 | 0.0067842 | 0.0067852 | 0.0067852 | 0.98691 | -0.53302 | 0.98688 | -0.53318 | 3.231
79 | -2.3013 | -1.0931 | 2.3018 | 1.0749 | 0.0005172 | -0.018215 | 0.074521 | 0.074291 | 0.074521 | 0.98691 | -0.53302 | 0.98714 | -0.53204 | 11.6805
80 | -0.44582 | -0.21429 | 0.44582 | 0.21326 | 1.089e-06 | -0.0010322 | 0.014463 | 0.01445 | 0.014463 | 0.98732 | -0.51714 | 0.98732 | -0.51713 | 2.2669
81 | 0.081972 | 0.038073 | -0.081972 | -0.039111 | 3.6744e-08 | -0.0010379 | 0.0026426 | 0.0026556 | 0.0026556 | 0.98732 | -0.51714 | 0.98731 | -0.51715 | 0.41623
82 | -0.44582 | -0.21326 | 0.44583 | 0.2123 | 1.014e-06 | -0.00096286 | 0.01445 | 0.014438 | 0.01445 | 0.98732 | -0.51713 | 0.98732 | -0.51713 | 2.2649
83 | 0.081972 | 0.039111 | -0.081972 | -0.039512 | 1.625e-07 | -0.00040092 | 0.0026556 | 0.0026606 | 0.0026606 | 0.98731 | -0.51715 | 0.98731 | -0.51713 | 1.2094
84 | -0.51949 | -0.24797 | 0.51949 | 0.24793 | 3.9183e-06 | -4.1676e-05 | 0.016831 | 0.01683 | 0.016831 | 0.98732 | -0.51713 | 0.98733 | -0.51635 | 2.6094
85 | 0.081972 | 0.039512 | -0.081972 | -0.039701 | 7.6869e-08 | -0.0001891 | 0.0026606 | 0.002663 | 0.002663 | 0.98731 | -0.51713 | 0.98731 | -0.51712 | 1.2105
86 | 2.5242 | 1.1832 | -2.5238 | -1.1824 | 0.00039954 | 0.0008474 | 0.081502 | 0.081505 | 0.081505 | 0.98743 | -0.51553 | 0.98714 | -0.53204 | 12.6364
87 | -4.397 | -2.0485 | 4.3971 | 2.048 | 5.5088e-05 | -0.00053447 | 0.14039 | 0.14038 | 0.14039 | 0.99745 | -0.086765 | 0.99746 | -0.086707 | 22.0045
88 | 4.0398 | 1.8755 | -4.0397 | -1.8769 | 0.00011846 | -0.0013753 | 0.1289 | 0.12892 | 0.12892 | 0.99745 | -0.086765 | 0.99742 | -0.086901 | 20.2072
89 | 0.069339 | 0.032668 | -0.069338 | -0.033218 | 1.525e-07 | -0.00054974 | 0.0022183 | 0.0022251 | 0.0022251 | 0.99746 | -0.086707 | 0.99746 | -0.086689 | 1.0114
90 | -4.4664 | -2.0807 | 4.4673 | 2.0726 | 0.00085951 | -0.0080751 | 0.1426 | 0.1425 | 0.1426 | 0.99746 | -0.086707 | 0.99766 | -0.085817 | 22.3512
91 | 4.0397 | 1.8769 | -4.0396 | -1.8774 | 0.00014958 | -0.00052713 | 0.12892 | 0.12893 | 0.12893 | 0.99742 | -0.086901 | 0.99738 | -0.087358 | 35.6159
92 | 0.069338 | 0.033218 | -0.069338 | -0.033582 | 1.0155e-07 | -0.00036417 | 0.0022251 | 0.0022297 | 0.0022297 | 0.99746 | -0.086689 | 0.99746 | -0.086676 | 1.0135
93 | -4.4673 | -2.0726 | 4.4675 | 2.0702 | 0.00024996 | -0.0023514 | 0.1425 | 0.14247 | 0.1425 | 0.99766 | -0.085817 | 0.99772 | -0.085554 | 22.3348
94 | 3.9681 | 1.8428 | -3.9673 | -1.8434 | 0.00078194 | -0.00063537 | 0.12663 | 0.12664 | 0.12664 | 0.99738 | -0.087358 | 0.99719 | -0.085799 | 57.5645
95 | -4.6215 | -2.1448 | 4.6215 | 2.1445 | 2.9386e-05 | -0.00025717 | 0.14741 | 0.14741 | 0.14741 | 0.99772 | -0.085554 | 0.99772 | -0.085525 | 23.1058
96 | 3.9673 | 1.8434 | -3.9672 | -1.8436 | 0.0001541 | -0.00012516 | 0.12664 | 0.12664 | 0.12664 | 0.99719 | -0.085799 | 0.99716 | -0.085491 | 57.5654
97 | -4.6215 | -2.1445 | 4.6237 | 2.1254 | 0.0021864 | -0.019179 | 0.14741 | 0.14716 | 0.14741 | 0.99772 | -0.085525 | 0.99821 | -0.083263 | 23.1053
98 | 4.8259 | 2.2149 | -4.8255 | -2.2183 | 0.00042426 | -0.0034079 | 0.15353 | 0.15357 | 0.15357 | 0.9984 | -0.082396 | 0.99831 | -0.082828 | 24.0713
99 | 1.1604 | 0.54656 | -1.1602 | -0.54884 | 0.00018013 | -0.002279 | 0.037088 | 0.037117 | 0.037117 | 0.9984 | -0.082396 | 0.99825 | -0.08112 | 16.8712
100 | 1.4106 | 0.64297 | -1.4104 | -0.64435 | 0.00016022 | -0.0013768 | 0.044797 | 0.044814 | 0.044814 | 0.99899 | -0.0071798 | 0.99888 | -0.0063196 | 20.3698
101 | 3.0698 | 1.4189 | -3.0689 | -1.4203 | 0.00090421 | -0.0014085 | 0.097905 | 0.097925 | 0.097925 | 0.99716 | -0.085491 | 0.99688 | -0.083185 | 44.5115
102 | 0.069443 | 0.033023 | -0.069443 | -0.033633 | 1.7087e-07 | -0.00061034 | 0.0022267 | 0.0022344 | 0.0022344 | 0.99688 | -0.083185 | 0.99688 | -0.083164 | 1.0156
103 | 2.9995 | 1.3873 | -2.9978 | -1.3901 | 0.0017079 | -0.0028047 | 0.095699 | 0.095739 | 0.095739 | 0.99688 | -0.083185 | 0.99635 | -0.078712 | 43.5177
104 | 2.9978 | 1.3901 | -2.9973 | -1.3909 | 0.0004952 | -0.00081204 | 0.095739 | 0.095751 | 0.095751 | 0.99635 | -0.078712 | 0.9962 | -0.077409 | 43.523
105 | -1.08 | -0.51219 | 1.08 | 0.51135 | 5.7051e-05 | -0.00083427 | 0.034566 | 0.034556 | 0.034566 | 0.9982 | -0.080682 | 0.99825 | -0.08112 | 15.712
106 | 0.49057 | 0.23121 | -0.49055 | -0.23265 | 1.9954e-05 | -0.001438 | 0.015684 | 0.015702 | 0.015702 | 0.9982 | -0.080682 | 0.99817 | -0.080347 | 7.1371
107 | 0.20119 | 0.092959 | -0.20118 | -0.097255 | 9.9918e-06 | -0.004296 | 0.0064093 | 0.0064625 | 0.0064625 | 0.9982 | -0.080682 | 0.99816 | -0.080273 | 2.9375
108 | 0.080229 | 0.037482 | -0.080229 | -0.038857 | 5.0904e-07 | -0.0013742 | 0.0025608 | 0.0025779 | 0.0025779 | 0.99825 | -0.08112 | 0.99825 | -0.081067 | 1.1718
109 | 0.49055 | 0.23265 | -0.49051 | -0.23554 | 4.0268e-05 | -0.0028916 | 0.015702 | 0.015738 | 0.015738 | 0.99817 | -0.080347 | 0.99809 | -0.079655 | 7.1535
110 | 0.083861 | 0.040435 | -0.083859 | -0.040615 | 1.9685e-06 | -0.00017988 | 0.0026925 | 0.0026948 | 0.0026948 | 0.99816 | -0.080273 | 0.99813 | -0.080429 | 1.2832
111 | 0.22481 | 0.10686 | -0.2248 | -0.10888 | 5.8965e-06 | -0.002018 | 0.0071993 | 0.0072246 | 0.0072246 | 0.99809 | -0.079655 | 0.99807 | -0.079431 | 3.2839
112 | 4.7292 | 2.1717 | -4.7288 | -2.1752 | 0.00042052 | -0.0035251 | 0.15048 | 0.15053 | 0.15053 | 0.99831 | -0.082828 | 0.99821 | -0.083263 | 23.5934
113 | 0.10503 | 0.049841 | -0.10503 | -0.05087 | 6.5546e-07 | -0.0010292 | 0.0033621 | 0.003375 | 0.003375 | 0.99821 | -0.083263 | 0.99821 | -0.08321 | 1.5341
114 | 1.219 | 0.55163 | -1.2189 | -0.553 | 0.00011809 | -0.0013736 | 0.038668 | 0.038685 | 0.038685 | 0.99888 | -0.0063196 | 0.99879 | -0.0055989 | 17.584
115 | 1.2189 | 0.553 | -1.2184 | -0.55826 | 0.00045281 | -0.0052532 | 0.038685 | 0.038749 | 0.038749 | 0.99879 | -0.0055989 | 0.99844 | -0.0027911 | 17.6134
116 | 0.18745 | 0.088453 | -0.18745 | -0.090785 | 4.722e-06 | -0.0023315 | 0.0059928 | 0.0060219 | 0.0060219 | 0.99844 | -0.0027911 | 0.99842 | -0.0025779 | 2.7372
117 | 1.031 | 0.4698 | -1.0304 | -0.47951 | 0.00059715 | -0.0097037 | 0.032757 | 0.032877 | 0.032877 | 0.99844 | -0.0027911 | 0.9979 | 0.0016977 | 14.9439
118 | 0.3974 | 0.19228 | -0.3974 | -0.19247 | 1.6917e-06 | -0.00018419 | 0.012771 | 0.012773 | 0.012773 | 0.9979 | 0.0016977 | 0.9979 | 0.0017348 | 5.8061
119 | -0.37066 | -0.17952 | 0.37066 | 0.17918 | 2.6727e-06 | -0.00033399 | 0.01192 | 0.011916 | 0.01192 | 0.99739 | 0.0060999 | 0.99739 | 0.0060372 | 5.4182

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 14.7449 | 6.687

## res_load
| p_mw | q_mvar
0 | 0.18492 | 0.089562
1 | 0.24819 | 0.1202
2 | 0.35251 | 0.17073
3 | 0.33184 | 0.16072
4 | 0.3024 | 0.14646
5 | 0.37642 | 0.18231
6 | 0.39296 | 0.19032
7 | 0.32141 | 0.15567
8 | 0.056281 | 0.027258
9 | 0.39638 | 0.19197
10 | 0.14609 | 0.070755
11 | 0.23247 | 0.11259
12 | 0.41297 | 0.20001
13 | 0.19511 | 0.094494
14 | 0.25102 | 0.12158
15 | 0.10337 | 0.050062
16 | 0.26201 | 0.1269
17 | 0.069984 | 0.033895
18 | 0.090935 | 0.044042
19 | 0.32023 | 0.15509
20 | 0.3127 | 0.15145
21 | 0.11557 | 0.055975
22 | 0.35374 | 0.17132
23 | 0.33576 | 0.16262
24 | 0.097359 | 0.047153
25 | 0.35997 | 0.17434
26 | 0.084055 | 0.04071
27 | 0.31756 | 0.1538
28 | 0.11654 | 0.056444
29 | 0.22082 | 0.10695
30 | 0.22594 | 0.10943
31 | 0.20368 | 0.098647
32 | 1.3696 | 0.66333
33 | 0.51898 | 0.25136
34 | 0.36385 | 0.17622
35 | 0.07366 | 0.035675
36 | 0.13136 | 0.06362
37 | 0.081972 | 0.039701
38 | 0.22203 | 0.10754
39 | 0.35719 | 0.17299
40 | 0.071478 | 0.034618
41 | 0.069338 | 0.033582
42 | 0.15397 | 0.074573
43 | 0.24793 | 0.12008
44 | 0.069443 | 0.033633
45 | 0.12892 | 0.062437
46 | 0.38821 | 0.18802
47 | 0.11732 | 0.05682
48 | 0.080229 | 0.038857
49 | 0.2657 | 0.12868
50 | 0.083859 | 0.040615
51 | 0.09633 | 0.046655
52 | 0.2248 | 0.10888
53 | 0.10503 | 0.05087
54 | 0.19144 | 0.092721
55 | 0.18745 | 0.090785
56 | 0.37066 | 0.17952
57 | 0.3974 | 0.19247
58 | 0.27819 | 0.13473
59 | 0.20877 | 0.10111

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1