## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_7_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_7_0_node_15 | 20 | n |  | TRUE
2 | bus_MV_7_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_7_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_7_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_7_0_node_196 | 20 | n |  | TRUE
6 | bus_MV_7_0_node_6 | 20 | n |  | TRUE
7 | bus_MV_7_0_node_5 | 20 | n |  | TRUE
8 | bus_MV_7_0_node_207 | 20 | n |  | TRUE
9 | bus_MV_7_0_node_197 | 20 | n |  | TRUE
10 | bus_MV_7_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_7_0_node_52 | 20 | n |  | TRUE
12 | bus_MV_7_0_node_54 | 20 | n |  | TRUE
13 | bus_MV_7_0_node_55 | 20 | n |  | TRUE
14 | bus_MV_7_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_7_0_node_9 | 20 | n |  | TRUE
16 | bus_MV_7_0_node_10 | 20 | n |  | TRUE
17 | bus_MV_7_0_node_11 | 20 | n |  | TRUE
18 | bus_MV_7_0_node_12 | 20 | n |  | TRUE
19 | bus_MV_7_0_node_13 | 20 | n |  | TRUE
20 | bus_MV_7_0_node_14 | 20 | n |  | TRUE
21 | bus_MV_7_0_node_51 | 20 | n |  | TRUE
22 | bus_MV_7_0_node_44 | 20 | n |  | TRUE
23 | bus_MV_7_0_node_188 | 20 | n |  | TRUE
24 | bus_MV_7_0_node_37 | 20 | n |  | TRUE
25 | bus_MV_7_0_node_16 | 20 | n |  | TRUE
26 | bus_MV_7_0_node_17 | 20 | n |  | TRUE
27 | bus_MV_7_0_node_18 | 20 | n |  | TRUE
28 | bus_MV_7_0_node_30 | 20 | n |  | TRUE
29 | bus_MV_7_0_node_21 | 20 | n |  | TRUE
30 | bus_MV_7_0_node_206 | 20 | n |  | TRUE
31 | bus_MV_7_0_node_19 | 20 | n |  | TRUE
32 | bus_MV_7_0_node_203 | 20 | n |  | TRUE
33 | bus_MV_7_0_node_20 | 20 | n |  | TRUE
34 | bus_MV_7_0_node_22 | 20 | n |  | TRUE
35 | bus_MV_7_0_node_139 | 20 | n |  | TRUE
36 | bus_MV_7_0_node_23 | 20 | n |  | TRUE
37 | bus_MV_7_0_node_24 | 20 | n |  | TRUE
38 | bus_MV_7_0_node_25 | 20 | n |  | TRUE
39 | bus_MV_7_0_node_29 | 20 | n |  | TRUE
40 | bus_MV_7_0_node_27 | 20 | n |  | TRUE
41 | bus_MV_7_0_node_28 | 20 | n |  | TRUE
42 | bus_MV_7_0_node_183 | 20 | n |  | TRUE
43 | bus_MV_7_0_node_26 | 20 | n |  | TRUE
44 | bus_MV_7_0_node_49 | 20 | n |  | TRUE
45 | bus_MV_7_0_node_198 | 20 | n |  | TRUE
46 | bus_MV_7_0_node_33 | 20 | n |  | TRUE
47 | bus_MV_7_0_node_31 | 20 | n |  | TRUE
48 | bus_MV_7_0_node_32 | 20 | n |  | TRUE
49 | bus_MV_7_0_node_208 | 20 | n |  | TRUE
50 | bus_MV_7_0_node_34 | 20 | n |  | TRUE
51 | bus_MV_7_0_node_35 | 20 | n |  | TRUE
52 | bus_MV_7_0_node_36 | 20 | n |  | TRUE
53 | bus_MV_7_0_node_38 | 20 | n |  | TRUE
54 | bus_MV_7_0_node_48 | 20 | n |  | TRUE
55 | bus_MV_7_0_node_187 | 20 | n |  | TRUE
56 | bus_MV_7_0_node_39 | 20 | n |  | TRUE
57 | bus_MV_7_0_node_205 | 20 | n |  | TRUE
58 | bus_MV_7_0_node_47 | 20 | n |  | TRUE
59 | bus_MV_7_0_node_140 | 20 | n |  | TRUE
60 | bus_MV_7_0_node_40 | 20 | n |  | TRUE
61 | bus_MV_7_0_node_41 | 20 | n |  | TRUE
62 | bus_MV_7_0_node_43 | 20 | n |  | TRUE
63 | bus_MV_7_0_node_45 | 20 | n |  | TRUE
64 | bus_MV_7_0_node_184 | 20 | n |  | TRUE
65 | bus_MV_7_0_node_46 | 20 | n |  | TRUE
66 | bus_MV_7_0_node_199 | 20 | n |  | TRUE
67 | bus_MV_7_0_node_50 | 20 | n |  | TRUE
68 | bus_MV_7_0_node_53 | 20 | n |  | TRUE
69 | bus_MV_7_0_node_195 | 20 | n |  | TRUE
70 | bus_HV_7_0_node_7 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_7_0_load_0 | 0 | 0.068937 | 0.033388 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_7_0_load_15 | 1 | 0.066346 | 0.032133 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_7_0_load_1 | 2 | 0.057498 | 0.027848 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_7_0_load_196 | 5 | 0.10919 | 0.052881 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_7_0_load_207 | 8 | 0.15617 | 0.075636 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_7_0_load_52 | 11 | 0.10131 | 0.049068 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_7_0_load_55 | 13 | 0.11597 | 0.056169 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_7_0_load_8 | 14 | 0.093213 | 0.045145 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_7_0_load_51 | 21 | 0.11512 | 0.055754 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_7_0_load_44 | 22 | 1.0516 | 0.50932 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_7_0_load_188 | 23 | 0.10962 | 0.05309 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_7_0_load_30 | 28 | 0.14818 | 0.071768 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_7_0_load_206 | 30 | 0.15364 | 0.074413 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_7_0_load_203 | 32 | 0.091683 | 0.044404 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_7_0_load_22 | 34 | 0.06932 | 0.033573 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_7_0_load_139 | 35 | 0.14733 | 0.071356 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_7_0_load_24 | 37 | 0.39363 | 0.19064 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_7_0_load_29 | 39 | 0.10185 | 0.049326 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_7_0_load_183 | 42 | 0.15055 | 0.072916 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_7_0_load_49 | 44 | 0.12329 | 0.059712 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_7_0_load_198 | 45 | 0.063724 | 0.030863 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_7_0_load_33 | 46 | 0.12478 | 0.060431 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_7_0_load_208 | 49 | 0.36593 | 0.17723 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_7_0_load_34 | 50 | 0.056338 | 0.027286 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_7_0_load_48 | 54 | 0.12529 | 0.060679 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_7_0_load_187 | 55 | 0.14541 | 0.070426 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_7_0_load_205 | 57 | 0.10809 | 0.052351 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_7_0_load_140 | 59 | 0.11757 | 0.056944 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_7_0_load_40 | 60 | 0.13819 | 0.066929 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_7_0_load_41 | 61 | 0.12028 | 0.058252 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_7_0_load_43 | 62 | 0.16106 | 0.078003 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_7_0_load_184 | 64 | 0.10314 | 0.049953 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_7_0_load_46 | 65 | 0.054229 | 0.026264 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_7_0_load_199 | 66 | 0.10973 | 0.053146 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_7_0_load_50 | 67 | 0.16095 | 0.077949 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_7_0_load_53 | 68 | 0.058083 | 0.028131 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_7_0_line_0 |  | 0 | 1 | 0.75402 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_7_0_line_1 |  | 1 | 25 | 0.008955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_7_0_line_2 |  | 2 | 3 | 0.026165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_7_0_line_3 |  | 2 | 4 | 0.064021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_7_0_line_4 |  | 3 | 5 | 0.28797 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_7_0_line_5 |  | 4 | 6 | 0.28251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_7_0_line_6 |  | 5 | 69 | 0.051176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_7_0_line_7 |  | 6 | 10 | 0.69442 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
8 | MV_7_0_line_8 |  | 6 | 11 | 0.091765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_7_0_line_9 |  | 6 | 12 | 0.43279 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_7_0_line_10 |  | 7 | 8 | 0.013356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_7_0_line_11 |  | 7 | 9 | 0.044478 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_7_0_line_12 |  | 8 | 17 | 0.010461 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_7_0_line_13 |  | 9 | 69 | 0.44877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_7_0_line_14 |  | 10 | 13 | 0.040631 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_7_0_line_15 |  | 11 | 44 | 0.92505 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_7_0_line_16 |  | 12 | 68 | 0.046736 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_7_0_line_17 |  | 14 | 15 | 0.017724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_7_0_line_18 |  | 14 | 16 | 0.027726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_7_0_line_19 |  | 15 | 17 | 0.10627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_7_0_line_20 |  | 16 | 18 | 0.066041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_7_0_line_21 |  | 16 | 19 | 0.33436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_7_0_line_22 |  | 18 | 20 | 0.17129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_7_0_line_23 |  | 18 | 21 | 0.004411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_7_0_line_24 |  | 19 | 22 | 0.13677 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_7_0_line_25 |  | 20 | 23 | 0.042688 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_7_0_line_26 |  | 20 | 24 | 0.2869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_7_0_line_27 |  | 22 | 62 | 0.035161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_7_0_line_28 |  | 24 | 55 | 0.050131 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_7_0_line_29 |  | 24 | 53 | 0.17492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_7_0_line_30 |  | 24 | 56 | 0.37142 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_7_0_line_31 |  | 25 | 26 | 0.22687 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_7_0_line_32 |  | 25 | 27 | 0.65319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_7_0_line_33 |  | 26 | 28 | 0.081424 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_7_0_line_34 |  | 27 | 29 | 0.17745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_7_0_line_35 |  | 27 | 30 | 0.038992 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_7_0_line_36 |  | 28 | 47 | 0.004331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_7_0_line_37 |  | 29 | 35 | 0.016631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_7_0_line_38 |  | 29 | 31 | 0.25502 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_7_0_line_39 |  | 29 | 33 | 0.61424 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_7_0_line_40 |  | 31 | 32 | 0.041894 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_7_0_line_41 |  | 33 | 34 | 0.01047 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_7_0_line_42 |  | 34 | 36 | 0.023649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_7_0_line_43 |  | 34 | 37 | 0.024641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_7_0_line_44 |  | 36 | 38 | 0.72988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_7_0_line_45 |  | 37 | 39 | 0.044225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_7_0_line_46 |  | 38 | 40 | 0.26547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_7_0_line_47 |  | 38 | 41 | 1.0934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_7_0_line_48 |  | 38 | 42 | 0.067022 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_7_0_line_49 |  | 40 | 45 | 0.043567 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_7_0_line_50 |  | 41 | 46 | 0.028265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_7_0_line_51 |  | 41 | 43 | 0.32758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_7_0_line_52 |  | 43 | 44 | 0.057638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_7_0_line_53 |  | 47 | 48 | 0.033956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_7_0_line_54 |  | 48 | 49 | 0.013426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_7_0_line_55 |  | 50 | 51 | 0.067977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_7_0_line_56 |  | 51 | 52 | 0.97156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_7_0_line_57 |  | 52 | 53 | 0.41398 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_7_0_line_58 |  | 52 | 54 | 0.044648 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_7_0_line_59 |  | 53 | 57 | 0.006616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_7_0_line_60 |  | 56 | 58 | 0.72895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_7_0_line_61 |  | 56 | 59 | 0.10337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_7_0_line_62 |  | 58 | 65 | 0.005729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_7_0_line_63 |  | 60 | 61 | 0.11705 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_7_0_line_64 |  | 61 | 62 | 0.22291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_7_0_line_65 |  | 61 | 63 | 0.68594 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_7_0_line_66 |  | 63 | 64 | 0.36735 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_7_0_line_67 |  | 65 | 66 | 2.657 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_7_0_line_68 |  | 66 | 67 | 0.33796 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_7_0_trafo_7 | 25 MVA 110/20 kV | 70 | 10 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2707547.4602 | 1250682.0643
1 | 2706843.4917 | 1250411.9134
2 | 2708038.6715 | 1247495.6133
3 | 2708063.4274 | 1247486.9352
4 | 2707978.1623 | 1247517.0284
5 | 2708281.4202 | 1247675.0965
6 | 2707848.4983 | 1247660.9621
7 | 2708582.4137 | 1247382.0535
8 | 2708595.0939 | 1247377.7489
9 | 2708594.2899 | 1247424.9166
10 | 2707971.8236 | 1247789.4096
11 | 2707797.4549 | 1247725.6748
12 | 2707503.9078 | 1247399.106
13 | 2708011.4152 | 1247780.2789
14 | 2708609.045 | 1247257.9414
15 | 2708605.4182 | 1247275.2778
16 | 2708614.729 | 1247231.0016
17 | 2708596.9371 | 1247367.4522
18 | 2708672.0072 | 1247244.3506
19 | 2708430.1383 | 1246975.5405
20 | 2708754.2479 | 1247309.8999
21 | 2708673.1506 | 1247240.0903
22 | 2708330.8869 | 1246883.4893
23 | 2708752.4906 | 1247352.5464
24 | 2708970.8278 | 1247232.747
25 | 2706839.4363 | 1250419.9023
26 | 2706679.8713 | 1250375.1921
27 | 2706830.7369 | 1249840.578
28 | 2706727.2305 | 1250308.9579
29 | 2706742.4367 | 1249786.1434
30 | 2706820.0938 | 1249803.0671
31 | 2706609.7395 | 1249856.701
32 | 2706583.7811 | 1249823.7744
33 | 2707092.6639 | 1249575.6018
34 | 2707084.7686 | 1249568.698
35 | 2706731.1893 | 1249773.8924
36 | 2707089.2137 | 1249545.4707
37 | 2707078.5203 | 1249592.5339
38 | 2707391.3883 | 1249455.865
39 | 2707058.5522 | 1249624.9031
40 | 2707318.4288 | 1249622.9786
41 | 2707195.2402 | 1248844.8783
42 | 2707425.572 | 1249398.2157
43 | 2707396.1172 | 1248606.3997
44 | 2707379.8755 | 1248551.1166
45 | 2707317.3075 | 1249666.5267
46 | 2707174.7438 | 1248864.4013
47 | 2706728.6933 | 1250304.8809
48 | 2706740.9978 | 1250273.2325
49 | 2706753.773 | 1250277.4771
50 | 2708573.6352 | 1246700.4673
51 | 2708628.5693 | 1246740.5832
52 | 2709174.0446 | 1246987.287
53 | 2709060.4299 | 1247279.0871
54 | 2709194.8719 | 1247026.78
55 | 2708928.5761 | 1247206.6942
56 | 2709070.554 | 1247404.6411
57 | 2709061.0718 | 1247285.6708
58 | 2709449.7544 | 1247642.698
59 | 2709168.7697 | 1247372.5465
60 | 2708046.7132 | 1246643.1205
61 | 2708129.2323 | 1246726.1399
62 | 2708299.9635 | 1246866.7554
63 | 2707711.9226 | 1246181.7398
64 | 2707977.3294 | 1245927.7626
65 | 2709454.1818 | 1247646.3493
66 | 2711369.6512 | 1249487.7191
67 | 2711658.1687 | 1249311.7246
68 | 2707470.4266 | 1247399.0546
69 | 2708332.3438 | 1247671.3792
70 | 2707971.8236 | 1247789.4096

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98744 | -0.0078384 | 0.068937 | 0.033388
1 | 0.98754 | -0.0071654 | 0.066346 | 0.032133
2 | 0.99666 | -0.014844 | 0.057498 | 0.027848
3 | 0.99656 | -0.014085 | 0 | 0
4 | 0.99691 | -0.016738 | 0 | 0
5 | 0.99489 | -0.027774 | 0.10919 | 0.052881
6 | 0.99802 | -0.025014 | 0 | 0
7 | 0.99278 | -0.015721 | 0 | 0
8 | 0.99273 | -0.015339 | 0.15617 | 0.075636
9 | 0.99303 | -0.013707 | 0 | 0
10 | 1 | 0 | -5.5006 | -2.3987
11 | 0.99777 | -0.023271 | 0.10131 | 0.049068
12 | 0.99797 | -0.025369 | 0 | 0
13 | 0.99999 | -5.7025e-05 | 0.11597 | 0.056169
14 | 0.99226 | -0.011734 | 0.093213 | 0.045145
15 | 0.99232 | -0.012211 | 0 | 0
16 | 0.99216 | -0.011018 | 0 | 0
17 | 0.99269 | -0.01506 | 0 | 0
18 | 0.99207 | -0.010492 | 0 | 0
19 | 0.99149 | -0.0049312 | 0 | 0
20 | 0.99186 | -0.0093359 | 0 | 0
21 | 0.99207 | -0.010486 | 0.11512 | 0.055754
22 | 0.99121 | -0.0023901 | 1.0516 | 0.50932
23 | 0.99185 | -0.0092804 | 0.10962 | 0.05309
24 | 0.99154 | -0.0076624 | 0 | 0
25 | 0.98754 | -0.0071797 | 0 | 0
26 | 0.98739 | -0.0058069 | 0 | 0
27 | 0.98808 | -0.011729 | 0 | 0
28 | 0.98731 | -0.0063347 | 0.14818 | 0.071768
29 | 0.98827 | -0.013186 | 0 | 0
30 | 0.98807 | -0.011804 | 0.15364 | 0.074413
31 | 0.98824 | -0.012965 | 0 | 0
32 | 0.98823 | -0.01292 | 0.091683 | 0.044404
33 | 0.98908 | -0.019357 | 0 | 0
34 | 0.9891 | -0.019457 | 0.06932 | 0.033573
35 | 0.98826 | -0.013156 | 0.14733 | 0.071356
36 | 0.98914 | -0.019843 | 0 | 0
37 | 0.98908 | -0.01931 | 0.39363 | 0.19064
38 | 0.99064 | -0.031332 | 0 | 0
39 | 0.98907 | -0.019256 | 0.10185 | 0.049326
40 | 0.99062 | -0.031197 | 0 | 0
41 | 0.99317 | -0.049289 | 0 | 0
42 | 0.99062 | -0.031456 | 0.15055 | 0.072916
43 | 0.99398 | -0.054778 | 0 | 0
44 | 0.99412 | -0.055726 | 0.12329 | 0.059712
45 | 0.99062 | -0.031164 | 0.063724 | 0.030863
46 | 0.99317 | -0.049246 | 0.12478 | 0.060431
47 | 0.98731 | -0.0063155 | 0 | 0
48 | 0.98729 | -0.0061646 | 0 | 0
49 | 0.98728 | -0.0061044 | 0.36593 | 0.17723
50 | 0.99131 | -0.007439 | 0.056338 | 0.027286
51 | 0.99132 | -0.0074821 | 0 | 0
52 | 0.99139 | -0.0073296 | 0 | 0
53 | 0.99148 | -0.0074582 | 0 | 0
54 | 0.99137 | -0.0073985 | 0.12529 | 0.060679
55 | 0.99153 | -0.0075757 | 0.14541 | 0.070426
56 | 0.99133 | -0.006322 | 0 | 0
57 | 0.99148 | -0.0074495 | 0.10809 | 0.052351
58 | 0.99103 | -0.0040083 | 0 | 0
59 | 0.99132 | -0.0061822 | 0.11757 | 0.056944
60 | 0.99105 | -0.0014578 | 0.13819 | 0.066929
61 | 0.99108 | -0.0012581 | 0.12028 | 0.058252
62 | 0.99119 | -0.0021823 | 0.16106 | 0.078003
63 | 0.99095 | -0.0021781 | 0 | 0
64 | 0.99087 | -0.0026512 | 0.10314 | 0.049953
65 | 0.99103 | -0.0039869 | 0.054229 | 0.026264
66 | 0.98963 | -0.013297 | 0.10973 | 0.053146
67 | 0.98952 | -0.013974 | 0.16095 | 0.077949
68 | 0.99797 | -0.025338 | 0.058083 | 0.028131
69 | 0.9947 | -0.026354 | 0 | 0
70 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.068937 | -0.033388 | 0.068943 | 0.032514 | 6.7031e-06 | -0.00087358 | 0.0022393 | 0.0022282 | 0.0022393 | 0.98744 | -0.0078384 | 0.98754 | -0.0071654 | 1.0663
1 | -0.13529 | -0.064647 | 0.13529 | 0.064438 | 2.2952e-07 | -0.00020845 | 0.004383 | 0.0043804 | 0.004383 | 0.98754 | -0.0071654 | 0.98754 | -0.0071797 | 1.9923
2 | 3.0516 | 1.3565 | -3.0513 | -1.357 | 0.00032683 | -0.00052354 | 0.096726 | 0.096733 | 0.096733 | 0.99666 | -0.014844 | 0.99656 | -0.014085 | 43.9696
3 | -3.1091 | -1.3843 | 3.1099 | 1.3831 | 0.00083035 | -0.0012725 | 0.098575 | 0.098557 | 0.098575 | 0.99666 | -0.014844 | 0.99691 | -0.016738 | 44.807
4 | 3.0513 | 1.357 | -3.0465 | -1.3544 | 0.0048012 | 0.0026665 | 0.096733 | 0.096737 | 0.096737 | 0.99656 | -0.014085 | 0.99489 | -0.027774 | 46.0653
5 | -3.1099 | -1.3831 | 3.1136 | 1.3774 | 0.0036605 | -0.0056252 | 0.098557 | 0.098479 | 0.098557 | 0.99691 | -0.016738 | 0.99802 | -0.025014 | 44.7988
6 | 2.9373 | 1.3015 | -2.9367 | -1.3025 | 0.00059378 | -0.0010331 | 0.093219 | 0.093233 | 0.093233 | 0.99489 | -0.027774 | 0.9947 | -0.026354 | 42.3787
7 | -5.361 | -2.3489 | 5.3706 | 2.3321 | 0.0095977 | -0.016801 | 0.1693 | 0.16902 | 0.1693 | 0.99802 | -0.025014 | 1 | 0 | 46.7673
8 | 2.1894 | 0.94496 | -2.1888 | -0.94697 | 0.00058302 | -0.0020088 | 0.068974 | 0.068999 | 0.068999 | 0.99802 | -0.025014 | 0.99777 | -0.023271 | 31.3631
9 | 0.058086 | 0.026507 | -0.058083 | -0.027019 | 2.6388e-06 | -0.00051295 | 0.0018468 | 0.001853 | 0.001853 | 0.99802 | -0.025014 | 0.99797 | -0.025369 | 0.88238
10 | 2.9308 | 1.3112 | -2.9306 | -1.3114 | 0.00015541 | -0.00026818 | 0.093359 | 0.093363 | 0.093363 | 0.99278 | -0.015721 | 0.99273 | -0.015339 | 42.4376
11 | -2.9308 | -1.3112 | 2.9315 | 1.3115 | 0.0006907 | 0.00038028 | 0.093359 | 0.093358 | 0.093359 | 0.99278 | -0.015721 | 0.99303 | -0.013707 | 44.4566
12 | 2.7744 | 1.2358 | -2.7743 | -1.236 | 0.00010894 | -0.00021383 | 0.088319 | 0.088322 | 0.088322 | 0.99273 | -0.015339 | 0.99269 | -0.01506 | 40.1465
13 | -2.9315 | -1.3115 | 2.9367 | 1.3025 | 0.0052147 | -0.0090369 | 0.093358 | 0.093233 | 0.093358 | 0.99303 | -0.013707 | 0.9947 | -0.026354 | 42.4356
14 | 0.11597 | 0.056121 | -0.11597 | -0.056169 | 1.0016e-06 | -4.7878e-05 | 0.0037193 | 0.0037199 | 0.0037199 | 1 | 0 | 0.99999 | -5.7025e-05 | 1.7714
15 | 2.0875 | 0.89791 | -2.0804 | -0.89454 | 0.0071255 | 0.0033678 | 0.065745 | 0.065758 | 0.065758 | 0.99777 | -0.023271 | 0.99412 | -0.055726 | 31.3132
16 | 0.058083 | 0.027019 | -0.058083 | -0.028131 | 2.1582e-07 | -0.0011113 | 0.001853 | 0.0018668 | 0.0018668 | 0.99797 | -0.025369 | 0.99797 | -0.025338 | 0.84854
17 | -2.773 | -1.2385 | 2.7732 | 1.2382 | 0.00018471 | -0.00036189 | 0.088357 | 0.088352 | 0.088357 | 0.99226 | -0.011734 | 0.99232 | -0.012211 | 40.1622
18 | 2.6798 | 1.1934 | -2.6796 | -1.194 | 0.00026963 | -0.00057173 | 0.085345 | 0.085353 | 0.085353 | 0.99226 | -0.011734 | 0.99216 | -0.011018 | 38.7967
19 | -2.7732 | -1.2382 | 2.7743 | 1.236 | 0.0011071 | -0.0021711 | 0.088352 | 0.088322 | 0.088352 | 0.99232 | -0.012211 | 0.99269 | -0.01506 | 40.1599
20 | 1.1036 | 0.44948 | -1.1035 | -0.451 | 0.00010603 | -0.0015206 | 0.034671 | 0.034688 | 0.034688 | 0.99216 | -0.011018 | 0.99207 | -0.010492 | 15.7671
21 | 1.576 | 0.74448 | -1.5748 | -0.75199 | 0.0011502 | -0.007512 | 0.050713 | 0.050811 | 0.050811 | 0.99216 | -0.011018 | 0.99149 | -0.0049312 | 23.0959
22 | 0.98836 | 0.39535 | -0.98814 | -0.39931 | 0.00021972 | -0.0039592 | 0.030975 | 0.031019 | 0.031019 | 0.99207 | -0.010492 | 0.99186 | -0.0093359 | 14.0995
23 | 0.11512 | 0.055651 | -0.11512 | -0.055754 | 8.154e-08 | -0.00010363 | 0.0037206 | 0.0037219 | 0.0037219 | 0.99207 | -0.010492 | 0.99207 | -0.010486 | 1.6918
24 | 1.5748 | 0.75199 | -1.5744 | -0.75506 | 0.00047178 | -0.0030694 | 0.050811 | 0.050851 | 0.050851 | 0.99149 | -0.0049312 | 0.99121 | -0.0023901 | 23.1142
25 | 0.10962 | 0.052087 | -0.10962 | -0.05309 | 7.1355e-07 | -0.0010025 | 0.0035322 | 0.0035448 | 0.0035448 | 0.99186 | -0.0093359 | 0.99185 | -0.0092804 | 1.6113
26 | 0.87852 | 0.34723 | -0.87823 | -0.35388 | 0.00029028 | -0.0066506 | 0.027494 | 0.027566 | 0.027566 | 0.99186 | -0.0093359 | 0.99154 | -0.0076624 | 12.5302
27 | 0.52274 | 0.24574 | -0.52273 | -0.24656 | 1.3292e-05 | -0.00082085 | 0.016822 | 0.016833 | 0.016833 | 0.99121 | -0.0023901 | 0.99119 | -0.0021823 | 7.6512
28 | 0.14541 | 0.069249 | -0.14541 | -0.070426 | 1.4761e-06 | -0.0011763 | 0.0046891 | 0.0047039 | 0.0047039 | 0.99154 | -0.0076624 | 0.99153 | -0.0075757 | 2.1381
29 | 0.28976 | 0.10191 | -0.28974 | -0.10601 | 1.8758e-05 | -0.0041003 | 0.0089425 | 0.0089829 | 0.0089829 | 0.99154 | -0.0076624 | 0.99148 | -0.0074582 | 4.0831
30 | 0.44306 | 0.18272 | -0.44297 | -0.19141 | 9.7215e-05 | -0.0086881 | 0.013953 | 0.014052 | 0.014052 | 0.99154 | -0.0076624 | 0.99133 | -0.006322 | 6.3872
31 | 0.51424 | 0.24247 | -0.51416 | -0.24772 | 8.3985e-05 | -0.0052568 | 0.016619 | 0.016686 | 0.016686 | 0.98754 | -0.0071797 | 0.98739 | -0.0058069 | 7.5844
32 | -0.64953 | -0.3069 | 0.64991 | 0.2918 | 0.00038111 | -0.015105 | 0.021 | 0.020814 | 0.021 | 0.98754 | -0.0071797 | 0.98808 | -0.011729 | 9.5453
33 | 0.51416 | 0.24772 | -0.51412 | -0.24779 | 4.0393e-05 | -6.946e-05 | 0.016686 | 0.016687 | 0.016687 | 0.98739 | -0.0058069 | 0.98731 | -0.0063347 | 7.9462
34 | -0.80356 | -0.36617 | 0.80371 | 0.36208 | 0.00015737 | -0.0040905 | 0.025799 | 0.025749 | 0.025799 | 0.98808 | -0.011729 | 0.98827 | -0.013186 | 11.7268
35 | 0.15365 | 0.074369 | -0.15364 | -0.074413 | 1.728e-06 | -4.4363e-05 | 0.004987 | 0.0049876 | 0.0049876 | 0.98808 | -0.011729 | 0.98807 | -0.011804 | 2.3751
36 | 0.36593 | 0.17602 | -0.36593 | -0.17613 | 8.1516e-07 | -0.00010056 | 0.011873 | 0.011874 | 0.011874 | 0.98731 | -0.0063347 | 0.98731 | -0.0063155 | 5.3974
37 | 0.14733 | 0.070968 | -0.14733 | -0.071356 | 5.0715e-07 | -0.00038767 | 0.0047769 | 0.0047818 | 0.0047818 | 0.98827 | -0.013186 | 0.98826 | -0.013156 | 2.1735
38 | 0.091687 | 0.037482 | -0.091684 | -0.043427 | 2.9174e-06 | -0.0059459 | 0.0028933 | 0.0029634 | 0.0029634 | 0.98827 | -0.013186 | 0.98824 | -0.012965 | 1.347
39 | -1.0427 | -0.47053 | 1.0436 | 0.45646 | 0.00091096 | -0.014065 | 0.033416 | 0.033246 | 0.033416 | 0.98827 | -0.013186 | 0.98908 | -0.019357 | 15.1891
40 | 0.091684 | 0.043427 | -0.091683 | -0.044404 | 4.932e-07 | -0.00097672 | 0.0029634 | 0.0029758 | 0.0029758 | 0.98824 | -0.012965 | 0.98823 | -0.01292 | 1.3526
41 | -1.0436 | -0.45646 | 1.0437 | 0.45622 | 1.5448e-05 | -0.00023998 | 0.033246 | 0.033243 | 0.033246 | 0.98908 | -0.019357 | 0.9891 | -0.019457 | 15.1118
42 | -1.6085 | -0.72816 | 1.6086 | 0.72763 | 8.3824e-05 | -0.00052756 | 0.051531 | 0.051524 | 0.051531 | 0.9891 | -0.019457 | 0.98914 | -0.019843 | 23.4231
43 | 0.49549 | 0.23837 | -0.49548 | -0.23894 | 8.4754e-06 | -0.00057305 | 0.016048 | 0.016055 | 0.016055 | 0.9891 | -0.019457 | 0.98908 | -0.01931 | 7.2977
44 | -1.6086 | -0.72763 | 1.6111 | 0.71132 | 0.0025765 | -0.016312 | 0.051524 | 0.051321 | 0.051524 | 0.98914 | -0.019843 | 0.99064 | -0.031332 | 23.42
45 | 0.10185 | 0.048293 | -0.10185 | -0.049326 | 6.4149e-07 | -0.0010328 | 0.0032898 | 0.0033028 | 0.0033028 | 0.98908 | -0.01931 | 0.98907 | -0.019256 | 1.5013
46 | 0.063726 | 0.023623 | -0.063725 | -0.029842 | 1.4372e-06 | -0.0062197 | 0.0019805 | 0.0020505 | 0.0020505 | 0.99064 | -0.031332 | 0.99062 | -0.031197 | 0.93206
47 | -1.8254 | -0.80778 | 1.8303 | 0.78356 | 0.0049134 | -0.024227 | 0.058168 | 0.05787 | 0.058168 | 0.99064 | -0.031332 | 0.99317 | -0.049289 | 26.4402
48 | 0.15056 | 0.072839 | -0.15055 | -0.072916 | 2.837e-06 | -7.6742e-05 | 0.0048737 | 0.0048747 | 0.0048747 | 0.99064 | -0.031332 | 0.99062 | -0.031456 | 2.3213
49 | 0.063725 | 0.029842 | -0.063724 | -0.030863 | 2.4607e-07 | -0.0010207 | 0.0020505 | 0.0020633 | 0.0020633 | 0.99062 | -0.031197 | 0.99062 | -0.031164 | 0.93787
50 | 0.12478 | 0.059766 | -0.12478 | -0.060431 | 6.1146e-07 | -0.00066549 | 0.0040213 | 0.0040297 | 0.0040297 | 0.99317 | -0.049289 | 0.99317 | -0.049246 | 1.8317
51 | -1.9551 | -0.84332 | 1.9568 | 0.8361 | 0.0016726 | -0.0072251 | 0.061888 | 0.0618 | 0.061888 | 0.99317 | -0.049289 | 0.99398 | -0.054778 | 28.131
52 | -1.9568 | -0.8361 | 1.9571 | 0.83483 | 0.0002938 | -0.0012727 | 0.0618 | 0.061784 | 0.0618 | 0.99398 | -0.054778 | 0.99412 | -0.055726 | 28.0907
53 | 0.36593 | 0.17613 | -0.36593 | -0.17691 | 6.397e-06 | -0.00078838 | 0.011874 | 0.011884 | 0.011884 | 0.98731 | -0.0063155 | 0.98729 | -0.0061646 | 5.4019
54 | 0.36593 | 0.17691 | -0.36593 | -0.17723 | 2.5323e-06 | -0.00031171 | 0.011884 | 0.011888 | 0.011888 | 0.98729 | -0.0061646 | 0.98728 | -0.0061044 | 5.4037
55 | -0.056338 | -0.027286 | 0.056339 | 0.025691 | 2.9825e-07 | -0.0015949 | 0.0018229 | 0.0018031 | 0.0018229 | 0.99131 | -0.007439 | 0.99132 | -0.0074821 | 0.82858
56 | -0.056339 | -0.025691 | 0.056342 | 0.0028946 | 3.7157e-06 | -0.022796 | 0.0018031 | 0.0016428 | 0.0018031 | 0.99132 | -0.0074821 | 0.99139 | -0.0073296 | 0.8196
57 | -0.18163 | -0.063522 | 0.18165 | 0.053812 | 1.7071e-05 | -0.0097105 | 0.0056029 | 0.005516 | 0.0056029 | 0.99139 | -0.0073296 | 0.99148 | -0.0074582 | 2.5468
58 | 0.12529 | 0.060628 | -0.12529 | -0.060679 | 1.3069e-06 | -5.1568e-05 | 0.0040529 | 0.0040536 | 0.0040536 | 0.99139 | -0.0073296 | 0.99137 | -0.0073985 | 1.9303
59 | 0.10809 | 0.052196 | -0.10809 | -0.052351 | 1.0795e-07 | -0.00015525 | 0.0034949 | 0.0034968 | 0.0034968 | 0.99148 | -0.0074582 | 0.99148 | -0.0074495 | 1.5895
60 | 0.32539 | 0.13689 | -0.32529 | -0.15396 | 0.00010483 | -0.017068 | 0.01028 | 0.010483 | 0.010483 | 0.99133 | -0.006322 | 0.99103 | -0.0040083 | 4.7649
61 | 0.11758 | 0.054519 | -0.11757 | -0.056944 | 1.9812e-06 | -0.0024249 | 0.003774 | 0.0038042 | 0.0038042 | 0.99133 | -0.006322 | 0.99132 | -0.0061822 | 1.7292
62 | 0.32529 | 0.15396 | -0.32528 | -0.15409 | 8.4059e-07 | -0.00013409 | 0.010483 | 0.010484 | 0.010484 | 0.99103 | -0.0040083 | 0.99103 | -0.0039869 | 4.7657
63 | -0.13819 | -0.066929 | 0.1382 | 0.066794 | 4.1702e-06 | -0.00013464 | 0.0044725 | 0.0044708 | 0.0044725 | 0.99105 | -0.0014578 | 0.99108 | -0.0012581 | 2.1298
64 | -0.36163 | -0.17378 | 0.36167 | 0.16856 | 4.0414e-05 | -0.0052163 | 0.011686 | 0.011621 | 0.011686 | 0.99108 | -0.0012581 | 0.99119 | -0.0021823 | 5.312
65 | 0.10316 | 0.048731 | -0.10315 | -0.049527 | 1.3538e-05 | -0.00079576 | 0.0033232 | 0.0033332 | 0.0033332 | 0.99108 | -0.0012581 | 0.99095 | -0.0021781 | 1.5873
66 | 0.10315 | 0.049527 | -0.10314 | -0.049953 | 7.2838e-06 | -0.00042604 | 0.0033332 | 0.0033387 | 0.0033387 | 0.99095 | -0.0021781 | 0.99087 | -0.0026512 | 1.5899
67 | 0.27106 | 0.12783 | -0.27069 | -0.13071 | 0.00036235 | -0.0028839 | 0.0087294 | 0.0087685 | 0.0087685 | 0.99103 | -0.0039869 | 0.98963 | -0.013297 | 4.1755
68 | 0.16096 | 0.077564 | -0.16095 | -0.077949 | 1.6373e-05 | -0.00038483 | 0.005212 | 0.005217 | 0.005217 | 0.98963 | -0.013297 | 0.98952 | -0.013974 | 2.4843

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 5.5006 | 2.3987

## res_load
| p_mw | q_mvar
0 | 0.068937 | 0.033388
1 | 0.066346 | 0.032133
2 | 0.057498 | 0.027848
3 | 0.10919 | 0.052881
4 | 0.15617 | 0.075636
5 | 0.10131 | 0.049068
6 | 0.11597 | 0.056169
7 | 0.093213 | 0.045145
8 | 0.11512 | 0.055754
9 | 1.0516 | 0.50932
10 | 0.10962 | 0.05309
11 | 0.14818 | 0.071768
12 | 0.15364 | 0.074413
13 | 0.091683 | 0.044404
14 | 0.06932 | 0.033573
15 | 0.14733 | 0.071356
16 | 0.39363 | 0.19064
17 | 0.10185 | 0.049326
18 | 0.15055 | 0.072916
19 | 0.12329 | 0.059712
20 | 0.063724 | 0.030863
21 | 0.12478 | 0.060431
22 | 0.36593 | 0.17723
23 | 0.056338 | 0.027286
24 | 0.12529 | 0.060679
25 | 0.14541 | 0.070426
26 | 0.10809 | 0.052351
27 | 0.11757 | 0.056944
28 | 0.13819 | 0.066929
29 | 0.12028 | 0.058252
30 | 0.16106 | 0.078003
31 | 0.10314 | 0.049953
32 | 0.054229 | 0.026264
33 | 0.10973 | 0.053146
34 | 0.16095 | 0.077949
35 | 0.058083 | 0.028131

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1