## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_80_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_80_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_80_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_80_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_80_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_80_0_node_217 | 20 | n |  | TRUE
6 | bus_MV_80_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_80_0_node_6 | 20 | n |  | TRUE
8 | bus_MV_80_0_node_14 | 20 | n |  | TRUE
9 | bus_MV_80_0_node_171 | 20 | n |  | TRUE
10 | bus_MV_80_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_80_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_80_0_node_9 | 20 | n |  | TRUE
13 | bus_MV_80_0_node_10 | 20 | n |  | TRUE
14 | bus_MV_80_0_node_11 | 20 | n |  | TRUE
15 | bus_MV_80_0_node_13 | 20 | n |  | TRUE
16 | bus_MV_80_0_node_12 | 20 | n |  | TRUE
17 | bus_MV_80_0_node_15 | 20 | n |  | TRUE
18 | bus_MV_80_0_node_16 | 20 | n |  | TRUE
19 | bus_MV_80_0_node_170 | 20 | n |  | TRUE
20 | bus_MV_80_0_node_17 | 20 | n |  | TRUE
21 | bus_MV_80_0_node_18 | 20 | n |  | TRUE
22 | bus_MV_80_0_node_19 | 20 | n |  | TRUE
23 | bus_MV_80_0_node_20 | 20 | n |  | TRUE
24 | bus_MV_80_0_node_21 | 20 | n |  | TRUE
25 | bus_MV_80_0_node_26 | 20 | n |  | TRUE
26 | bus_MV_80_0_node_22 | 20 | n |  | TRUE
27 | bus_MV_80_0_node_23 | 20 | n |  | TRUE
28 | bus_MV_80_0_node_188 | 20 | n |  | TRUE
29 | bus_MV_80_0_node_24 | 20 | n |  | TRUE
30 | bus_MV_80_0_node_153 | 20 | n |  | TRUE
31 | bus_MV_80_0_node_25 | 20 | n |  | TRUE
32 | bus_MV_80_0_node_27 | 20 | n |  | TRUE
33 | bus_MV_80_0_node_28 | 20 | n |  | TRUE
34 | bus_MV_80_0_node_29 | 20 | n |  | TRUE
35 | bus_MV_80_0_node_195 | 20 | n |  | TRUE
36 | bus_MV_80_0_node_30 | 20 | n |  | TRUE
37 | bus_MV_80_0_node_43 | 20 | n |  | TRUE
38 | bus_MV_80_0_node_189 | 20 | n |  | TRUE
39 | bus_MV_80_0_node_31 | 20 | n |  | TRUE
40 | bus_MV_80_0_node_33 | 20 | n |  | TRUE
41 | bus_MV_80_0_node_34 | 20 | n |  | TRUE
42 | bus_MV_80_0_node_35 | 20 | n |  | TRUE
43 | bus_MV_80_0_node_36 | 20 | n |  | TRUE
44 | bus_MV_80_0_node_37 | 20 | n |  | TRUE
45 | bus_MV_80_0_node_212 | 20 | n |  | TRUE
46 | bus_MV_80_0_node_38 | 20 | n |  | TRUE
47 | bus_MV_80_0_node_40 | 20 | n |  | TRUE
48 | bus_MV_80_0_node_196 | 20 | n |  | TRUE
49 | bus_MV_80_0_node_39 | 20 | n |  | TRUE
50 | bus_MV_80_0_node_41 | 20 | n |  | TRUE
51 | bus_MV_80_0_node_42 | 20 | n |  | TRUE
52 | bus_MV_80_0_node_130 | 20 | n |  | TRUE
53 | bus_MV_80_0_node_132 | 20 | n |  | TRUE
54 | bus_MV_80_0_node_131 | 20 | n |  | TRUE
55 | bus_MV_80_0_node_134 | 20 | n |  | TRUE
56 | bus_MV_80_0_node_133 | 20 | n |  | TRUE
57 | bus_MV_80_0_node_135 | 20 | n |  | TRUE
58 | bus_MV_80_0_node_146 | 20 | n |  | TRUE
59 | bus_MV_80_0_node_187 | 20 | n |  | TRUE
60 | bus_MV_80_0_node_140 | 20 | n |  | TRUE
61 | bus_MV_80_0_node_136 | 20 | n |  | TRUE
62 | bus_MV_80_0_node_137 | 20 | n |  | TRUE
63 | bus_MV_80_0_node_138 | 20 | n |  | TRUE
64 | bus_MV_80_0_node_139 | 20 | n |  | TRUE
65 | bus_MV_80_0_node_164 | 20 | n |  | TRUE
66 | bus_MV_80_0_node_191 | 20 | n |  | TRUE
67 | bus_MV_80_0_node_147 | 20 | n |  | TRUE
68 | bus_MV_80_0_node_192 | 20 | n |  | TRUE
69 | bus_MV_80_0_node_148 | 20 | n |  | TRUE
70 | bus_MV_80_0_node_154 | 20 | n |  | TRUE
71 | bus_MV_80_0_node_157 | 20 | n |  | TRUE
72 | bus_MV_80_0_node_155 | 20 | n |  | TRUE
73 | bus_MV_80_0_node_156 | 20 | n |  | TRUE
74 | bus_MV_80_0_node_158 | 20 | n |  | TRUE
75 | bus_MV_80_0_node_159 | 20 | n |  | TRUE
76 | bus_MV_80_0_node_160 | 20 | n |  | TRUE
77 | bus_MV_80_0_node_161 | 20 | n |  | TRUE
78 | bus_MV_80_0_node_163 | 20 | n |  | TRUE
79 | bus_MV_80_0_node_165 | 20 | n |  | TRUE
80 | bus_MV_80_0_node_166 | 20 | n |  | TRUE
81 | bus_MV_80_0_node_167 | 20 | n |  | TRUE
82 | bus_MV_80_0_node_168 | 20 | n |  | TRUE
83 | bus_MV_80_0_node_169 | 20 | n |  | TRUE
84 | bus_MV_80_0_node_193 | 20 | n |  | TRUE
85 | bus_HV_80_0_node_33 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_80_0_load_0 | 0 | 0.27359 | 0.1325 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_80_0_load_217 | 5 | 0.17675 | 0.085604 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_80_0_load_5 | 6 | 0.28309 | 0.13711 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_80_0_load_6 | 7 | 0.1652 | 0.080008 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_80_0_load_171 | 9 | 0.19153 | 0.092764 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_80_0_load_7 | 10 | 0.33015 | 0.1599 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_80_0_load_13 | 15 | 0.28578 | 0.13841 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_80_0_load_12 | 16 | 0.24429 | 0.11832 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_80_0_load_15 | 17 | 0.12537 | 0.060719 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_80_0_load_170 | 19 | 0.13309 | 0.06446 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_80_0_load_18 | 21 | 0.12704 | 0.061527 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_80_0_load_21 | 24 | 0.1572 | 0.076134 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_80_0_load_22 | 26 | 0.069098 | 0.033466 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_80_0_load_153 | 30 | 0.075255 | 0.036448 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_80_0_load_195 | 35 | 0.14816 | 0.071755 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_80_0_load_30 | 36 | 0.10625 | 0.051461 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_80_0_load_189 | 38 | 0.076339 | 0.036973 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_80_0_load_31 | 39 | 0.10412 | 0.050426 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_80_0_load_33 | 40 | 0.095658 | 0.04633 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_80_0_load_212 | 45 | 0.15965 | 0.077324 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_80_0_load_38 | 46 | 0.054841 | 0.026561 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_80_0_load_196 | 48 | 0.15571 | 0.075416 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_80_0_load_39 | 49 | 0.15094 | 0.073104 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_80_0_load_42 | 51 | 0.14313 | 0.069321 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_80_0_load_130 | 52 | 0.12996 | 0.062943 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_80_0_load_146 | 58 | 0.051303 | 0.024847 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_80_0_load_187 | 59 | 0.12373 | 0.059924 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_80_0_load_140 | 60 | 0.063544 | 0.030776 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_80_0_load_136 | 61 | 0.16124 | 0.07809 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_80_0_load_138 | 63 | 0.11298 | 0.054718 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_80_0_load_191 | 66 | 0.11888 | 0.057578 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_80_0_load_154 | 70 | 0.086378 | 0.041835 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_80_0_load_155 | 72 | 0.099149 | 0.04802 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_80_0_load_160 | 76 | 0.1047 | 0.050707 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_80_0_load_161 | 77 | 0.055713 | 0.026983 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_80_0_load_163 | 78 | 0.091655 | 0.044391 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_80_0_load_165 | 79 | 0.41161 | 0.19935 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_80_0_load_168 | 82 | 0.35743 | 0.17311 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_80_0_load_193 | 84 | 0.15163 | 0.073439 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_80_0_line_0 |  | 0 | 1 | 0.0387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_80_0_line_1 |  | 1 | 2 | 0.45426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_80_0_line_2 |  | 1 | 3 | 0.74381 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
3 | MV_80_0_line_3 |  | 1 | 4 | 1.2524 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
4 | MV_80_0_line_4 |  | 2 | 5 | 0.023809 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_80_0_line_5 |  | 3 | 6 | 0.11513 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
6 | MV_80_0_line_6 |  | 4 | 7 | 0.086465 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_80_0_line_7 |  | 4 | 8 | 2.1626 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
8 | MV_80_0_line_8 |  | 6 | 9 | 0.8951 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
9 | MV_80_0_line_9 |  | 8 | 15 | 0.046278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_80_0_line_10 |  | 9 | 83 | 1.4759 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
11 | MV_80_0_line_11 |  | 10 | 11 | 0.060187 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_80_0_line_12 |  | 10 | 12 | 0.065733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_80_0_line_13 |  | 11 | 13 | 0.47893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_80_0_line_14 |  | 12 | 14 | 0.57655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_80_0_line_15 |  | 13 | 15 | 0.015362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_80_0_line_16 |  | 14 | 16 | 0.035929 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_80_0_line_17 |  | 17 | 18 | 0.007452 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
18 | MV_80_0_line_18 |  | 17 | 19 | 1.3612 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
19 | MV_80_0_line_19 |  | 18 | 20 | 0.20528 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
20 | MV_80_0_line_20 |  | 19 | 81 | 0.68854 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
21 | MV_80_0_line_21 |  | 20 | 21 | 0.029572 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
22 | MV_80_0_line_22 |  | 21 | 22 | 0.09528 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
23 | MV_80_0_line_23 |  | 22 | 23 | 0.033014 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
24 | MV_80_0_line_24 |  | 23 | 24 | 0.011596 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
25 | MV_80_0_line_25 |  | 24 | 25 | 0.009201 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
26 | MV_80_0_line_26 |  | 25 | 34 | 0.56613 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
27 | MV_80_0_line_27 |  | 25 | 35 | 0.073673 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_80_0_line_28 |  | 26 | 27 | 0.03652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_80_0_line_29 |  | 26 | 28 | 1.2128 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_80_0_line_30 |  | 27 | 29 | 0.29918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_80_0_line_31 |  | 28 | 38 | 0.30369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_80_0_line_32 |  | 28 | 39 | 0.85838 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_80_0_line_33 |  | 29 | 30 | 0.25019 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_80_0_line_34 |  | 30 | 71 | 0.75543 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_80_0_line_35 |  | 31 | 32 | 0.042418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_80_0_line_36 |  | 31 | 33 | 0.42783 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_80_0_line_37 |  | 32 | 35 | 0.046285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_80_0_line_38 |  | 33 | 36 | 0.18295 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_80_0_line_39 |  | 34 | 37 | 0.006909 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
40 | MV_80_0_line_40 |  | 34 | 38 | 0.15098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_80_0_line_41 |  | 37 | 51 | 0.16244 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
42 | MV_80_0_line_42 |  | 40 | 41 | 0.11308 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
43 | MV_80_0_line_43 |  | 41 | 42 | 1.2202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_80_0_line_44 |  | 41 | 43 | 0.99262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_80_0_line_45 |  | 41 | 44 | 1.0634 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
46 | MV_80_0_line_46 |  | 42 | 45 | 0.050746 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_80_0_line_47 |  | 43 | 46 | 0.034131 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_80_0_line_48 |  | 44 | 47 | 1.1195 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
49 | MV_80_0_line_49 |  | 44 | 48 | 0.08972 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_80_0_line_50 |  | 47 | 50 | 0.46583 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
51 | MV_80_0_line_51 |  | 47 | 49 | 0.10216 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_80_0_line_52 |  | 50 | 51 | 0.013069 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
53 | MV_80_0_line_53 |  | 52 | 53 | 0.046467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_80_0_line_54 |  | 52 | 54 | 0.063759 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_80_0_line_55 |  | 52 | 55 | 0.2671 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_80_0_line_56 |  | 53 | 57 | 0.077334 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_80_0_line_57 |  | 54 | 56 | 0.21434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_80_0_line_58 |  | 55 | 59 | 0.011567 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_80_0_line_59 |  | 56 | 58 | 0.020236 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_80_0_line_60 |  | 57 | 60 | 0.30473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_80_0_line_61 |  | 57 | 61 | 0.033565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_80_0_line_62 |  | 60 | 67 | 0.26135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_80_0_line_63 |  | 60 | 68 | 0.70575 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_80_0_line_64 |  | 61 | 62 | 0.009096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_80_0_line_65 |  | 62 | 63 | 0.061944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_80_0_line_66 |  | 62 | 64 | 0.092601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_80_0_line_67 |  | 64 | 65 | 0.23676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_80_0_line_68 |  | 64 | 66 | 0.056554 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_80_0_line_69 |  | 65 | 75 | 0.10522 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_80_0_line_70 |  | 65 | 78 | 0.018718 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_80_0_line_71 |  | 67 | 69 | 0.66982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_80_0_line_72 |  | 68 | 84 | 0.090345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_80_0_line_73 |  | 69 | 70 | 0.080585 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_80_0_line_74 |  | 71 | 75 | 0.4066 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_80_0_line_75 |  | 71 | 72 | 0.070567 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_80_0_line_76 |  | 72 | 73 | 0.038065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_80_0_line_77 |  | 73 | 74 | 0.79453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_80_0_line_78 |  | 74 | 76 | 0.10398 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_80_0_line_79 |  | 76 | 77 | 0.99428 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_80_0_line_80 |  | 79 | 80 | 0.11628 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_80_0_line_81 |  | 80 | 81 | 0.56389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_80_0_line_82 |  | 81 | 82 | 0.01987 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
83 | MV_80_0_line_83 |  | 82 | 83 | 0.044925 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_80_0_trafo_33 | 25 MVA 110/20 kV | 85 | 40 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2622111.9939 | 1167875.6242
1 | 2622147.4558 | 1167889.5281
2 | 2622485.2521 | 1167720.9279
3 | 2621658.7676 | 1167575.3036
4 | 2623214.4199 | 1167554.7213
5 | 2622493.0822 | 1167743.4129
6 | 2621544.481 | 1167561.4312
7 | 2623133.9911 | 1167586.4612
8 | 2625335.3143 | 1167132.1124
9 | 2621292.9534 | 1168420.4595
10 | 2625758.6788 | 1167055.0473
11 | 2625699.8532 | 1167051.1829
12 | 2625806.9517 | 1167011.7432
13 | 2625340.9435 | 1167084.1229
14 | 2626133.237 | 1167197.0889
15 | 2625326.0915 | 1167088.2069
16 | 2626167.1472 | 1167208.9645
17 | 2619520.5982 | 1167753.8643
18 | 2619526.0184 | 1167748.7348
19 | 2619421.8784 | 1169111.5298
20 | 2619637.6926 | 1167636.8414
21 | 2619659.9452 | 1167617.3041
22 | 2619716.2317 | 1167540.4271
23 | 2619732.7511 | 1167511.8223
24 | 2619742.8061 | 1167507.9199
25 | 2619742.7354 | 1167499.1375
26 | 2619475.3899 | 1165484.5549
27 | 2619476.4037 | 1165448.0621
28 | 2619581.0454 | 1166692.7153
29 | 2619483.0432 | 1165161.2062
30 | 2619497.1748 | 1164911.4155
31 | 2619807.9464 | 1167544.0185
32 | 2619835.2351 | 1167529.4899
33 | 2620209.2029 | 1167580.7806
34 | 2619745.9622 | 1166984.0999
35 | 2619815.6676 | 1167488.7161
36 | 2620346.1607 | 1167459.4804
37 | 2619747.8671 | 1166977.4584
38 | 2619604.2698 | 1166975.3885
39 | 2618722.8147 | 1166676.5579
40 | 2621230.3728 | 1166775.631
41 | 2621342.5919 | 1166761.7204
42 | 2622019.8713 | 1166011.4241
43 | 2621612.8389 | 1166450.4714
44 | 2620739.1357 | 1166627.8013
45 | 2622069.2558 | 1166000.1769
46 | 2621641.1031 | 1166469.6047
47 | 2620212.7303 | 1166739.5021
48 | 2620689.1894 | 1166702.3337
49 | 2620134.7771 | 1166673.4746
50 | 2619919.4751 | 1166997.4554
51 | 2619906.6625 | 1166994.7006
52 | 2619435.9369 | 1163843.3381
53 | 2619482.3104 | 1163838.741
54 | 2619372.2879 | 1163847.0796
55 | 2619331.2724 | 1164089.0803
56 | 2619224.2698 | 1163802.8393
57 | 2619559.3487 | 1163829.7971
58 | 2619204.503 | 1163807.4231
59 | 2619333.6632 | 1164100.3971
60 | 2619504.6181 | 1163531.8039
61 | 2619569.9446 | 1163861.6474
62 | 2619572.9649 | 1163870.2282
63 | 2619576.425 | 1163932.0593
64 | 2619664.9164 | 1163877.1419
65 | 2619852.3736 | 1163985.9441
66 | 2619654.7816 | 1163821.5032
67 | 2619259.8458 | 1163450.2764
68 | 2619877.827 | 1162932.8117
69 | 2618781.1433 | 1163456.6142
70 | 2618708.3265 | 1163422.0929
71 | 2620009.6233 | 1164356.3718
72 | 2620060.4354 | 1164399.9625
73 | 2620095.2769 | 1164389.351
74 | 2620583.6399 | 1164517.7076
75 | 2619862.3522 | 1164090.685
76 | 2620664.1285 | 1164451.8833
77 | 2621655.6543 | 1164525.879
78 | 2619833.6368 | 1163987.1052
79 | 2620178.462 | 1169896.9468
80 | 2620161.3032 | 1169781.9423
81 | 2620076.6219 | 1169324.606
82 | 2620087.4207 | 1169307.9114
83 | 2620127.4253 | 1169325.9763
84 | 2619875.695 | 1162845.3165
85 | 2621230.3728 | 1166775.631

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99034 | -0.2917 | 0.27359 | 0.1325
1 | 0.99035 | -0.29183 | 0 | 0
2 | 0.99025 | -0.29101 | 0 | 0
3 | 0.9907 | -0.28893 | 0 | 0
4 | 0.98994 | -0.29468 | 0 | 0
5 | 0.99024 | -0.29106 | 0.17675 | 0.085604
6 | 0.99078 | -0.28576 | 0.28309 | 0.13711
7 | 0.98991 | -0.29486 | 0.1652 | 0.080008
8 | 0.9887 | -0.36732 | 0 | 0
9 | 0.99151 | -0.25685 | 0.19153 | 0.092764
10 | 0.98824 | -0.36383 | 0.33015 | 0.1599
11 | 0.98829 | -0.36418 | 0 | 0
12 | 0.98822 | -0.36369 | 0 | 0
13 | 0.98864 | -0.36684 | 0 | 0
14 | 0.98804 | -0.36225 | 0 | 0
15 | 0.98865 | -0.36692 | 0.28578 | 0.13841
16 | 0.98803 | -0.36215 | 0.24429 | 0.11832
17 | 0.99567 | -0.10156 | 0.12537 | 0.060719
18 | 0.99567 | -0.10146 | 0 | 0
19 | 0.9938 | -0.17049 | 0.13309 | 0.06446
20 | 0.9958 | -0.09876 | 0 | 0
21 | 0.99582 | -0.098369 | 0.12704 | 0.061527
22 | 0.99597 | -0.093124 | 0 | 0
23 | 0.99599 | -0.092671 | 0 | 0
24 | 0.99599 | -0.092511 | 0.1572 | 0.076134
25 | 0.996 | -0.092379 | 0 | 0
26 | 0.99204 | -0.10947 | 0.069098 | 0.033466
27 | 0.99198 | -0.10905 | 0 | 0
28 | 0.99549 | -0.077475 | 0 | 0
29 | 0.99144 | -0.10554 | 0 | 0
30 | 0.99076 | -0.11177 | 0.075255 | 0.036448
31 | 0.99595 | -0.092638 | 0 | 0
32 | 0.99596 | -0.092663 | 0 | 0
33 | 0.9959 | -0.092235 | 0 | 0
34 | 0.99642 | -0.083538 | 0 | 0
35 | 0.99597 | -0.092687 | 0.14816 | 0.071755
36 | 0.99586 | -0.092473 | 0.10625 | 0.051461
37 | 0.99643 | -0.083378 | 0 | 0
38 | 0.9961 | -0.081468 | 0.076339 | 0.036973
39 | 0.99531 | -0.078602 | 0.10412 | 0.050426
40 | 1 | 0 | -5.9125 | -2.2354
41 | 0.99969 | -0.012155 | 0 | 0
42 | 0.99945 | -0.011049 | 0 | 0
43 | 0.99963 | -0.012255 | 0 | 0
44 | 0.99844 | -0.040109 | 0 | 0
45 | 0.99944 | -0.010954 | 0.15965 | 0.077324
46 | 0.99962 | -0.012278 | 0.054841 | 0.026561
47 | 0.99715 | -0.068128 | 0 | 0
48 | 0.99842 | -0.040278 | 0.15571 | 0.075416
49 | 0.99712 | -0.068316 | 0.15094 | 0.073104
50 | 0.99662 | -0.079294 | 0 | 0
51 | 0.99661 | -0.079605 | 0.14313 | 0.069321
52 | 0.98755 | -0.12432 | 0.12996 | 0.062943
53 | 0.98756 | -0.12447 | 0 | 0
54 | 0.98754 | -0.12439 | 0 | 0
55 | 0.98748 | -0.12474 | 0 | 0
56 | 0.98753 | -0.1243 | 0 | 0
57 | 0.98759 | -0.12472 | 0 | 0
58 | 0.98752 | -0.12429 | 0.051303 | 0.024847
59 | 0.98748 | -0.12472 | 0.12373 | 0.059924
60 | 0.98748 | -0.12416 | 0.063544 | 0.030776
61 | 0.98762 | -0.12488 | 0.16124 | 0.07809
62 | 0.98763 | -0.12494 | 0 | 0
63 | 0.98762 | -0.12486 | 0.11298 | 0.054718
64 | 0.98773 | -0.12568 | 0 | 0
65 | 0.98803 | -0.12783 | 0 | 0
66 | 0.98772 | -0.12576 | 0.11888 | 0.057578
67 | 0.98745 | -0.1242 | 0 | 0
68 | 0.98727 | -0.12564 | 0 | 0
69 | 0.98738 | -0.12384 | 0 | 0
70 | 0.98736 | -0.12392 | 0.086378 | 0.041835
71 | 0.98882 | -0.12988 | 0 | 0
72 | 0.98879 | -0.12975 | 0.099149 | 0.04802
73 | 0.98879 | -0.12973 | 0 | 0
74 | 0.98863 | -0.12872 | 0 | 0
75 | 0.98825 | -0.12594 | 0 | 0
76 | 0.98859 | -0.12893 | 0.1047 | 0.050707
77 | 0.98849 | -0.12967 | 0.055713 | 0.026983
78 | 0.98803 | -0.12781 | 0.091655 | 0.044391
79 | 0.99251 | -0.20192 | 0.41161 | 0.19935
80 | 0.99261 | -0.20133 | 0 | 0
81 | 0.9929 | -0.2039 | 0 | 0
82 | 0.99289 | -0.20411 | 0.35743 | 0.17311
83 | 0.99287 | -0.20451 | 0 | 0
84 | 0.98725 | -0.12548 | 0.15163 | 0.073439
85 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.27359 | -0.1325 | 0.27359 | 0.1316 | 4.0512e-06 | -0.00090504 | 0.0088609 | 0.0088494 | 0.0088609 | 0.99034 | -0.2917 | 0.99035 | -0.29183 | 4.0277
1 | 0.17677 | 0.074946 | -0.17675 | -0.085577 | 1.942e-05 | -0.010631 | 0.0055966 | 0.0057248 | 0.0057248 | 0.99035 | -0.29183 | 0.99025 | -0.29101 | 2.6022
2 | -1.4771 | -0.59509 | 1.4776 | 0.54951 | 0.00049001 | -0.045577 | 0.046419 | 0.045936 | 0.046419 | 0.99035 | -0.29183 | 0.9907 | -0.28893 | 7.2757
3 | 1.0268 | 0.38854 | -1.0264 | -0.46546 | 0.00040662 | -0.076916 | 0.032 | 0.032863 | 0.032863 | 0.99035 | -0.29183 | 0.98994 | -0.29468 | 5.151
4 | 0.17675 | 0.085577 | -0.17675 | -0.085604 | 1.3904e-06 | -2.7001e-05 | 0.0057248 | 0.0057251 | 0.0057251 | 0.99025 | -0.29101 | 0.99024 | -0.29106 | 2.7263
5 | -1.4776 | -0.54951 | 1.4777 | 0.54934 | 8.6576e-05 | -0.00016718 | 0.045936 | 0.045934 | 0.045936 | 0.9907 | -0.28893 | 0.99078 | -0.28576 | 5.602
6 | 0.1652 | 0.07991 | -0.1652 | -0.080008 | 4.4128e-06 | -9.8388e-05 | 0.0053514 | 0.0053527 | 0.0053527 | 0.98994 | -0.29468 | 0.98991 | -0.29486 | 2.5489
7 | 0.86115 | 0.38555 | -0.86057 | -0.3869 | 0.0005852 | -0.0013522 | 0.027514 | 0.027549 | 0.027549 | 0.98994 | -0.29468 | 0.9887 | -0.36732 | 4.2712
8 | -1.7608 | -0.68645 | 1.7618 | 0.68557 | 0.00096682 | -0.00087647 | 0.055064 | 0.05504 | 0.055064 | 0.99078 | -0.28576 | 0.99151 | -0.25685 | 6.7151
9 | 0.86057 | 0.3869 | -0.86052 | -0.38797 | 4.691e-05 | -0.0010661 | 0.027549 | 0.027562 | 0.027562 | 0.9887 | -0.36732 | 0.98865 | -0.36692 | 12.5281
10 | -1.9533 | -0.77834 | 1.9553 | 0.77743 | 0.00197 | -0.00090907 | 0.061218 | 0.061177 | 0.061218 | 0.99151 | -0.25685 | 0.99287 | -0.20451 | 7.4656
11 | -0.57449 | -0.26242 | 0.57452 | 0.26102 | 2.7324e-05 | -0.0013954 | 0.018449 | 0.018432 | 0.018449 | 0.98824 | -0.36383 | 0.98829 | -0.36418 | 8.3861
12 | 0.24435 | 0.10252 | -0.24434 | -0.10405 | 5.2695e-06 | -0.0015312 | 0.0077404 | 0.0077579 | 0.0077579 | 0.98824 | -0.36383 | 0.98822 | -0.36369 | 3.5263
13 | -0.57452 | -0.26102 | 0.57474 | 0.24991 | 0.00021566 | -0.011109 | 0.018432 | 0.0183 | 0.018432 | 0.98829 | -0.36418 | 0.98864 | -0.36684 | 8.3783
14 | 0.24434 | 0.10405 | -0.2443 | -0.11748 | 4.7272e-05 | -0.013427 | 0.0077579 | 0.0079199 | 0.0079199 | 0.98822 | -0.36369 | 0.98804 | -0.36225 | 3.6
15 | -0.57474 | -0.24991 | 0.57474 | 0.24956 | 6.8663e-06 | -0.00035647 | 0.0183 | 0.018296 | 0.0183 | 0.98864 | -0.36684 | 0.98865 | -0.36692 | 8.3181
16 | 0.2443 | 0.11748 | -0.24429 | -0.11832 | 3.0127e-06 | -0.00083656 | 0.0079199 | 0.0079306 | 0.0079306 | 0.98804 | -0.36225 | 0.98803 | -0.36215 | 3.6048
17 | -2.9887 | -1.26 | 2.9887 | 1.2594 | 1.2059e-05 | -0.00055337 | 0.094037 | 0.094031 | 0.094037 | 0.99567 | -0.10156 | 0.99567 | -0.10146 | 11.1683
18 | 2.8633 | 1.1992 | -2.8594 | -1.197 | 0.0039318 | 0.0022057 | 0.090004 | 0.090043 | 0.090043 | 0.99567 | -0.10156 | 0.9938 | -0.17049 | 10.9809
19 | -2.9887 | -1.2594 | 2.9891 | 1.2442 | 0.00033154 | -0.015246 | 0.094031 | 0.093857 | 0.094031 | 0.99567 | -0.10146 | 0.9958 | -0.09876 | 11.1676
20 | 2.7263 | 1.1326 | -2.7245 | -1.1317 | 0.001805 | 0.00085453 | 0.085754 | 0.085774 | 0.085774 | 0.9938 | -0.17049 | 0.9929 | -0.2039 | 10.4602
21 | -2.9891 | -1.2442 | 2.9891 | 1.242 | 4.7659e-05 | -0.0021968 | 0.093857 | 0.093832 | 0.093857 | 0.9958 | -0.09876 | 0.99582 | -0.098369 | 11.1469
22 | -3.1161 | -1.3035 | 3.1165 | 1.3037 | 0.00032557 | 0.00022674 | 0.097917 | 0.097914 | 0.097917 | 0.99582 | -0.098369 | 0.99597 | -0.093124 | 11.9411
23 | -3.1165 | -1.3037 | 3.1165 | 1.3013 | 5.7905e-05 | -0.002449 | 0.097914 | 0.097886 | 0.097914 | 0.99597 | -0.093124 | 0.99599 | -0.092671 | 11.6288
24 | -3.1165 | -1.3013 | 3.1165 | 1.3004 | 2.0331e-05 | -0.00086022 | 0.097886 | 0.097877 | 0.097886 | 0.99599 | -0.092671 | 0.99599 | -0.092511 | 11.6255
25 | -3.2737 | -1.3765 | 3.2738 | 1.3759 | 1.7838e-05 | -0.000681 | 0.10293 | 0.10292 | 0.10293 | 0.99599 | -0.092511 | 0.996 | -0.092379 | 12.2247
26 | -3.5282 | -1.4865 | 3.5295 | 1.4448 | 0.0012702 | -0.041761 | 0.11097 | 0.11049 | 0.11097 | 0.996 | -0.092379 | 0.99642 | -0.083538 | 13.1787
27 | 0.25443 | 0.11069 | -0.25442 | -0.11077 | 8.4902e-06 | -8.1928e-05 | 0.0080419 | 0.0080429 | 0.0080429 | 0.996 | -0.092379 | 0.99597 | -0.092687 | 3.83
28 | 1.4319 | 0.60119 | -1.4318 | -0.60202 | 9.9585e-05 | -0.00082854 | 0.04519 | 0.0452 | 0.0452 | 0.99204 | -0.10947 | 0.99198 | -0.10905 | 20.5454
29 | -1.501 | -0.63465 | 1.5059 | 0.63627 | 0.0048575 | 0.0016128 | 0.047421 | 0.047405 | 0.047421 | 0.99204 | -0.10947 | 0.99549 | -0.077475 | 22.5816
30 | 1.4318 | 0.60202 | -1.431 | -0.6088 | 0.00081745 | -0.0067829 | 0.0452 | 0.04528 | 0.04528 | 0.99198 | -0.10905 | 0.99144 | -0.10554 | 20.5817
31 | -1.61 | -0.68569 | 1.611 | 0.67881 | 0.0010423 | -0.0068808 | 0.050745 | 0.050663 | 0.050745 | 0.99549 | -0.077475 | 0.9961 | -0.081468 | 23.0658
32 | 0.10413 | 0.049421 | -0.10412 | -0.050426 | 1.7152e-05 | -0.0010046 | 0.0033425 | 0.0033552 | 0.0033552 | 0.99549 | -0.077475 | 0.99531 | -0.078602 | 1.5977
33 | 1.431 | 0.6088 | -1.4301 | -0.60852 | 0.00091399 | 0.00027911 | 0.04528 | 0.045283 | 0.045283 | 0.99144 | -0.10554 | 0.99076 | -0.11177 | 21.5633
34 | 1.3548 | 0.57207 | -1.3523 | -0.57141 | 0.0024719 | 0.00066479 | 0.04285 | 0.04286 | 0.04286 | 0.99076 | -0.11177 | 0.98882 | -0.12988 | 20.4094
35 | -0.10626 | -0.041117 | 0.10627 | 0.040113 | 6.1569e-07 | -0.0010044 | 0.0033026 | 0.0032922 | 0.0033026 | 0.99595 | -0.092638 | 0.99596 | -0.092663 | 1.5012
36 | 0.10626 | 0.041117 | -0.10626 | -0.051247 | 6.4418e-06 | -0.01013 | 0.0033026 | 0.0034196 | 0.0034196 | 0.99595 | -0.092638 | 0.9959 | -0.092235 | 1.5543
37 | -0.10627 | -0.040113 | 0.10627 | 0.039017 | 6.6745e-07 | -0.001096 | 0.0032922 | 0.0032811 | 0.0032922 | 0.99596 | -0.092663 | 0.99597 | -0.092687 | 1.4965
38 | 0.10626 | 0.051247 | -0.10625 | -0.051461 | 3.8147e-06 | -0.00021422 | 0.0034196 | 0.0034223 | 0.0034223 | 0.9959 | -0.092235 | 0.99586 | -0.092473 | 1.6297
39 | -5.2174 | -2.1572 | 5.2174 | 2.1567 | 3.3824e-05 | -0.00049306 | 0.16356 | 0.16356 | 0.16356 | 0.99642 | -0.083538 | 0.99643 | -0.083378 | 19.4256
40 | 1.6879 | 0.71237 | -1.6874 | -0.71578 | 0.00056829 | -0.0034094 | 0.053078 | 0.053118 | 0.053118 | 0.99642 | -0.083538 | 0.9961 | -0.081468 | 24.1447
41 | -5.2174 | -2.1567 | 5.2182 | 2.1451 | 0.00079454 | -0.011595 | 0.16356 | 0.16342 | 0.16356 | 0.99643 | -0.083378 | 0.99661 | -0.079605 | 19.4249
42 | 5.8985 | 2.2249 | -5.8971 | -2.2233 | 0.0013347 | 0.0016398 | 0.18198 | 0.18199 | 0.18199 | 1 | 0 | 0.99969 | -0.012155 | 22.1936
43 | 0.1597 | 0.047016 | -0.15966 | -0.076114 | 3.9792e-05 | -0.029098 | 0.0048071 | 0.0051086 | 0.0051086 | 0.99969 | -0.012155 | 0.99945 | -0.011049 | 2.3221
44 | 0.054845 | 0.0028374 | -0.054841 | -0.02652 | 3.5618e-06 | -0.023683 | 0.0015858 | 0.0017592 | 0.0017592 | 0.99969 | -0.012155 | 0.99963 | -0.012255 | 0.79963
45 | 5.6826 | 2.1734 | -5.6765 | -2.249 | 0.0060356 | -0.075559 | 0.17569 | 0.17654 | 0.17654 | 0.99969 | -0.012155 | 0.99844 | -0.040109 | 20.9662
46 | 0.15966 | 0.076114 | -0.15965 | -0.077324 | 1.7733e-06 | -0.0012098 | 0.0051086 | 0.0051238 | 0.0051238 | 0.99945 | -0.011049 | 0.99944 | -0.010954 | 2.329
47 | 0.054841 | 0.02652 | -0.054841 | -0.026561 | 1.8825e-07 | -4.0598e-05 | 0.0017592 | 0.0017597 | 0.0017597 | 0.99963 | -0.012255 | 0.99962 | -0.012278 | 0.83795
48 | 5.5208 | 2.1737 | -5.5148 | -2.2533 | 0.0060609 | -0.079591 | 0.17155 | 0.17247 | 0.17247 | 0.99844 | -0.040109 | 0.99715 | -0.068128 | 20.4828
49 | 0.15572 | 0.075311 | -0.15571 | -0.075416 | 3.9992e-06 | -0.00010427 | 0.0050011 | 0.0050025 | 0.0050025 | 0.99844 | -0.040109 | 0.99842 | -0.040278 | 2.3821
50 | 5.3638 | 2.1803 | -5.3614 | -2.2135 | 0.0024007 | -0.033166 | 0.16762 | 0.16801 | 0.16801 | 0.99715 | -0.068128 | 0.99662 | -0.079294 | 19.9536
51 | 0.15095 | 0.072986 | -0.15094 | -0.073104 | 4.2897e-06 | -0.00011857 | 0.0048539 | 0.0048554 | 0.0048554 | 0.99715 | -0.068128 | 0.99712 | -0.068316 | 2.3121
52 | 5.3614 | 2.2135 | -5.3614 | -2.2144 | 6.7513e-05 | -0.00092979 | 0.16801 | 0.16802 | 0.16802 | 0.99662 | -0.079294 | 0.99661 | -0.079605 | 19.9549
53 | -0.305 | -0.1416 | 0.30501 | 0.14052 | 5.9857e-06 | -0.0010802 | 0.0098297 | 0.0098164 | 0.0098297 | 0.98755 | -0.12432 | 0.98756 | -0.12447 | 4.468
54 | 0.051304 | 0.019311 | -0.051304 | -0.019385 | 2.9183e-07 | -7.4048e-05 | 0.0016024 | 0.0016032 | 0.0016032 | 0.98755 | -0.12432 | 0.98754 | -0.12439 | 0.76342
55 | 0.12374 | 0.059349 | -0.12373 | -0.059655 | 7.6658e-06 | -0.00030615 | 0.0040115 | 0.0040155 | 0.0040155 | 0.98755 | -0.12432 | 0.98748 | -0.12474 | 1.9121
56 | -0.30501 | -0.14052 | 0.30502 | 0.13872 | 9.9262e-06 | -0.0017979 | 0.0098164 | 0.0097945 | 0.0098164 | 0.98756 | -0.12447 | 0.98759 | -0.12472 | 4.462
57 | 0.051304 | 0.019385 | -0.051303 | -0.024376 | 7.6062e-07 | -0.0049905 | 0.0016032 | 0.0016604 | 0.0016604 | 0.98754 | -0.12439 | 0.98753 | -0.1243 | 0.75471
58 | 0.12373 | 0.059655 | -0.12373 | -0.059924 | 2.4919e-07 | -0.00026922 | 0.0040155 | 0.0040189 | 0.0040189 | 0.98748 | -0.12474 | 0.98748 | -0.12472 | 1.8268
59 | 0.051303 | 0.024376 | -0.051303 | -0.024847 | 7.4742e-08 | -0.00047116 | 0.0016604 | 0.0016663 | 0.0016663 | 0.98753 | -0.1243 | 0.98752 | -0.12429 | 0.75742
60 | 0.30163 | 0.11429 | -0.3016 | -0.12138 | 3.645e-05 | -0.0070846 | 0.0094285 | 0.009504 | 0.009504 | 0.98759 | -0.12472 | 0.98748 | -0.12416 | 4.32
61 | -0.60665 | -0.25302 | 0.60667 | 0.25224 | 1.6533e-05 | -0.00077676 | 0.019213 | 0.019204 | 0.019213 | 0.98759 | -0.12472 | 0.98762 | -0.12488 | 8.7332
62 | 0.086388 | 0.020067 | -0.086385 | -0.026151 | 2.3844e-06 | -0.0060838 | 0.0025927 | 0.0026386 | 0.0026386 | 0.98748 | -0.12416 | 0.98745 | -0.1242 | 1.1994
63 | 0.15166 | 0.070534 | -0.15163 | -0.071337 | 3.0127e-05 | -0.00080251 | 0.0048897 | 0.0048999 | 0.0048999 | 0.98748 | -0.12416 | 0.98727 | -0.12564 | 2.3333
64 | -0.7679 | -0.33033 | 0.76791 | 0.33012 | 7.249e-06 | -0.00020968 | 0.024434 | 0.024431 | 0.024434 | 0.98762 | -0.12488 | 0.98763 | -0.12494 | 11.1063
65 | 0.11298 | 0.053276 | -0.11298 | -0.054718 | 1.1078e-06 | -0.0014423 | 0.0036511 | 0.0036692 | 0.0036692 | 0.98763 | -0.12494 | 0.98762 | -0.12486 | 1.6678
66 | -0.88089 | -0.3834 | 0.88099 | 0.38127 | 9.7392e-05 | -0.0021279 | 0.028081 | 0.028056 | 0.028081 | 0.98763 | -0.12494 | 0.98773 | -0.12568 | 12.7639
67 | -0.99987 | -0.43878 | 1.0002 | 0.43336 | 0.00032123 | -0.0054214 | 0.031912 | 0.031848 | 0.031912 | 0.98773 | -0.12568 | 0.98803 | -0.12783 | 14.5056
68 | 0.11889 | 0.057513 | -0.11888 | -0.057578 | 1.5015e-06 | -6.4927e-05 | 0.0038598 | 0.0038606 | 0.0038606 | 0.98773 | -0.12568 | 0.98772 | -0.12576 | 1.8384
69 | -1.0918 | -0.47732 | 1.0921 | 0.47734 | 0.00022722 | 1.9678e-05 | 0.034816 | 0.034814 | 0.034816 | 0.98803 | -0.12783 | 0.98825 | -0.12594 | 16.579
70 | 0.091655 | 0.043954 | -0.091655 | -0.044391 | 2.2082e-07 | -0.00043621 | 0.0029699 | 0.0029754 | 0.0029754 | 0.98803 | -0.12783 | 0.98803 | -0.12781 | 1.3525
71 | 0.086385 | 0.026151 | -0.086379 | -0.041742 | 6.5838e-06 | -0.015591 | 0.0026386 | 0.0028048 | 0.0028048 | 0.98745 | -0.1242 | 0.98738 | -0.12384 | 1.2749
72 | 0.15163 | 0.071337 | -0.15163 | -0.073439 | 2.9113e-06 | -0.0021016 | 0.0048999 | 0.0049264 | 0.0049264 | 0.98727 | -0.12564 | 0.98725 | -0.12548 | 2.2393
73 | 0.086379 | 0.041742 | -0.086378 | -0.041835 | 1.13e-06 | -9.3081e-05 | 0.0028048 | 0.002806 | 0.002806 | 0.98738 | -0.12384 | 0.98736 | -0.12392 | 1.3362
74 | 1.0927 | 0.46804 | -1.0921 | -0.47734 | 0.00065583 | -0.0092922 | 0.034704 | 0.034814 | 0.034814 | 0.98882 | -0.12988 | 0.98825 | -0.12594 | 15.8247
75 | 0.2596 | 0.10337 | -0.2596 | -0.10501 | 6.2828e-06 | -0.0016455 | 0.0081576 | 0.0081755 | 0.0081755 | 0.98882 | -0.12988 | 0.98879 | -0.12975 | 3.7161
76 | 0.16045 | 0.056992 | -0.16045 | -0.05788 | 1.2579e-06 | -0.00088821 | 0.004971 | 0.0049798 | 0.0049798 | 0.98879 | -0.12975 | 0.98879 | -0.12973 | 2.2635
77 | 0.16045 | 0.05788 | -0.16042 | -0.076416 | 2.7351e-05 | -0.018536 | 0.0049798 | 0.0051885 | 0.0051885 | 0.98879 | -0.12973 | 0.98863 | -0.12872 | 2.3584
78 | 0.16042 | 0.076416 | -0.16042 | -0.076534 | 4.9887e-06 | -0.00011819 | 0.0051885 | 0.0051901 | 0.0051901 | 0.98863 | -0.12872 | 0.98859 | -0.12893 | 2.4715
79 | 0.055719 | 0.025827 | -0.055713 | -0.026983 | 5.7429e-06 | -0.0011563 | 0.0017933 | 0.0018078 | 0.0018078 | 0.98859 | -0.12893 | 0.98849 | -0.12967 | 0.86086
80 | -0.41161 | -0.19935 | 0.41165 | 0.19924 | 3.6653e-05 | -0.0001138 | 0.013302 | 0.0133 | 0.013302 | 0.99251 | -0.20192 | 0.99261 | -0.20133 | 6.3343
81 | -0.41165 | -0.19924 | 0.41178 | 0.18601 | 0.00013151 | -0.01323 | 0.0133 | 0.013137 | 0.0133 | 0.99261 | -0.20133 | 0.9929 | -0.2039 | 6.0456
82 | 2.3127 | 0.9457 | -2.3127 | -0.94718 | 1.9193e-05 | -0.001479 | 0.072645 | 0.072661 | 0.072661 | 0.9929 | -0.2039 | 0.99289 | -0.20411 | 8.6296
83 | 1.9553 | 0.77407 | -1.9553 | -0.77743 | 3.0751e-05 | -0.0033555 | 0.061141 | 0.061177 | 0.061177 | 0.99289 | -0.20411 | 0.99287 | -0.20451 | 7.2657

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 6.0081 | 2.2818

## res_load
| p_mw | q_mvar
0 | 0.27359 | 0.1325
1 | 0.17675 | 0.085604
2 | 0.28309 | 0.13711
3 | 0.1652 | 0.080008
4 | 0.19153 | 0.092764
5 | 0.33015 | 0.1599
6 | 0.28578 | 0.13841
7 | 0.24429 | 0.11832
8 | 0.12537 | 0.060719
9 | 0.13309 | 0.06446
10 | 0.12704 | 0.061527
11 | 0.1572 | 0.076134
12 | 0.069098 | 0.033466
13 | 0.075255 | 0.036448
14 | 0.14816 | 0.071755
15 | 0.10625 | 0.051461
16 | 0.076339 | 0.036973
17 | 0.10412 | 0.050426
18 | 0.095658 | 0.04633
19 | 0.15965 | 0.077324
20 | 0.054841 | 0.026561
21 | 0.15571 | 0.075416
22 | 0.15094 | 0.073104
23 | 0.14313 | 0.069321
24 | 0.12996 | 0.062943
25 | 0.051303 | 0.024847
26 | 0.12373 | 0.059924
27 | 0.063544 | 0.030776
28 | 0.16124 | 0.07809
29 | 0.11298 | 0.054718
30 | 0.11888 | 0.057578
31 | 0.086378 | 0.041835
32 | 0.099149 | 0.04802
33 | 0.1047 | 0.050707
34 | 0.055713 | 0.026983
35 | 0.091655 | 0.044391
36 | 0.41161 | 0.19935
37 | 0.35743 | 0.17311
38 | 0.15163 | 0.073439

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1