## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_82_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_82_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_82_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_82_0_node_107 | 20 | n |  | TRUE
4 | bus_MV_82_0_node_65 | 20 | n |  | TRUE
5 | bus_MV_82_0_node_106 | 20 | n |  | TRUE
6 | bus_MV_82_0_node_70 | 20 | n |  | TRUE
7 | bus_MV_82_0_node_64 | 20 | n |  | TRUE
8 | bus_MV_82_0_node_3 | 20 | n |  | TRUE
9 | bus_MV_82_0_node_4 | 20 | n |  | TRUE
10 | bus_MV_82_0_node_8 | 20 | n |  | TRUE
11 | bus_MV_82_0_node_10 | 20 | n |  | TRUE
12 | bus_MV_82_0_node_11 | 20 | n |  | TRUE
13 | bus_MV_82_0_node_6 | 20 | n |  | TRUE
14 | bus_MV_82_0_node_93 | 20 | n |  | TRUE
15 | bus_MV_82_0_node_111 | 20 | n |  | TRUE
16 | bus_MV_82_0_node_16 | 20 | n |  | TRUE
17 | bus_MV_82_0_node_91 | 20 | n |  | TRUE
18 | bus_MV_82_0_node_7 | 20 | n |  | TRUE
19 | bus_MV_82_0_node_9 | 20 | n |  | TRUE
20 | bus_MV_82_0_node_13 | 20 | n |  | TRUE
21 | bus_MV_82_0_node_12 | 20 | n |  | TRUE
22 | bus_MV_82_0_node_23 | 20 | n |  | TRUE
23 | bus_MV_82_0_node_108 | 20 | n |  | TRUE
24 | bus_MV_82_0_node_14 | 20 | n |  | TRUE
25 | bus_MV_82_0_node_18 | 20 | n |  | TRUE
26 | bus_MV_82_0_node_69 | 20 | n |  | TRUE
27 | bus_MV_82_0_node_20 | 20 | n |  | TRUE
28 | bus_MV_82_0_node_15 | 20 | n |  | TRUE
29 | bus_MV_82_0_node_17 | 20 | n |  | TRUE
30 | bus_MV_82_0_node_115 | 20 | n |  | TRUE
31 | bus_MV_82_0_node_114 | 20 | n |  | TRUE
32 | bus_MV_82_0_node_19 | 20 | n |  | TRUE
33 | bus_MV_82_0_node_21 | 20 | n |  | TRUE
34 | bus_MV_82_0_node_22 | 20 | n |  | TRUE
35 | bus_MV_82_0_node_112 | 20 | n |  | TRUE
36 | bus_MV_82_0_node_24 | 20 | n |  | TRUE
37 | bus_MV_82_0_node_25 | 20 | n |  | TRUE
38 | bus_MV_82_0_node_27 | 20 | n |  | TRUE
39 | bus_MV_82_0_node_76 | 20 | n |  | TRUE
40 | bus_MV_82_0_node_56 | 20 | n |  | TRUE
41 | bus_MV_82_0_node_50 | 20 | n |  | TRUE
42 | bus_MV_82_0_node_29 | 20 | n |  | TRUE
43 | bus_MV_82_0_node_30 | 20 | n |  | TRUE
44 | bus_MV_82_0_node_31 | 20 | n |  | TRUE
45 | bus_MV_82_0_node_63 | 20 | n |  | TRUE
46 | bus_MV_82_0_node_110 | 20 | n |  | TRUE
47 | bus_MV_82_0_node_61 | 20 | n |  | TRUE
48 | bus_MV_82_0_node_60 | 20 | n |  | TRUE
49 | bus_MV_82_0_node_66 | 20 | n |  | TRUE
50 | bus_MV_82_0_node_32 | 20 | n |  | TRUE
51 | bus_MV_82_0_node_33 | 20 | n |  | TRUE
52 | bus_MV_82_0_node_36 | 20 | n |  | TRUE
53 | bus_MV_82_0_node_34 | 20 | n |  | TRUE
54 | bus_MV_82_0_node_35 | 20 | n |  | TRUE
55 | bus_MV_82_0_node_98 | 20 | n |  | TRUE
56 | bus_MV_82_0_node_53 | 20 | n |  | TRUE
57 | bus_MV_82_0_node_113 | 20 | n |  | TRUE
58 | bus_MV_82_0_node_95 | 20 | n |  | TRUE
59 | bus_MV_82_0_node_52 | 20 | n |  | TRUE
60 | bus_MV_82_0_node_45 | 20 | n |  | TRUE
61 | bus_MV_82_0_node_37 | 20 | n |  | TRUE
62 | bus_MV_82_0_node_38 | 20 | n |  | TRUE
63 | bus_MV_82_0_node_40 | 20 | n |  | TRUE
64 | bus_MV_82_0_node_41 | 20 | n |  | TRUE
65 | bus_MV_82_0_node_39 | 20 | n |  | TRUE
66 | bus_MV_82_0_node_42 | 20 | n |  | TRUE
67 | bus_MV_82_0_node_58 | 20 | n |  | TRUE
68 | bus_MV_82_0_node_51 | 20 | n |  | TRUE
69 | bus_MV_82_0_node_59 | 20 | n |  | TRUE
70 | bus_MV_82_0_node_99 | 20 | n |  | TRUE
71 | bus_MV_82_0_node_72 | 20 | n |  | TRUE
72 | bus_MV_82_0_node_46 | 20 | n |  | TRUE
73 | bus_MV_82_0_node_73 | 20 | n |  | TRUE
74 | bus_MV_82_0_node_71 | 20 | n |  | TRUE
75 | bus_MV_82_0_node_74 | 20 | n |  | TRUE
76 | bus_MV_82_0_node_43 | 20 | n |  | TRUE
77 | bus_MV_82_0_node_44 | 20 | n |  | TRUE
78 | bus_MV_82_0_node_116 | 20 | n |  | TRUE
79 | bus_MV_82_0_node_47 | 20 | n |  | TRUE
80 | bus_MV_82_0_node_48 | 20 | n |  | TRUE
81 | bus_MV_82_0_node_49 | 20 | n |  | TRUE
82 | bus_MV_82_0_node_54 | 20 | n |  | TRUE
83 | bus_MV_82_0_node_55 | 20 | n |  | TRUE
84 | bus_MV_82_0_node_57 | 20 | n |  | TRUE
85 | bus_MV_82_0_node_102 | 20 | n |  | TRUE
86 | bus_MV_82_0_node_109 | 20 | n |  | TRUE
87 | bus_MV_82_0_node_62 | 20 | n |  | TRUE
88 | bus_MV_82_0_node_67 | 20 | n |  | TRUE
89 | bus_MV_82_0_node_68 | 20 | n |  | TRUE
90 | bus_MV_82_0_node_75 | 20 | n |  | TRUE
91 | bus_MV_82_0_node_77 | 20 | n |  | TRUE
92 | bus_MV_82_0_node_78 | 20 | n |  | TRUE
93 | bus_MV_82_0_node_80 | 20 | n |  | TRUE
94 | bus_MV_82_0_node_89 | 20 | n |  | TRUE
95 | bus_MV_82_0_node_100 | 20 | n |  | TRUE
96 | bus_MV_82_0_node_86 | 20 | n |  | TRUE
97 | bus_MV_82_0_node_81 | 20 | n |  | TRUE
98 | bus_MV_82_0_node_82 | 20 | n |  | TRUE
99 | bus_MV_82_0_node_83 | 20 | n |  | TRUE
100 | bus_MV_82_0_node_84 | 20 | n |  | TRUE
101 | bus_MV_82_0_node_85 | 20 | n |  | TRUE
102 | bus_MV_82_0_node_87 | 20 | n |  | TRUE
103 | bus_MV_82_0_node_88 | 20 | n |  | TRUE
104 | bus_MV_82_0_node_101 | 20 | n |  | TRUE
105 | bus_MV_82_0_node_97 | 20 | n |  | TRUE
106 | bus_MV_82_0_node_94 | 20 | n |  | TRUE
107 | bus_MV_82_0_node_90 | 20 | n |  | TRUE
108 | bus_MV_82_0_node_92 | 20 | n |  | TRUE
109 | bus_MV_82_0_node_96 | 20 | n |  | TRUE
110 | bus_MV_82_0_node_103 | 20 | n |  | TRUE
111 | bus_MV_82_0_node_105 | 20 | n |  | TRUE
112 | bus_HV_82_0_node_52 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_82_0_load_0 | 0 | 0.27549 | 0.13342 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_82_0_load_2 | 2 | 0.38903 | 0.18842 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_82_0_load_107 | 3 | 0.067521 | 0.032702 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_82_0_load_70 | 6 | 0.11076 | 0.053642 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_82_0_load_3 | 8 | 0.11072 | 0.053625 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_82_0_load_6 | 13 | 0.13212 | 0.063988 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_82_0_load_111 | 15 | 0.085664 | 0.041489 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_82_0_load_12 | 21 | 0.16064 | 0.077802 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_82_0_load_23 | 22 | 0.14205 | 0.0688 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_82_0_load_108 | 23 | 0.088871 | 0.043042 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_82_0_load_14 | 24 | 0.13132 | 0.063603 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_82_0_load_20 | 27 | 0.08161 | 0.039526 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_82_0_load_115 | 30 | 0.076586 | 0.037092 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_82_0_load_114 | 31 | 0.070112 | 0.033957 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_82_0_load_19 | 32 | 0.082797 | 0.040101 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_82_0_load_112 | 35 | 0.09506 | 0.04604 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_82_0_load_24 | 36 | 0.13636 | 0.066042 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_82_0_load_76 | 39 | 0.1076 | 0.052115 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_82_0_load_29 | 42 | 0.10663 | 0.051642 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_82_0_load_110 | 46 | 0.15187 | 0.073553 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_82_0_load_60 | 48 | 0.07918 | 0.038349 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_82_0_load_66 | 49 | 0.087749 | 0.042499 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_82_0_load_32 | 50 | 0.13239 | 0.06412 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_82_0_load_98 | 55 | 0.10696 | 0.051801 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_82_0_load_113 | 57 | 0.14602 | 0.070722 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_82_0_load_52 | 59 | 0.072137 | 0.034938 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_82_0_load_37 | 61 | 0.15994 | 0.077461 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_82_0_load_58 | 67 | 0.11922 | 0.057739 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_82_0_load_51 | 68 | 0.10618 | 0.051424 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_82_0_load_59 | 69 | 0.12748 | 0.061742 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_82_0_load_99 | 70 | 0.12 | 0.058118 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_82_0_load_71 | 74 | 0.15929 | 0.077147 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_82_0_load_74 | 75 | 0.10105 | 0.04894 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_82_0_load_43 | 76 | 0.13009 | 0.063008 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_82_0_load_116 | 78 | 0.11231 | 0.054395 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_82_0_load_47 | 79 | 0.13119 | 0.063537 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_82_0_load_49 | 81 | 0.1394 | 0.067512 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_82_0_load_102 | 85 | 0.12818 | 0.06208 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_82_0_load_109 | 86 | 0.072003 | 0.034873 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_82_0_load_67 | 88 | 0.090513 | 0.043837 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_82_0_load_75 | 90 | 0.072482 | 0.035105 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_82_0_load_77 | 91 | 0.14294 | 0.069231 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_82_0_load_89 | 94 | 0.062047 | 0.030051 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_82_0_load_100 | 95 | 0.15974 | 0.077364 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_82_0_load_82 | 98 | 0.12782 | 0.061905 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_82_0_load_83 | 99 | 0.14805 | 0.071702 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_82_0_load_88 | 103 | 0.10289 | 0.04983 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_82_0_load_101 | 104 | 0.16185 | 0.078386 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_82_0_load_90 | 107 | 0.1287 | 0.062333 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_82_0_load_96 | 109 | 0.075937 | 0.036778 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_82_0_load_103 | 110 | 0.11216 | 0.054323 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_82_0_line_0 |  | 0 | 1 | 0.094044 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
1 | MV_82_0_line_1 |  | 0 | 2 | 2.9352 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
2 | MV_82_0_line_2 |  | 1 | 3 | 5.4737 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
3 | MV_82_0_line_3 |  | 2 | 4 | 5.0999 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
4 | MV_82_0_line_4 |  | 3 | 5 | 0.007378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_82_0_line_5 |  | 4 | 6 | 0.063617 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_82_0_line_6 |  | 4 | 7 | 0.15697 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
7 | MV_82_0_line_7 |  | 5 | 111 | 0.85947 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_82_0_line_8 |  | 7 | 88 | 0.045944 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
9 | MV_82_0_line_9 |  | 7 | 87 | 0.24562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_82_0_line_10 |  | 8 | 9 | 0.058661 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_82_0_line_11 |  | 9 | 10 | 0.27055 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_82_0_line_12 |  | 10 | 11 | 0.12467 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
13 | MV_82_0_line_13 |  | 10 | 12 | 0.63905 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
14 | MV_82_0_line_14 |  | 10 | 13 | 0.064004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_82_0_line_15 |  | 11 | 22 | 0.18005 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_82_0_line_16 |  | 11 | 23 | 7.1037 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
17 | MV_82_0_line_17 |  | 12 | 24 | 0.086342 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
18 | MV_82_0_line_18 |  | 12 | 25 | 0.38532 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_82_0_line_19 |  | 13 | 18 | 0.047245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_82_0_line_20 |  | 14 | 15 | 0.01684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_82_0_line_21 |  | 14 | 16 | 6.3962 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
22 | MV_82_0_line_22 |  | 14 | 17 | 0.11913 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
23 | MV_82_0_line_23 |  | 16 | 29 | 0.35033 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
24 | MV_82_0_line_24 |  | 16 | 30 | 0.1171 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_82_0_line_25 |  | 17 | 107 | 0.063584 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
26 | MV_82_0_line_26 |  | 18 | 19 | 0.082903 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_82_0_line_27 |  | 19 | 20 | 0.040784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_82_0_line_28 |  | 19 | 21 | 0.044445 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_82_0_line_29 |  | 20 | 27 | 0.23778 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_82_0_line_30 |  | 23 | 26 | 0.02492 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_82_0_line_31 |  | 24 | 28 | 0.11549 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
32 | MV_82_0_line_32 |  | 25 | 32 | 0.054208 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_82_0_line_33 |  | 26 | 89 | 0.068935 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
34 | MV_82_0_line_34 |  | 27 | 33 | 0.1446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_82_0_line_35 |  | 28 | 29 | 0.17915 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
36 | MV_82_0_line_36 |  | 29 | 31 | 0.018338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_82_0_line_37 |  | 33 | 34 | 0.80881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_82_0_line_38 |  | 34 | 35 | 0.44943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_82_0_line_39 |  | 36 | 37 | 0.025955 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_82_0_line_40 |  | 37 | 38 | 0.15227 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_82_0_line_41 |  | 38 | 39 | 0.042914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_82_0_line_42 |  | 39 | 40 | 0.053425 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_82_0_line_43 |  | 40 | 41 | 0.17141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_82_0_line_44 |  | 41 | 82 | 0.27361 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_82_0_line_45 |  | 41 | 81 | 0.046486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_82_0_line_46 |  | 42 | 43 | 0.028487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_82_0_line_47 |  | 43 | 44 | 0.069236 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_82_0_line_48 |  | 44 | 45 | 0.23022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_82_0_line_49 |  | 44 | 46 | 0.039256 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_82_0_line_50 |  | 45 | 49 | 0.017854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_82_0_line_51 |  | 45 | 47 | 0.099316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_82_0_line_52 |  | 47 | 48 | 0.027622 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_82_0_line_53 |  | 48 | 87 | 0.031892 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_82_0_line_54 |  | 50 | 51 | 0.053116 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_82_0_line_55 |  | 51 | 52 | 0.1864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_82_0_line_56 |  | 52 | 57 | 0.060804 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_82_0_line_57 |  | 52 | 54 | 0.58431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_82_0_line_58 |  | 53 | 54 | 0.23975 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
59 | MV_82_0_line_59 |  | 53 | 55 | 0.025868 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
60 | MV_82_0_line_60 |  | 54 | 56 | 1.4459 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_82_0_line_61 |  | 55 | 58 | 0.075257 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_82_0_line_62 |  | 56 | 59 | 0.016242 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_82_0_line_63 |  | 57 | 60 | 0.06036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_82_0_line_64 |  | 58 | 108 | 0.041694 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
65 | MV_82_0_line_65 |  | 59 | 82 | 0.11348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_82_0_line_66 |  | 60 | 72 | 0.37975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_82_0_line_67 |  | 60 | 77 | 0.34335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_82_0_line_68 |  | 61 | 62 | 0.011176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_82_0_line_69 |  | 62 | 63 | 0.25401 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_82_0_line_70 |  | 62 | 64 | 0.34202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_82_0_line_71 |  | 63 | 68 | 0.020994 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_82_0_line_72 |  | 63 | 65 | 0.18657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_82_0_line_73 |  | 64 | 69 | 0.046312 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_82_0_line_74 |  | 65 | 66 | 0.18063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_82_0_line_75 |  | 65 | 67 | 0.024185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_82_0_line_76 |  | 66 | 70 | 0.065283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_82_0_line_77 |  | 66 | 71 | 0.52893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_82_0_line_78 |  | 67 | 72 | 0.010299 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_82_0_line_79 |  | 71 | 73 | 0.56961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_82_0_line_80 |  | 71 | 74 | 0.068238 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_82_0_line_81 |  | 73 | 75 | 0.012488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_82_0_line_82 |  | 75 | 90 | 0.064692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_82_0_line_83 |  | 76 | 77 | 0.093741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_82_0_line_84 |  | 77 | 78 | 0.067263 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_82_0_line_85 |  | 79 | 80 | 0.063355 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_82_0_line_86 |  | 80 | 81 | 0.048044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_82_0_line_87 |  | 82 | 83 | 0.16362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_82_0_line_88 |  | 83 | 84 | 0.19007 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_82_0_line_89 |  | 83 | 85 | 0.02817 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_82_0_line_90 |  | 84 | 86 | 0.019842 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_82_0_line_91 |  | 88 | 89 | 0.064851 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
92 | MV_82_0_line_92 |  | 91 | 92 | 0.076996 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_82_0_line_93 |  | 92 | 93 | 0.13895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_82_0_line_94 |  | 93 | 97 | 0.2257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_82_0_line_95 |  | 93 | 95 | 0.084845 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_82_0_line_96 |  | 94 | 95 | 1.7048 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_82_0_line_97 |  | 94 | 96 | 0.040502 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_82_0_line_98 |  | 96 | 100 | 0.39598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_82_0_line_99 |  | 97 | 98 | 0.047536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_82_0_line_100 |  | 99 | 100 | 0.019071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_82_0_line_101 |  | 100 | 101 | 0.48978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_82_0_line_102 |  | 100 | 102 | 0.33817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_82_0_line_103 |  | 101 | 103 | 0.16646 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
104 | MV_82_0_line_104 |  | 102 | 104 | 0.1049 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_82_0_line_105 |  | 103 | 105 | 0.066149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_82_0_line_106 |  | 105 | 106 | 0.98598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_82_0_line_107 |  | 106 | 109 | 0.043485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_82_0_line_108 |  | 107 | 108 | 0.082006 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
109 | MV_82_0_line_109 |  | 107 | 109 | 0.77016 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_82_0_line_110 |  | 110 | 111 | 0.043437 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_82_0_trafo_52 | 25 MVA 110/20 kV | 112 | 59 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2640269.5385 | 1173471.559
1 | 2640356.9917 | 1173437.136
2 | 2640077.2084 | 1176400.402
3 | 2645747.7786 | 1174385.9911
4 | 2644673.6602 | 1178609.8386
5 | 2645754.4095 | 1174382.7177
6 | 2644669.3141 | 1178673.3069
7 | 2644790.0204 | 1178571.1738
8 | 2645726.125 | 1185913.7453
9 | 2645675.0913 | 1185941.8204
10 | 2645429.7735 | 1185827.7388
11 | 2645428.7516 | 1185738.0599
12 | 2645797.9484 | 1185480.7173
13 | 2645385.0598 | 1185873.4806
14 | 2647056.0972 | 1178819.2331
15 | 2647072.8428 | 1178818.4529
16 | 2646424.9959 | 1185184.2336
17 | 2646980.5336 | 1178759.1644
18 | 2645354.9388 | 1185909.9392
19 | 2645295.8378 | 1185954.2054
20 | 2645263.2314 | 1185958.1613
21 | 2645329.1149 | 1185983.6508
22 | 2645534.9916 | 1185592.6978
23 | 2644968.6088 | 1178649.2953
24 | 2645867.9882 | 1185430.2252
25 | 2646183.2675 | 1185479.5501
26 | 2644950.0843 | 1178632.5699
27 | 2645058.6473 | 1186070.6149
28 | 2645959.5226 | 1185359.4876
29 | 2646121.5556 | 1185308.4039
30 | 2646515.2215 | 1185258.8736
31 | 2646127.6729 | 1185325.6938
32 | 2646228.192 | 1185449.2131
33 | 2644944.5791 | 1186159.5405
34 | 2644342.7545 | 1186431.885
35 | 2644081.938 | 1186732.2362
36 | 2645311.303 | 1178275.2495
37 | 2645337.2567 | 1178275.5012
38 | 2645482.2857 | 1178284.5698
39 | 2645474.2394 | 1178319.9278
40 | 2645453.4202 | 1178369.1298
41 | 2645386.1635 | 1178466.6066
42 | 2645133.0651 | 1178340.5752
43 | 2645120.7429 | 1178314.8799
44 | 2645066.3045 | 1178357.416
45 | 2644911.3924 | 1178445.9802
46 | 2645089.1466 | 1178389.3824
47 | 2644872.0728 | 1178446.1863
48 | 2644844.4647 | 1178444.5347
49 | 2644916.3224 | 1178463.093
50 | 2646267.0541 | 1178290.0923
51 | 2646307.0869 | 1178255.0599
52 | 2646440.7085 | 1178158.3958
53 | 2646864.445 | 1178552.3454
54 | 2646710.3202 | 1178400.529
55 | 2646886.5653 | 1178565.8588
56 | 2645730.6664 | 1178470.5789
57 | 2646493.7548 | 1178128.4125
58 | 2646940.5879 | 1178617.9535
59 | 2645715.2761 | 1178475.8979
60 | 2646542.7404 | 1178093.0286
61 | 2646951.4561 | 1177958.0545
62 | 2646962.3669 | 1177955.634
63 | 2646926.9239 | 1177866.1643
64 | 2647193.5998 | 1178103.8828
65 | 2646873.8645 | 1177856.1666
66 | 2646976.9676 | 1177708.9266
67 | 2646856.7365 | 1177873.2865
68 | 2646912.2247 | 1177851.1746
69 | 2647233.4703 | 1178080.3215
70 | 2646924.4754 | 1177670.1953
71 | 2647335.5538 | 1177332.9411
72 | 2646849.6405 | 1177880.7685
73 | 2647559.1569 | 1177629.1011
74 | 2647282.0344 | 1177290.6077
75 | 2647567.1658 | 1177638.6827
76 | 2646639.2836 | 1178315.2867
77 | 2646731.1773 | 1178296.78
78 | 2646762.215 | 1178356.4538
79 | 2645405.8927 | 1178555.2589
80 | 2645351.5793 | 1178522.6419
81 | 2645340.4872 | 1178475.8997
82 | 2645639.0209 | 1178441.1545
83 | 2645711.6593 | 1178350.9255
84 | 2645852.0812 | 1178374.6647
85 | 2645711.7975 | 1178322.7558
86 | 2645842.2687 | 1178391.9101
87 | 2644812.8072 | 1178449.0006
88 | 2644835.7051 | 1178576.9068
89 | 2644896.0542 | 1178600.6484
90 | 2647608.6547 | 1177688.3188
91 | 2650608.0316 | 1177825.0701
92 | 2650653.3315 | 1177887.3305
93 | 2650640.828 | 1178007.09
94 | 2648911.9626 | 1178424.6233
95 | 2650578.2072 | 1178064.3375
96 | 2648895.0022 | 1178387.843
97 | 2650793.8747 | 1178117.0429
98 | 2650829.675 | 1178148.2905
99 | 2648613.4326 | 1178337.2425
100 | 2648626.8231 | 1178323.663
101 | 2648464.3176 | 1178438.3774
102 | 2648561.659 | 1178064.551
103 | 2648425.9455 | 1178600.3552
104 | 2648632.6745 | 1177987.3398
105 | 2648366.124 | 1178578.2165
106 | 2647741.5047 | 1178880.6901
107 | 2646985.0872 | 1178695.7436
108 | 2646919.6244 | 1178648.0392
109 | 2647723.4319 | 1178914.8315
110 | 2645752.6778 | 1174923.9152
111 | 2645710.8978 | 1174926.9209
112 | 2645715.2761 | 1178475.8979

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98742 | -0.70034 | 0.27549 | 0.13342
1 | 0.98741 | -0.7005 | 0 | 0
2 | 0.98784 | -0.6737 | 0.38903 | 0.18842
3 | 0.98634 | -0.73573 | 0.067521 | 0.032702
4 | 0.98924 | -0.58887 | 0 | 0
5 | 0.98634 | -0.73573 | 0 | 0
6 | 0.98923 | -0.58895 | 0.11076 | 0.053642
7 | 0.98926 | -0.58871 | 0 | 0
8 | 0.99281 | -0.36743 | 0.11072 | 0.053625
9 | 0.99282 | -0.36751 | 0 | 0
10 | 0.99287 | -0.3671 | 0 | 0
11 | 0.99284 | -0.36735 | 0 | 0
12 | 0.99311 | -0.36519 | 0 | 0
13 | 0.99284 | -0.36692 | 0.13212 | 0.063988
14 | 0.99838 | -0.018509 | 0 | 0
15 | 0.99838 | -0.018492 | 0.085664 | 0.041489
16 | 0.99342 | -0.35868 | 0 | 0
17 | 0.99843 | -0.01801 | 0 | 0
18 | 0.99282 | -0.36686 | 0 | 0
19 | 0.99278 | -0.36674 | 0 | 0
20 | 0.99277 | -0.36676 | 0 | 0
21 | 0.99277 | -0.36666 | 0.16064 | 0.077802
22 | 0.99279 | -0.36766 | 0.14205 | 0.0688
23 | 0.98933 | -0.5866 | 0.088871 | 0.043042
24 | 0.99317 | -0.36109 | 0.13132 | 0.063603
25 | 0.99304 | -0.36559 | 0 | 0
26 | 0.98932 | -0.58664 | 0 | 0
27 | 0.99272 | -0.3668 | 0.08161 | 0.039526
28 | 0.99321 | -0.36069 | 0 | 0
29 | 0.99328 | -0.36005 | 0 | 0
30 | 0.99341 | -0.35879 | 0.076586 | 0.037092
31 | 0.99328 | -0.36003 | 0.070112 | 0.033957
32 | 0.99303 | -0.36564 | 0.082797 | 0.040101
33 | 0.99271 | -0.36693 | 0 | 0
34 | 0.99261 | -0.36704 | 0 | 0
35 | 0.99256 | -0.36668 | 0.09506 | 0.04604
36 | 0.9996 | 0.0026979 | 0.13636 | 0.066042
37 | 0.99961 | 0.0027408 | 0 | 0
38 | 0.99963 | 0.0025101 | 0 | 0
39 | 0.99964 | 0.0024515 | 0.1076 | 0.052115
40 | 0.99967 | 0.0026306 | 0 | 0
41 | 0.99972 | 0.0022042 | 0 | 0
42 | 0.98897 | -0.58633 | 0.10663 | 0.051642
43 | 0.98897 | -0.58636 | 0 | 0
44 | 0.98898 | -0.58645 | 0 | 0
45 | 0.98906 | -0.58709 | 0 | 0
46 | 0.98897 | -0.58637 | 0.15187 | 0.073553
47 | 0.9891 | -0.58744 | 0 | 0
48 | 0.98911 | -0.58754 | 0.07918 | 0.038349
49 | 0.98906 | -0.58707 | 0.087749 | 0.042499
50 | 0.99763 | -0.0044874 | 0.13239 | 0.06412
51 | 0.99764 | -0.0045698 | 0 | 0
52 | 0.99767 | -0.0048249 | 0 | 0
53 | 0.99862 | -0.013291 | 0 | 0
54 | 0.99876 | -0.011905 | 0 | 0
55 | 0.9986 | -0.013437 | 0.10696 | 0.051801
56 | 0.99999 | -0.00014297 | 0 | 0
57 | 0.99757 | -0.004132 | 0.14602 | 0.070722
58 | 0.99855 | -0.013855 | 0 | 0
59 | 1 | 0 | -6.1882 | -2.2077
60 | 0.99748 | -0.0035443 | 0 | 0
61 | 0.99679 | 0.0010439 | 0.15994 | 0.077461
62 | 0.99679 | 0.0010225 | 0 | 0
63 | 0.99689 | 0.00034702 | 0 | 0
64 | 0.99674 | 0.0014344 | 0 | 0
65 | 0.99698 | -0.00032467 | 0 | 0
66 | 0.99688 | 0.0002932 | 0 | 0
67 | 0.997 | -0.00048724 | 0.11922 | 0.057739
68 | 0.99688 | 0.00031989 | 0.10618 | 0.051424
69 | 0.99673 | 0.0015039 | 0.12748 | 0.061742
70 | 0.99687 | 0.00038427 | 0.12 | 0.058118
71 | 0.99665 | 0.001677 | 0 | 0
72 | 0.99702 | -0.00057097 | 0 | 0
73 | 0.99653 | 0.0025539 | 0 | 0
74 | 0.99663 | 0.0015445 | 0.15929 | 0.077147
75 | 0.99653 | 0.0025786 | 0.10105 | 0.04894
76 | 0.99736 | -0.0025439 | 0.13009 | 0.063008
77 | 0.99737 | -0.0026839 | 0 | 0
78 | 0.99736 | -0.0027759 | 0.11231 | 0.054395
79 | 0.99968 | 0.0023223 | 0.13119 | 0.063537
80 | 0.9997 | 0.002423 | 0 | 0
81 | 0.9997 | 0.0023495 | 0.1394 | 0.067512
82 | 0.9999 | 0.00077111 | 0 | 0
83 | 0.99986 | 0.0010948 | 0 | 0
84 | 0.99984 | 0.0012308 | 0 | 0
85 | 0.99985 | 0.0010511 | 0.12818 | 0.06208
86 | 0.99984 | 0.0012135 | 0.072003 | 0.034873
87 | 0.98913 | -0.58768 | 0 | 0
88 | 0.98927 | -0.58864 | 0.090513 | 0.043837
89 | 0.9893 | -0.58675 | 0 | 0
90 | 0.99652 | 0.0026319 | 0.072482 | 0.035105
91 | 0.99327 | -0.027877 | 0.14294 | 0.069231
92 | 0.99329 | -0.027742 | 0 | 0
93 | 0.99332 | -0.027967 | 0 | 0
94 | 0.99477 | -0.017039 | 0.062047 | 0.030051
95 | 0.99336 | -0.027614 | 0.15974 | 0.077364
96 | 0.99481 | -0.016754 | 0 | 0
97 | 0.99328 | -0.027673 | 0 | 0
98 | 0.99327 | -0.027601 | 0.12782 | 0.061905
99 | 0.99505 | -0.018658 | 0.14805 | 0.071702
100 | 0.99506 | -0.018692 | 0 | 0
101 | 0.99556 | -0.02232 | 0 | 0
102 | 0.99499 | -0.01812 | 0 | 0
103 | 0.99581 | -0.020096 | 0.10289 | 0.04983
104 | 0.99496 | -0.018328 | 0.16185 | 0.078386
105 | 0.99588 | -0.020639 | 0 | 0
106 | 0.99701 | -0.027935 | 0 | 0
107 | 0.99848 | -0.01453 | 0.1287 | 0.062333
108 | 0.99853 | -0.014084 | 0 | 0
109 | 0.99706 | -0.028223 | 0.075937 | 0.036778
110 | 0.98621 | -0.7351 | 0.11216 | 0.054323
111 | 0.98622 | -0.73516 | 0 | 0
112 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.17986 | 0.056222 | -0.17985 | -0.059367 | 1.3855e-06 | -0.0031446 | 0.0055091 | 0.0055372 | 0.0055372 | 0.98742 | -0.70034 | 0.98741 | -0.7005 | 1.5296
1 | -0.45534 | -0.18965 | 0.45545 | 0.18202 | 0.00010829 | -0.0076238 | 0.014421 | 0.014333 | 0.014421 | 0.98742 | -0.70034 | 0.98784 | -0.6737 | 1.1179
2 | 0.17985 | 0.059367 | -0.1797 | -0.065887 | 0.00015582 | -0.0065208 | 0.0055372 | 0.0056016 | 0.0056016 | 0.98741 | -0.7005 | 0.98634 | -0.73573 | 1.6005
3 | -0.84449 | -0.37044 | 0.84514 | 0.35843 | 0.00065716 | -0.012011 | 0.026948 | 0.026789 | 0.026948 | 0.98784 | -0.6737 | 0.98924 | -0.58887 | 2.089
4 | 0.11218 | 0.033185 | -0.11218 | -0.033357 | 1.1551e-07 | -0.00017134 | 0.0034238 | 0.0034252 | 0.0034252 | 0.98634 | -0.73573 | 0.98634 | -0.73573 | 1.5569
5 | 0.11076 | 0.053568 | -0.11076 | -0.053642 | 1.4614e-06 | -7.3404e-05 | 0.0035903 | 0.0035912 | 0.0035912 | 0.98924 | -0.58887 | 0.98923 | -0.58895 | 1.7101
6 | -0.9559 | -0.412 | 0.95592 | 0.39271 | 2.2214e-05 | -0.019292 | 0.030375 | 0.030157 | 0.030375 | 0.98924 | -0.58887 | 0.98926 | -0.58871 | 2.3805
7 | 0.11218 | 0.033357 | -0.11216 | -0.053314 | 1.4214e-05 | -0.019957 | 0.0034252 | 0.0036351 | 0.0036351 | 0.98634 | -0.73573 | 0.98622 | -0.73516 | 1.6523
8 | -1.3815 | -0.58034 | 1.3815 | 0.5747 | 1.3551e-05 | -0.0056426 | 0.043725 | 0.043661 | 0.043725 | 0.98926 | -0.58871 | 0.98927 | -0.58864 | 3.4267
9 | 0.42554 | 0.18764 | -0.42548 | -0.19336 | 6.0696e-05 | -0.0057205 | 0.013571 | 0.01364 | 0.01364 | 0.98926 | -0.58871 | 0.98913 | -0.58768 | 6.1998
10 | -0.11072 | -0.053625 | 0.11072 | 0.052245 | 9.9721e-07 | -0.0013802 | 0.0035771 | 0.0035598 | 0.0035771 | 0.99281 | -0.36743 | 0.99282 | -0.36751 | 1.626
11 | -0.11072 | -0.052245 | 0.11073 | 0.05193 | 6.1017e-06 | -0.00031455 | 0.0035598 | 0.0035559 | 0.0035598 | 0.99282 | -0.36751 | 0.99287 | -0.3671 | 1.6952
12 | 1.7061 | 0.6921 | -1.706 | -0.70751 | 5.5368e-05 | -0.015412 | 0.053531 | 0.053701 | 0.053701 | 0.99287 | -0.3671 | 0.99284 | -0.36735 | 4.2085
13 | -2.2863 | -0.92623 | 2.2868 | 0.84733 | 0.0005019 | -0.078901 | 0.071722 | 0.07089 | 0.071722 | 0.99287 | -0.3671 | 0.99311 | -0.36519 | 5.6209
14 | 0.4695 | 0.1822 | -0.46948 | -0.1837 | 1.8339e-05 | -0.001501 | 0.014642 | 0.014658 | 0.014658 | 0.99287 | -0.3671 | 0.99284 | -0.36692 | 6.6628
15 | 0.14206 | 0.068592 | -0.14205 | -0.0688 | 6.7529e-06 | -0.00020763 | 0.0045868 | 0.0045895 | 0.0045895 | 0.99284 | -0.36735 | 0.99279 | -0.36766 | 2.1855
16 | 1.564 | 0.63892 | -1.5609 | -0.64995 | 0.0030731 | -0.011027 | 0.049122 | 0.049336 | 0.049336 | 0.99284 | -0.36735 | 0.98933 | -0.5866 | 3.8245
17 | -2.3696 | -0.88692 | 2.3697 | 0.88691 | 8.3364e-05 | -1.1265e-05 | 0.073547 | 0.073545 | 0.073547 | 0.99311 | -0.36519 | 0.99317 | -0.36109 | 5.7013
18 | 0.082803 | 0.039587 | -0.082798 | -0.040037 | 4.8967e-06 | -0.00045058 | 0.0026678 | 0.0026735 | 0.0026735 | 0.99311 | -0.36519 | 0.99304 | -0.36559 | 1.2731
19 | 0.33736 | 0.11971 | -0.33735 | -0.12082 | 6.8398e-06 | -0.0011099 | 0.010408 | 0.010419 | 0.010419 | 0.99284 | -0.36692 | 0.99282 | -0.36686 | 4.736
20 | 0.085664 | 0.041088 | -0.085664 | -0.041489 | 1.6997e-07 | -0.00040072 | 0.0027471 | 0.0027521 | 0.0027521 | 0.99838 | -0.018509 | 0.99838 | -0.018492 | 1.251
21 | 2.656 | 0.94427 | -2.6484 | -0.94137 | 0.0076004 | 0.0028997 | 0.081504 | 0.081675 | 0.081675 | 0.99838 | -0.018509 | 0.99342 | -0.35868 | 6.3314
22 | -2.7416 | -0.98536 | 2.7418 | 0.97051 | 0.00013038 | -0.014849 | 0.084237 | 0.084092 | 0.084237 | 0.99838 | -0.018509 | 0.99843 | -0.01801 | 6.6016
23 | 2.5718 | 0.90441 | -2.5714 | -0.94766 | 0.00034149 | -0.043249 | 0.079219 | 0.079646 | 0.079646 | 0.99342 | -0.35868 | 0.99328 | -0.36005 | 6.2419
24 | 0.076587 | 0.036955 | -0.076586 | -0.037092 | 1.2748e-06 | -0.00013716 | 0.0024711 | 0.0024728 | 0.0024728 | 0.99342 | -0.35868 | 0.99341 | -0.35879 | 1.1775
25 | -2.7418 | -0.97051 | 2.7418 | 0.97055 | 8.0257e-05 | 4.0577e-05 | 0.084092 | 0.08409 | 0.084092 | 0.99843 | -0.01801 | 0.99848 | -0.01453 | 6.5187
26 | 0.33735 | 0.12082 | -0.33734 | -0.12277 | 1.2037e-05 | -0.0019474 | 0.010419 | 0.010438 | 0.010438 | 0.99282 | -0.36686 | 0.99278 | -0.36674 | 4.7447
27 | 0.1767 | 0.046015 | -0.1767 | -0.046974 | 1.5368e-06 | -0.0009593 | 0.0053092 | 0.0053163 | 0.0053163 | 0.99278 | -0.36674 | 0.99277 | -0.36676 | 2.4165
28 | 0.16064 | 0.076757 | -0.16064 | -0.077802 | 1.5942e-06 | -0.0010454 | 0.0051769 | 0.0051901 | 0.0051901 | 0.99278 | -0.36674 | 0.99277 | -0.36666 | 2.3591
29 | 0.1767 | 0.046974 | -0.17669 | -0.052567 | 9.0445e-06 | -0.0055925 | 0.0053163 | 0.0053604 | 0.0053604 | 0.99277 | -0.36676 | 0.99272 | -0.3668 | 2.4366
30 | 1.472 | 0.6069 | -1.472 | -0.60996 | 8.3167e-06 | -0.0030603 | 0.04646 | 0.046494 | 0.046494 | 0.98933 | -0.5866 | 0.98932 | -0.58664 | 3.6437
31 | -2.501 | -0.95051 | 2.5011 | 0.93625 | 0.00010771 | -0.014256 | 0.077768 | 0.077622 | 0.077768 | 0.99317 | -0.36109 | 0.99321 | -0.36069 | 6.0947
32 | 0.082798 | 0.040037 | -0.082797 | -0.040101 | 6.9057e-07 | -6.3384e-05 | 0.0026735 | 0.0026744 | 0.0026744 | 0.99304 | -0.36559 | 0.99303 | -0.36564 | 1.2735
33 | 1.472 | 0.60996 | -1.472 | -0.61843 | 2.307e-05 | -0.0084655 | 0.046494 | 0.046589 | 0.046589 | 0.98932 | -0.58664 | 0.9893 | -0.58675 | 3.6512
34 | 0.095076 | 0.013041 | -0.095074 | -0.016443 | 1.511e-06 | -0.0034019 | 0.0027906 | 0.0028058 | 0.0028058 | 0.99272 | -0.3668 | 0.99271 | -0.36693 | 1.2753
35 | -2.5011 | -0.93625 | 2.5013 | 0.91414 | 0.00016629 | -0.022116 | 0.077622 | 0.077398 | 0.077622 | 0.99321 | -0.36069 | 0.99328 | -0.36005 | 6.0832
36 | 0.070113 | 0.033525 | -0.070112 | -0.033957 | 1.2518e-07 | -0.00043194 | 0.0022586 | 0.0022641 | 0.0022641 | 0.99328 | -0.36005 | 0.99328 | -0.36003 | 1.0291
37 | 0.095074 | 0.016443 | -0.095065 | -0.035469 | 8.8686e-06 | -0.019026 | 0.0028058 | 0.0029509 | 0.0029509 | 0.99271 | -0.36693 | 0.99261 | -0.36704 | 1.3413
38 | 0.095065 | 0.035469 | -0.09506 | -0.04604 | 5.429e-06 | -0.010571 | 0.0029509 | 0.0030719 | 0.0030719 | 0.99261 | -0.36704 | 0.99256 | -0.36668 | 1.3963
39 | -0.13636 | -0.066042 | 0.13636 | 0.066012 | 8.8526e-07 | -3.0406e-05 | 0.0043755 | 0.0043751 | 0.0043755 | 0.9996 | 0.0026979 | 0.99961 | 0.0027408 | 2.0836
40 | -0.13636 | -0.066012 | 0.13637 | 0.06238 | 3.8509e-06 | -0.0036316 | 0.0043751 | 0.0043304 | 0.0043751 | 0.99961 | 0.0027408 | 0.99963 | 0.0025101 | 1.9887
41 | -0.13637 | -0.06238 | 0.13637 | 0.061357 | 1.0713e-06 | -0.0010236 | 0.0043304 | 0.0043182 | 0.0043304 | 0.99963 | 0.0025101 | 0.99964 | 0.0024515 | 1.9684
42 | -0.24397 | -0.11347 | 0.24398 | 0.11341 | 5.7463e-06 | -6.0136e-05 | 0.0077701 | 0.0077693 | 0.0077701 | 0.99964 | 0.0024515 | 0.99967 | 0.0026306 | 3.7
43 | -0.24398 | -0.11341 | 0.24399 | 0.10933 | 1.3725e-05 | -0.0040861 | 0.0077693 | 0.0077203 | 0.0077693 | 0.99967 | 0.0026306 | 0.99972 | 0.0022042 | 3.5315
44 | -0.51458 | -0.23805 | 0.51468 | 0.23155 | 9.7433e-05 | -0.0065013 | 0.016372 | 0.016293 | 0.016372 | 0.99972 | 0.0022042 | 0.9999 | 0.00077111 | 7.4417
45 | 0.27059 | 0.12872 | -0.27059 | -0.12983 | 4.6535e-06 | -0.0011079 | 0.0086525 | 0.0086663 | 0.0086663 | 0.99972 | 0.0022042 | 0.9997 | 0.0023495 | 3.9392
46 | -0.10663 | -0.051642 | 0.10663 | 0.050977 | 4.5371e-07 | -0.0006651 | 0.0034582 | 0.0034498 | 0.0034582 | 0.98897 | -0.58633 | 0.98897 | -0.58636 | 1.5719
47 | -0.10663 | -0.050977 | 0.10663 | 0.04936 | 1.0936e-06 | -0.0016165 | 0.0034498 | 0.0034297 | 0.0034498 | 0.98897 | -0.58636 | 0.98898 | -0.58645 | 1.5681
48 | -0.2585 | -0.122 | 0.25852 | 0.11663 | 2.1225e-05 | -0.0053703 | 0.0083435 | 0.0082777 | 0.0083435 | 0.98898 | -0.58645 | 0.98906 | -0.58709 | 3.7925
49 | 0.15187 | 0.072637 | -0.15187 | -0.073553 | 1.2684e-06 | -0.00091636 | 0.0049139 | 0.0049255 | 0.0049255 | 0.98898 | -0.58645 | 0.98897 | -0.58637 | 2.2389
50 | 0.087749 | 0.042082 | -0.087749 | -0.042499 | 1.9266e-07 | -0.00041695 | 0.0028404 | 0.0028457 | 0.0028457 | 0.98906 | -0.58709 | 0.98906 | -0.58707 | 1.2935
51 | -0.34627 | -0.15871 | 0.34629 | 0.15639 | 1.6346e-05 | -0.0023149 | 0.011118 | 0.011089 | 0.011118 | 0.98906 | -0.58709 | 0.9891 | -0.58744 | 5.0534
52 | -0.34629 | -0.15639 | 0.34629 | 0.15575 | 4.5316e-06 | -0.00064387 | 0.011089 | 0.011082 | 0.011089 | 0.9891 | -0.58744 | 0.98911 | -0.58754 | 5.0407
53 | -0.42547 | -0.1941 | 0.42548 | 0.19336 | 7.9259e-06 | -0.00074263 | 0.013649 | 0.01364 | 0.013649 | 0.98911 | -0.58754 | 0.98913 | -0.58768 | 6.2039
54 | -0.13239 | -0.06412 | 0.13239 | 0.062858 | 1.28e-06 | -0.0012618 | 0.0042565 | 0.0042407 | 0.0042565 | 0.99763 | -0.0044874 | 0.99764 | -0.0045698 | 1.9348
55 | -0.13239 | -0.062858 | 0.1324 | 0.05843 | 4.4182e-06 | -0.0044284 | 0.0042407 | 0.0041874 | 0.0042407 | 0.99764 | -0.0045698 | 0.99767 | -0.0048249 | 1.9276
56 | 1.3551 | 0.57917 | -1.3549 | -0.58057 | 0.00014765 | -0.0014011 | 0.04264 | 0.042657 | 0.042657 | 0.99767 | -0.0048249 | 0.99757 | -0.004132 | 19.3895
57 | -1.4875 | -0.6376 | 1.4892 | 0.62421 | 0.0017048 | -0.013396 | 0.046828 | 0.046671 | 0.046828 | 0.99767 | -0.0048249 | 0.99876 | -0.011905 | 21.2852
58 | -3.9631 | -1.4653 | 3.9637 | 1.4356 | 0.00055127 | -0.029739 | 0.12214 | 0.12185 | 0.12214 | 0.99862 | -0.013291 | 0.99876 | -0.011905 | 9.5724
59 | 3.9631 | 1.4653 | -3.9631 | -1.4685 | 5.9642e-05 | -0.003208 | 0.12214 | 0.12218 | 0.12218 | 0.99862 | -0.013291 | 0.9986 | -0.013437 | 9.575
60 | -5.4529 | -2.0598 | 5.4591 | 1.8819 | 0.0062727 | -0.17794 | 0.16848 | 0.16669 | 0.16848 | 0.99876 | -0.011905 | 0.99999 | -0.00014297 | 13.2034
61 | 3.8561 | 1.4167 | -3.8559 | -1.4261 | 0.00016411 | -0.0093378 | 0.11876 | 0.11885 | 0.11885 | 0.9986 | -0.013437 | 0.99855 | -0.013855 | 9.3144
62 | -5.4591 | -1.8819 | 5.4592 | 1.8798 | 6.972e-05 | -0.0020017 | 0.16669 | 0.16668 | 0.16669 | 0.99999 | -0.00014297 | 1 | 0 | 13.0638
63 | 1.2089 | 0.50985 | -1.2088 | -0.51125 | 0.00011621 | -0.0013996 | 0.037967 | 0.037984 | 0.037984 | 0.99757 | -0.004132 | 0.99748 | -0.0035443 | 17.2652
64 | 3.8559 | 1.4261 | -3.8559 | -1.4312 | 9.1035e-05 | -0.0051729 | 0.11885 | 0.1189 | 0.1189 | 0.99855 | -0.013855 | 0.99853 | -0.014084 | 9.3185
65 | 0.71495 | 0.31732 | -0.71487 | -0.32 | 7.735e-05 | -0.0026862 | 0.02258 | 0.022612 | 0.022612 | 1 | 0 | 0.9999 | 0.00077111 | 10.2782
66 | 0.96636 | 0.4043 | -0.96589 | -0.41318 | 0.00046749 | -0.0088784 | 0.030316 | 0.030418 | 0.030418 | 0.99748 | -0.0035443 | 0.99702 | -0.00057097 | 13.8262
67 | 0.24244 | 0.10695 | -0.24241 | -0.1151 | 2.7298e-05 | -0.0081477 | 0.0076687 | 0.0077669 | 0.0077669 | 0.99748 | -0.0035443 | 0.99737 | -0.0026839 | 3.5304
68 | -0.15994 | -0.077461 | 0.15994 | 0.077196 | 3.9494e-07 | -0.00026502 | 0.0051465 | 0.0051432 | 0.0051465 | 0.99679 | 0.0010439 | 0.99679 | 0.0010225 | 2.3393
69 | -0.28743 | -0.12973 | 0.28746 | 0.12371 | 2.8063e-05 | -0.0060182 | 0.0091326 | 0.0090622 | 0.0091326 | 0.99679 | 0.0010225 | 0.99689 | 0.00034702 | 4.1512
70 | 0.12749 | 0.052532 | -0.12748 | -0.060644 | 7.4506e-06 | -0.0081111 | 0.0039933 | 0.0040886 | 0.0040886 | 0.99679 | 0.0010225 | 0.99674 | 0.0014344 | 1.8584
71 | 0.10618 | 0.051399 | -0.10618 | -0.051424 | 4.3651e-07 | -2.4634e-05 | 0.003416 | 0.0034163 | 0.0034163 | 0.99689 | 0.00034702 | 0.99688 | 0.00031989 | 1.6268
72 | -0.39363 | -0.17511 | 0.39367 | 0.17069 | 3.8606e-05 | -0.0044159 | 0.012476 | 0.012424 | 0.012476 | 0.99689 | 0.00034702 | 0.99698 | -0.00032467 | 5.6708
73 | 0.12748 | 0.060644 | -0.12748 | -0.061742 | 1.037e-06 | -0.0010982 | 0.0040886 | 0.0041024 | 0.0041024 | 0.99674 | 0.0014344 | 0.99673 | 0.0015039 | 1.8647
74 | 0.45297 | 0.18556 | -0.45292 | -0.18983 | 4.8605e-05 | -0.0042719 | 0.014174 | 0.014221 | 0.014221 | 0.99698 | -0.00032467 | 0.99688 | 0.0002932 | 6.4641
75 | -0.84664 | -0.35625 | 0.84666 | 0.35568 | 2.2833e-05 | -0.0005672 | 0.026596 | 0.02659 | 0.026596 | 0.99698 | -0.00032467 | 0.997 | -0.00048724 | 12.0892
76 | 0.12 | 0.056569 | -0.12 | -0.058118 | 1.2927e-06 | -0.0015486 | 0.0038417 | 0.003861 | 0.003861 | 0.99688 | 0.0002932 | 0.99687 | 0.00038427 | 1.755
77 | 0.33292 | 0.13326 | -0.33285 | -0.14578 | 7.7158e-05 | -0.012524 | 0.010384 | 0.010525 | 0.010525 | 0.99688 | 0.0002932 | 0.99665 | 0.001677 | 4.784
78 | -0.96588 | -0.41342 | 0.96589 | 0.41318 | 1.2722e-05 | -0.00024066 | 0.03042 | 0.030418 | 0.03042 | 0.997 | -0.00048724 | 0.99702 | -0.00057097 | 13.8275
79 | 0.17355 | 0.068714 | -0.17353 | -0.082215 | 2.2849e-05 | -0.013501 | 0.0054065 | 0.0055625 | 0.0055625 | 0.99665 | 0.001677 | 0.99653 | 0.0025539 | 2.5284
80 | 0.15929 | 0.077068 | -0.15929 | -0.077147 | 3.1945e-06 | -7.8916e-05 | 0.0051254 | 0.0051265 | 0.0051265 | 0.99665 | 0.001677 | 0.99663 | 0.0015445 | 2.4412
81 | 0.17353 | 0.082215 | -0.17353 | -0.082511 | 5.1618e-07 | -0.00029595 | 0.0055625 | 0.0055662 | 0.0055662 | 0.99653 | 0.0025539 | 0.99653 | 0.0025786 | 2.5301
82 | 0.072483 | 0.033571 | -0.072482 | -0.035105 | 4.6621e-07 | -0.0015337 | 0.002314 | 0.002333 | 0.002333 | 0.99653 | 0.0025786 | 0.99652 | 0.0026319 | 1.0604
83 | -0.13009 | -0.063008 | 0.1301 | 0.060782 | 2.176e-06 | -0.0022257 | 0.0041839 | 0.0041562 | 0.0041839 | 0.99736 | -0.0025439 | 0.99737 | -0.0026839 | 1.9018
84 | 0.11231 | 0.054316 | -0.11231 | -0.054395 | 1.5631e-06 | -7.8897e-05 | 0.0036109 | 0.003612 | 0.003612 | 0.99737 | -0.0026839 | 0.99736 | -0.0027759 | 1.72
85 | -0.13119 | -0.063537 | 0.13119 | 0.063463 | 1.9995e-06 | -7.4334e-05 | 0.0042092 | 0.0042083 | 0.0042092 | 0.99968 | 0.0023223 | 0.9997 | 0.002423 | 2.0044
86 | -0.13119 | -0.063463 | 0.13119 | 0.062317 | 1.132e-06 | -0.0011461 | 0.0042083 | 0.0041939 | 0.0042083 | 0.9997 | 0.002423 | 0.9997 | 0.0023495 | 1.9128
87 | 0.20019 | 0.088457 | -0.20019 | -0.09236 | 8.7849e-06 | -0.0039031 | 0.0063188 | 0.0063652 | 0.0063652 | 0.9999 | 0.00077111 | 0.99986 | 0.0010948 | 2.8933
88 | 0.072004 | 0.030313 | -0.072003 | -0.034849 | 1.3212e-06 | -0.0045364 | 0.0022556 | 0.0023096 | 0.0023096 | 0.99986 | 0.0010948 | 0.99984 | 0.0012308 | 1.0498
89 | 0.12818 | 0.062047 | -0.12818 | -0.06208 | 8.4856e-07 | -3.3088e-05 | 0.0041116 | 0.004112 | 0.004112 | 0.99986 | 0.0010948 | 0.99985 | 0.0010511 | 1.9581
90 | 0.072003 | 0.034849 | -0.072003 | -0.034873 | 1.886e-07 | -2.3561e-05 | 0.0023096 | 0.0023099 | 0.0023099 | 0.99984 | 0.0012308 | 0.99984 | 0.0012135 | 1.0999
91 | -1.472 | -0.61854 | 1.472 | 0.61843 | 2.5128e-05 | -0.0001079 | 0.046591 | 0.046589 | 0.046591 | 0.98927 | -0.58864 | 0.9893 | -0.58675 | 3.6117
92 | -0.14294 | -0.069231 | 0.14295 | 0.069142 | 2.9223e-06 | -8.8857e-05 | 0.004616 | 0.0046148 | 0.004616 | 0.99327 | -0.027877 | 0.99329 | -0.027742 | 2.1981
93 | -0.14295 | -0.069142 | 0.14295 | 0.06587 | 3.9154e-06 | -0.0032721 | 0.0046148 | 0.0045742 | 0.0046148 | 0.99329 | -0.027742 | 0.99332 | -0.027967 | 2.0977
94 | 0.12782 | 0.05547 | -0.12782 | -0.060785 | 5.0179e-06 | -0.0053154 | 0.0040495 | 0.0041134 | 0.0041134 | 0.99332 | -0.027967 | 0.99328 | -0.027673 | 1.8697
95 | -0.27077 | -0.12134 | 0.27079 | 0.12125 | 1.1239e-05 | -9.2903e-05 | 0.0086232 | 0.008622 | 0.0086232 | 0.99332 | -0.027967 | 0.99336 | -0.027614 | 4.1063
96 | 0.4311 | 0.19696 | -0.43052 | -0.19861 | 0.0005756 | -0.0016505 | 0.013754 | 0.013778 | 0.013778 | 0.99477 | -0.017039 | 0.99336 | -0.027614 | 6.5611
97 | -0.49314 | -0.22701 | 0.49316 | 0.22697 | 1.791e-05 | -3.6632e-05 | 0.015754 | 0.015754 | 0.015754 | 0.99477 | -0.017039 | 0.99481 | -0.016754 | 7.502
98 | -0.49316 | -0.22697 | 0.49329 | 0.21765 | 0.00013026 | -0.0093202 | 0.015754 | 0.015642 | 0.015754 | 0.99481 | -0.016754 | 0.99506 | -0.018692 | 7.1607
99 | 0.12782 | 0.060785 | -0.12782 | -0.061905 | 1.0774e-06 | -0.0011194 | 0.0041134 | 0.0041275 | 0.0041275 | 0.99328 | -0.027673 | 0.99327 | -0.027601 | 1.8761
100 | -0.14805 | -0.071702 | 0.14805 | 0.071251 | 5.7913e-07 | -0.00045068 | 0.0047722 | 0.0047665 | 0.0047722 | 0.99505 | -0.018658 | 0.99506 | -0.018692 | 2.1692
101 | -0.8032 | -0.35918 | 0.80363 | 0.34772 | 0.00042375 | -0.011459 | 0.025525 | 0.02539 | 0.025525 | 0.99506 | -0.018692 | 0.99556 | -0.02232 | 11.6024
102 | 0.16186 | 0.070275 | -0.16185 | -0.078266 | 1.2051e-05 | -0.0079904 | 0.0051193 | 0.005216 | 0.005216 | 0.99506 | -0.018692 | 0.99499 | -0.01812 | 2.3709
103 | -0.80363 | -0.34772 | 0.80382 | 0.34764 | 0.00019118 | -7.7262e-05 | 0.02539 | 0.025388 | 0.02539 | 0.99556 | -0.02232 | 0.99581 | -0.020096 | 12.0905
104 | 0.16185 | 0.078266 | -0.16185 | -0.078386 | 5.0867e-06 | -0.00012079 | 0.005216 | 0.0052176 | 0.0052176 | 0.99499 | -0.01812 | 0.99496 | -0.018328 | 2.4846
105 | -0.9067 | -0.39747 | 0.90678 | 0.39593 | 7.2688e-05 | -0.0015447 | 0.028699 | 0.028681 | 0.028699 | 0.99581 | -0.020096 | 0.99588 | -0.020639 | 13.045
106 | -0.90678 | -0.39593 | 0.90785 | 0.37287 | 0.0010727 | -0.023056 | 0.028681 | 0.028417 | 0.028681 | 0.99588 | -0.020639 | 0.99701 | -0.027935 | 13.0368
107 | -0.90785 | -0.37287 | 0.9079 | 0.37186 | 4.6859e-05 | -0.0010182 | 0.028417 | 0.028405 | 0.028417 | 0.99701 | -0.027935 | 0.99706 | -0.028223 | 12.9167
108 | -3.8557 | -1.4414 | 3.8559 | 1.4312 | 0.00017929 | -0.010173 | 0.11901 | 0.1189 | 0.11901 | 0.99848 | -0.01453 | 0.99853 | -0.014084 | 9.3267
109 | 0.98514 | 0.40854 | -0.98383 | -0.40863 | 0.001305 | -9.7912e-05 | 0.030834 | 0.030844 | 0.030844 | 0.99848 | -0.01453 | 0.99706 | -0.028223 | 14.6876
110 | -0.11216 | -0.054323 | 0.11216 | 0.053314 | 7.6895e-07 | -0.0010085 | 0.0036479 | 0.0036351 | 0.0036479 | 0.98621 | -0.7351 | 0.98622 | -0.73516 | 1.6581

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 6.2603 | 2.2426

## res_load
| p_mw | q_mvar
0 | 0.27549 | 0.13342
1 | 0.38903 | 0.18842
2 | 0.067521 | 0.032702
3 | 0.11076 | 0.053642
4 | 0.11072 | 0.053625
5 | 0.13212 | 0.063988
6 | 0.085664 | 0.041489
7 | 0.16064 | 0.077802
8 | 0.14205 | 0.0688
9 | 0.088871 | 0.043042
10 | 0.13132 | 0.063603
11 | 0.08161 | 0.039526
12 | 0.076586 | 0.037092
13 | 0.070112 | 0.033957
14 | 0.082797 | 0.040101
15 | 0.09506 | 0.04604
16 | 0.13636 | 0.066042
17 | 0.1076 | 0.052115
18 | 0.10663 | 0.051642
19 | 0.15187 | 0.073553
20 | 0.07918 | 0.038349
21 | 0.087749 | 0.042499
22 | 0.13239 | 0.06412
23 | 0.10696 | 0.051801
24 | 0.14602 | 0.070722
25 | 0.072137 | 0.034938
26 | 0.15994 | 0.077461
27 | 0.11922 | 0.057739
28 | 0.10618 | 0.051424
29 | 0.12748 | 0.061742
30 | 0.12 | 0.058118
31 | 0.15929 | 0.077147
32 | 0.10105 | 0.04894
33 | 0.13009 | 0.063008
34 | 0.11231 | 0.054395
35 | 0.13119 | 0.063537
36 | 0.1394 | 0.067512
37 | 0.12818 | 0.06208
38 | 0.072003 | 0.034873
39 | 0.090513 | 0.043837
40 | 0.072482 | 0.035105
41 | 0.14294 | 0.069231
42 | 0.062047 | 0.030051
43 | 0.15974 | 0.077364
44 | 0.12782 | 0.061905
45 | 0.14805 | 0.071702
46 | 0.10289 | 0.04983
47 | 0.16185 | 0.078386
48 | 0.1287 | 0.062333
49 | 0.075937 | 0.036778
50 | 0.11216 | 0.054323

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1