## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_8_1_node_128 | 20 | n |  | TRUE
1 | bus_MV_8_1_node_126 | 20 | n |  | TRUE
2 | bus_MV_8_1_node_133 | 20 | n |  | TRUE
3 | bus_MV_8_1_node_129 | 20 | n |  | TRUE
4 | bus_MV_8_1_node_130 | 20 | n |  | TRUE
5 | bus_MV_8_1_node_131 | 20 | n |  | TRUE
6 | bus_MV_8_1_node_57 | 20 | n |  | TRUE
7 | bus_MV_8_1_node_132 | 20 | n |  | TRUE
8 | bus_MV_8_1_node_153 | 20 | n |  | TRUE
9 | bus_MV_8_1_node_134 | 20 | n |  | TRUE
10 | bus_MV_8_1_node_60 | 20 | n |  | TRUE
11 | bus_MV_8_1_node_135 | 20 | n |  | TRUE
12 | bus_MV_8_1_node_64 | 20 | n |  | TRUE
13 | bus_MV_8_1_node_76 | 20 | n |  | TRUE
14 | bus_MV_8_1_node_136 | 20 | n |  | TRUE
15 | bus_MV_8_1_node_138 | 20 | n |  | TRUE
16 | bus_MV_8_1_node_80 | 20 | n |  | TRUE
17 | bus_MV_8_1_node_85 | 20 | n |  | TRUE
18 | bus_MV_8_1_node_139 | 20 | n |  | TRUE
19 | bus_MV_8_1_node_84 | 20 | n |  | TRUE
20 | bus_MV_8_1_node_140 | 20 | n |  | TRUE
21 | bus_MV_8_1_node_141 | 20 | n |  | TRUE
22 | bus_MV_8_1_node_142 | 20 | n |  | TRUE
23 | bus_MV_8_1_node_62 | 20 | n |  | TRUE
24 | bus_MV_8_1_node_34 | 20 | n |  | TRUE
25 | bus_MV_8_1_node_77 | 20 | n |  | TRUE
26 | bus_MV_8_1_node_149 | 20 | n |  | TRUE
27 | bus_MV_8_1_node_151 | 20 | n |  | TRUE
28 | bus_MV_8_1_node_65 | 20 | n |  | TRUE
29 | bus_MV_8_1_node_152 | 20 | n |  | TRUE
30 | bus_MV_8_1_node_59 | 20 | n |  | TRUE
31 | bus_MV_8_1_node_124 | 20 | n |  | TRUE
32 | bus_MV_8_1_node_54 | 20 | n |  | TRUE
33 | bus_MV_8_1_node_56 | 20 | n |  | TRUE
34 | bus_MV_8_1_node_55 | 20 | n |  | TRUE
35 | bus_MV_8_1_node_58 | 20 | n |  | TRUE
36 | bus_MV_8_1_node_67 | 20 | n |  | TRUE
37 | bus_MV_8_1_node_121 | 20 | n |  | TRUE
38 | bus_MV_8_1_node_79 | 20 | n |  | TRUE
39 | bus_MV_8_1_node_61 | 20 | n |  | TRUE
40 | bus_MV_8_1_node_63 | 20 | n |  | TRUE
41 | bus_MV_8_1_node_120 | 20 | n |  | TRUE
42 | bus_MV_8_1_node_68 | 20 | n |  | TRUE
43 | bus_MV_8_1_node_66 | 20 | n |  | TRUE
44 | bus_MV_8_1_node_122 | 20 | n |  | TRUE
45 | bus_MV_8_1_node_69 | 20 | n |  | TRUE
46 | bus_MV_8_1_node_72 | 20 | n |  | TRUE
47 | bus_MV_8_1_node_74 | 20 | n |  | TRUE
48 | bus_MV_8_1_node_75 | 20 | n |  | TRUE
49 | bus_MV_8_1_node_73 | 20 | n |  | TRUE
50 | bus_MV_8_1_node_78 | 20 | n |  | TRUE
51 | bus_MV_8_1_node_81 | 20 | n |  | TRUE
52 | bus_MV_8_1_node_82 | 20 | n |  | TRUE
53 | bus_MV_8_1_node_83 | 20 | n |  | TRUE
54 | bus_MV_8_1_node_123 | 20 | n |  | TRUE
55 | bus_MV_8_1_node_125 | 20 | n |  | TRUE
56 | bus_MV_8_1_node_127 | 20 | n |  | TRUE
57 | bus_HV_8_1_node_54 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_8_1_load_133 | 2 | 0.35813 | 0.17345 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_8_1_load_129 | 3 | 0.30273 | 0.14662 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_8_1_load_130 | 4 | 0.3299 | 0.15978 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_8_1_load_153 | 8 | 0.44487 | 0.21546 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_8_1_load_134 | 9 | 0.16817 | 0.08145 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_8_1_load_135 | 11 | 0.12445 | 0.060275 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_8_1_load_136 | 14 | 0.071738 | 0.034744 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_8_1_load_138 | 15 | 0.19574 | 0.094799 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_8_1_load_139 | 18 | 0.13654 | 0.066132 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_8_1_load_140 | 20 | 0.24872 | 0.12046 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_8_1_load_34 | 24 | 0.18889 | 0.091483 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_8_1_load_77 | 25 | 0.21458 | 0.10392 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_8_1_load_149 | 26 | 0.14076 | 0.068171 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_8_1_load_151 | 27 | 0.28503 | 0.13805 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_8_1_load_152 | 29 | 0.26163 | 0.12671 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_8_1_load_54 | 32 | 0.28095 | 0.13607 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_8_1_load_121 | 37 | 0.092698 | 0.044896 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_8_1_load_61 | 39 | 0.12836 | 0.062169 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_8_1_load_120 | 41 | 0.084286 | 0.040822 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_8_1_load_68 | 42 | 0.11384 | 0.055133 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_8_1_load_66 | 43 | 0.33959 | 0.16447 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_8_1_load_122 | 44 | 0.071646 | 0.0347 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_8_1_load_69 | 45 | 0.085904 | 0.041605 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_8_1_load_72 | 46 | 0.41122 | 0.19916 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_8_1_load_74 | 47 | 0.075676 | 0.036651 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_8_1_load_73 | 49 | 0.068968 | 0.033403 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_8_1_load_78 | 50 | 0.36002 | 0.17437 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_8_1_load_81 | 51 | 0.31071 | 0.15049 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_8_1_load_123 | 54 | 0.15977 | 0.07738 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_8_1_load_127 | 56 | 0.12127 | 0.058734 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_8_1_line_0 |  | 0 | 1 | 0.015924 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
1 | MV_8_1_line_1 |  | 0 | 2 | 0.0091694 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
2 | MV_8_1_line_2 |  | 1 | 3 | 0.031322 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_8_1_line_3 |  | 1 | 31 | 0.053059 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
4 | MV_8_1_line_4 |  | 2 | 9 | 0.016797 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
5 | MV_8_1_line_5 |  | 4 | 5 | 0.040483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_8_1_line_6 |  | 5 | 6 | 0.081231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_8_1_line_7 |  | 5 | 7 | 0.13995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_8_1_line_8 |  | 6 | 26 | 0.039828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_8_1_line_9 |  | 6 | 34 | 0.19599 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_8_1_line_10 |  | 7 | 8 | 0.024865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_8_1_line_11 |  | 9 | 10 | 0.043441 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
12 | MV_8_1_line_12 |  | 10 | 33 | 0.30714 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
13 | MV_8_1_line_13 |  | 11 | 12 | 0.0030179 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_8_1_line_14 |  | 11 | 13 | 0.028248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_8_1_line_15 |  | 12 | 28 | 0.11136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_8_1_line_16 |  | 12 | 14 | 0.037819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_8_1_line_17 |  | 13 | 48 | 0.013615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_8_1_line_18 |  | 15 | 16 | 0.044321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_8_1_line_19 |  | 15 | 17 | 0.015183 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_8_1_line_20 |  | 16 | 38 | 0.44377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_8_1_line_21 |  | 17 | 53 | 0.19492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_8_1_line_22 |  | 18 | 19 | 0.12933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_8_1_line_23 |  | 19 | 52 | 0.46452 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_8_1_line_24 |  | 20 | 21 | 0.043066 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
25 | MV_8_1_line_25 |  | 20 | 22 | 1.2854 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
26 | MV_8_1_line_26 |  | 21 | 23 | 1.511 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
27 | MV_8_1_line_27 |  | 22 | 24 | 1.3557 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
28 | MV_8_1_line_28 |  | 22 | 25 | 1.3444 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_8_1_line_29 |  | 23 | 28 | 1.3239 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
30 | MV_8_1_line_30 |  | 23 | 39 | 0.042676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_8_1_line_31 |  | 24 | 31 | 1.2026 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
32 | MV_8_1_line_32 |  | 27 | 28 | 0.026749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_8_1_line_33 |  | 28 | 40 | 0.34964 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
34 | MV_8_1_line_34 |  | 29 | 30 | 0.014984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_8_1_line_35 |  | 30 | 38 | 1.0192 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
36 | MV_8_1_line_36 |  | 30 | 35 | 0.97329 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
37 | MV_8_1_line_37 |  | 31 | 54 | 0.036348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_8_1_line_38 |  | 32 | 33 | 0.038915 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
39 | MV_8_1_line_39 |  | 34 | 35 | 0.273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_8_1_line_40 |  | 35 | 36 | 0.097976 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
41 | MV_8_1_line_41 |  | 35 | 37 | 0.030075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_8_1_line_42 |  | 36 | 40 | 0.45489 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
43 | MV_8_1_line_43 |  | 37 | 44 | 0.030984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_8_1_line_44 |  | 38 | 50 | 0.055561 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_8_1_line_45 |  | 40 | 41 | 0.070079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_8_1_line_46 |  | 40 | 42 | 0.21629 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_8_1_line_47 |  | 42 | 45 | 0.081994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_8_1_line_48 |  | 43 | 44 | 0.068216 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_8_1_line_49 |  | 46 | 47 | 0.015518 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_8_1_line_50 |  | 46 | 48 | 0.051549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_8_1_line_51 |  | 46 | 49 | 0.020053 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_8_1_line_52 |  | 51 | 52 | 0.01839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_8_1_line_53 |  | 51 | 53 | 0.029374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_8_1_line_54 |  | 54 | 55 | 0.082138 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_8_1_line_55 |  | 55 | 56 | 0.055922 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_8_1_trafo_54 | 25 MVA 110/20 kV | 57 | 32 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2704445.1152 | 1237212.3908
1 | 2704429.3546 | 1237214.4042
2 | 2704454.0636 | 1237214.3919
3 | 2704408.7241 | 1237190.8357
4 | 2704455.8766 | 1237079.6603
5 | 2704416.506 | 1237070.2347
6 | 2704470.377 | 1237023.9798
7 | 2704378.4959 | 1236997.3777
8 | 2704402.7551 | 1237003.1417
9 | 2704470.4562 | 1237218.0578
10 | 2704512.8499 | 1237227.5382
11 | 2704494.5332 | 1236347.1403
12 | 2704493.5716 | 1236344.2797
13 | 2704498.4359 | 1236374.9331
14 | 2704466.8378 | 1236318.4712
15 | 2706095.3464 | 1237219.7306
16 | 2706052.3569 | 1237221.7534
17 | 2706109.0936 | 1237226.2478
18 | 2706280.882 | 1237545.454
19 | 2706363.6773 | 1237546.9594
20 | 2702684.9207 | 1237937.554
21 | 2702714.6527 | 1237906.3221
22 | 2703258.5618 | 1239087.9014
23 | 2704074.8902 | 1237248.2979
24 | 2704460.6762 | 1238461.133
25 | 2701919.2835 | 1239205.4762
26 | 2704490.8664 | 1237058.1664
27 | 2704597.7058 | 1236316.9024
28 | 2704578.8428 | 1236335.9182
29 | 2705135.6415 | 1237028.2646
30 | 2705140.2756 | 1237014.0135
31 | 2704405.8458 | 1237259.8145
32 | 2704703.8695 | 1237062.2868
33 | 2704723.6131 | 1237095.7715
34 | 2704644.9739 | 1236948.751
35 | 2704654.56 | 1236799.5057
36 | 2704745.6858 | 1236763.5176
37 | 2704639.5965 | 1236773.4177
38 | 2705761.6559 | 1237150.0709
39 | 2704110.5424 | 1237224.8826
40 | 2704720.7198 | 1236570.4076
41 | 2704675.6967 | 1236624.1099
42 | 2704904.4887 | 1236456.3403
43 | 2704688.1362 | 1236721.1485
44 | 2704624.7059 | 1236746.2473
45 | 2704964.2784 | 1236460.6564
46 | 2704434.424 | 1236370.1111
47 | 2704437.7886 | 1236354.9625
48 | 2704484.9902 | 1236377.3095
49 | 2704414.8484 | 1236365.7634
50 | 2705706.1434 | 1237147.7476
51 | 2706249.6895 | 1237282.9825
52 | 2706261.7604 | 1237296.8869
53 | 2706225.204 | 1237299.3127
54 | 2704374.6845 | 1237241.324
55 | 2704310.0591 | 1237193.8368
56 | 2704325.7223 | 1237140.1624
57 | 2704703.8695 | 1237062.2868

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99947 | -0.010095 | 0 | 0
1 | 0.99945 | -0.010449 | 0 | 0
2 | 0.99948 | -0.0098909 | 0.35813 | 0.17345
3 | 0.99944 | -0.010336 | 0.30273 | 0.14662
4 | 0.98269 | -0.47733 | 0.3299 | 0.15978
5 | 0.9827 | -0.4775 | 0 | 0
6 | 0.98278 | -0.47825 | 0 | 0
7 | 0.98262 | -0.47675 | 0 | 0
8 | 0.98261 | -0.47661 | 0.44487 | 0.21546
9 | 0.9995 | -0.0094942 | 0.16817 | 0.08145
10 | 0.99956 | -0.0084398 | 0 | 0
11 | 0.98459 | -0.4647 | 0.12445 | 0.060275
12 | 0.98459 | -0.46473 | 0 | 0
13 | 0.98457 | -0.46451 | 0 | 0
14 | 0.98459 | -0.46469 | 0.071738 | 0.034744
15 | 0.98172 | -0.49618 | 0.19574 | 0.094799
16 | 0.98176 | -0.49647 | 0 | 0
17 | 0.98172 | -0.49611 | 0 | 0
18 | 0.98148 | -0.49436 | 0.13654 | 0.066132
19 | 0.9815 | -0.49457 | 0 | 0
20 | 0.99068 | -0.31844 | 0.24872 | 0.12046
21 | 0.99064 | -0.31921 | 0 | 0
22 | 0.99346 | -0.21963 | 0 | 0
23 | 0.98756 | -0.42959 | 0 | 0
24 | 0.99654 | -0.11108 | 0.18889 | 0.091483
25 | 0.9929 | -0.22325 | 0.21458 | 0.10392
26 | 0.98278 | -0.47818 | 0.14076 | 0.068171
27 | 0.98469 | -0.46563 | 0.28503 | 0.13805
28 | 0.9847 | -0.46572 | 0 | 0
29 | 0.98267 | -0.49212 | 0.26163 | 0.12671
30 | 0.98268 | -0.49217 | 0 | 0
31 | 0.99939 | -0.011567 | 0 | 0
32 | 1 | 0 | -5.9687 | -2.6739
33 | 0.99995 | -0.00095271 | 0 | 0
34 | 0.98302 | -0.48034 | 0 | 0
35 | 0.98334 | -0.48316 | 0 | 0
36 | 0.98348 | -0.48136 | 0 | 0
37 | 0.98332 | -0.48298 | 0.092698 | 0.044896
38 | 0.98213 | -0.49926 | 0 | 0
39 | 0.98756 | -0.42953 | 0.12836 | 0.062169
40 | 0.98414 | -0.47292 | 0 | 0
41 | 0.98413 | -0.47285 | 0.084286 | 0.040822
42 | 0.98405 | -0.4735 | 0.11384 | 0.055133
43 | 0.98326 | -0.48311 | 0.33959 | 0.16447
44 | 0.9833 | -0.48282 | 0.071646 | 0.0347
45 | 0.98405 | -0.47342 | 0.085904 | 0.041605
46 | 0.98452 | -0.46407 | 0.41122 | 0.19916
47 | 0.98452 | -0.46406 | 0.075676 | 0.036651
48 | 0.98456 | -0.46442 | 0 | 0
49 | 0.98452 | -0.46409 | 0.068968 | 0.033403
50 | 0.98209 | -0.49951 | 0.36002 | 0.17437
51 | 0.98159 | -0.49511 | 0.31071 | 0.15049
52 | 0.98158 | -0.4951 | 0 | 0
53 | 0.9816 | -0.49525 | 0 | 0
54 | 0.99938 | -0.011453 | 0.15977 | 0.07738
55 | 0.99937 | -0.011346 | 0 | 0
56 | 0.99936 | -0.011267 | 0.12127 | 0.058734
57 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 5.4257 | 2.4377 | -5.4256 | -2.4389 | 8.6017e-05 | -0.0011364 | 0.1718 | 0.17181 | 0.17181 | 0.99947 | -0.010095 | 0.99945 | -0.010449 | 20.4055
1 | -5.4257 | -2.4377 | 5.4257 | 2.4371 | 4.9524e-05 | -0.00065438 | 0.1718 | 0.17179 | 0.1718 | 0.99947 | -0.010095 | 0.99948 | -0.0098909 | 20.4038
2 | 0.30273 | 0.14587 | -0.30273 | -0.14662 | 3.9432e-06 | -0.00074585 | 0.0097062 | 0.0097156 | 0.0097156 | 0.99945 | -0.010449 | 0.99944 | -0.010336 | 4.4162
3 | 5.1229 | 2.293 | -5.1226 | -2.2968 | 0.00025525 | -0.0038149 | 0.16211 | 0.16216 | 0.16216 | 0.99945 | -0.010449 | 0.99939 | -0.011567 | 19.2588
4 | -5.7839 | -2.6105 | 5.784 | 2.6093 | 0.00010325 | -0.0011873 | 0.18328 | 0.18326 | 0.18328 | 0.99948 | -0.0098909 | 0.9995 | -0.0094942 | 21.7672
5 | -0.3299 | -0.15978 | 0.32991 | 0.15885 | 6.2597e-06 | -0.00093156 | 0.010768 | 0.010756 | 0.010768 | 0.98269 | -0.47733 | 0.9827 | -0.4775 | 4.8946
6 | -0.77483 | -0.37052 | 0.77489 | 0.36867 | 6.8963e-05 | -0.0018527 | 0.02523 | 0.025206 | 0.02523 | 0.9827 | -0.4775 | 0.98278 | -0.47825 | 11.468
7 | 0.44491 | 0.21167 | -0.44488 | -0.21489 | 3.9248e-05 | -0.0032149 | 0.014473 | 0.014514 | 0.014514 | 0.9827 | -0.4775 | 0.98262 | -0.47675 | 6.5975
8 | 0.14076 | 0.067253 | -0.14076 | -0.068171 | 1.1192e-06 | -0.00091814 | 0.0045822 | 0.0045939 | 0.0045939 | 0.98278 | -0.47825 | 0.98278 | -0.47818 | 2.0881
9 | -0.91565 | -0.43592 | 0.91588 | 0.43147 | 0.00023172 | -0.004452 | 0.029788 | 0.029731 | 0.029788 | 0.98278 | -0.47825 | 0.98302 | -0.48034 | 13.54
10 | 0.44488 | 0.21489 | -0.44487 | -0.21546 | 6.9966e-06 | -0.00057114 | 0.014514 | 0.014522 | 0.014522 | 0.98262 | -0.47675 | 0.98261 | -0.47661 | 6.6008
11 | -5.9521 | -2.6908 | 5.9524 | 2.6877 | 0.00028289 | -0.0030562 | 0.18866 | 0.18862 | 0.18866 | 0.9995 | -0.0094942 | 0.99956 | -0.0084398 | 22.4061
12 | -5.9524 | -2.6877 | 5.9544 | 2.6661 | 0.0019967 | -0.021622 | 0.18862 | 0.18834 | 0.18862 | 0.99956 | -0.0084398 | 0.99995 | -0.00095271 | 22.4015
13 | -0.68036 | -0.32696 | 0.68036 | 0.32689 | 1.9733e-06 | -6.9267e-05 | 0.022132 | 0.022131 | 0.022132 | 0.98459 | -0.4647 | 0.98459 | -0.46473 | 10.0598
14 | 0.5559 | 0.26668 | -0.55589 | -0.26733 | 1.2329e-05 | -0.00065015 | 0.018077 | 0.018086 | 0.018086 | 0.98459 | -0.4647 | 0.98457 | -0.46451 | 8.2207
15 | -0.7521 | -0.36076 | 0.75218 | 0.35821 | 8.8799e-05 | -0.0025514 | 0.024457 | 0.024424 | 0.024457 | 0.98459 | -0.46473 | 0.9847 | -0.46572 | 11.1166
16 | 0.071738 | 0.033869 | -0.071738 | -0.034744 | 2.7444e-07 | -0.00087526 | 0.0023259 | 0.002337 | 0.002337 | 0.98459 | -0.46473 | 0.98459 | -0.46469 | 1.0623
17 | 0.55589 | 0.26733 | -0.55588 | -0.26765 | 5.9464e-06 | -0.00031335 | 0.018086 | 0.01809 | 0.01809 | 0.98457 | -0.46451 | 0.98456 | -0.46442 | 8.2225
18 | -0.64308 | -0.29185 | 0.6431 | 0.29084 | 2.5499e-05 | -0.0010124 | 0.020766 | 0.020753 | 0.020766 | 0.98172 | -0.49618 | 0.98176 | -0.49647 | 9.439
19 | 0.44734 | 0.19705 | -0.44734 | -0.1974 | 4.1888e-06 | -0.00034814 | 0.014374 | 0.014378 | 0.014378 | 0.98172 | -0.49618 | 0.98172 | -0.49611 | 6.5353
20 | -0.6431 | -0.29084 | 0.64335 | 0.28069 | 0.00025365 | -0.010141 | 0.020753 | 0.020631 | 0.020753 | 0.98176 | -0.49647 | 0.98213 | -0.49926 | 9.4334
21 | 0.44734 | 0.1974 | -0.44728 | -0.20186 | 5.3992e-05 | -0.0044687 | 0.014378 | 0.014431 | 0.014431 | 0.98172 | -0.49611 | 0.9816 | -0.49525 | 6.5598
22 | -0.13654 | -0.066132 | 0.13655 | 0.063158 | 3.4088e-06 | -0.0029736 | 0.0044623 | 0.0044249 | 0.0044623 | 0.98148 | -0.49436 | 0.9815 | -0.49457 | 2.0283
23 | -0.13655 | -0.063158 | 0.13656 | 0.052476 | 1.1795e-05 | -0.010682 | 0.0044249 | 0.0043024 | 0.0044249 | 0.9815 | -0.49457 | 0.98158 | -0.4951 | 2.0113
24 | 4.1597 | 1.8176 | -4.1596 | -1.8207 | 0.00013793 | -0.0031026 | 0.13228 | 0.13231 | 0.13231 | 0.99068 | -0.31844 | 0.99064 | -0.31921 | 15.7142
25 | -4.4084 | -1.938 | 4.4175 | 1.9478 | 0.0090184 | 0.0097819 | 0.14032 | 0.14028 | 0.14032 | 0.99068 | -0.31844 | 0.99346 | -0.21963 | 17.1126
26 | 4.1596 | 1.8207 | -4.1502 | -1.8108 | 0.0094313 | 0.0098279 | 0.13231 | 0.13236 | 0.13236 | 0.99064 | -0.31921 | 0.98756 | -0.42959 | 16.1413
27 | -4.6321 | -2.0502 | 4.6426 | 2.0619 | 0.010465 | 0.011678 | 0.14719 | 0.14715 | 0.14719 | 0.99346 | -0.21963 | 0.99654 | -0.11108 | 17.9504
28 | 0.21469 | 0.10241 | -0.21458 | -0.10392 | 0.00011476 | -0.0015113 | 0.0069118 | 0.0069318 | 0.0069318 | 0.99346 | -0.21963 | 0.9929 | -0.22325 | 3.3008
29 | 4.0218 | 1.7497 | -4.0112 | -1.7862 | 0.010553 | -0.036499 | 0.1282 | 0.12873 | 0.12873 | 0.98756 | -0.42959 | 0.9847 | -0.46572 | 35.5595
30 | 0.12836 | 0.061175 | -0.12836 | -0.062169 | 9.8726e-07 | -0.00099345 | 0.0041565 | 0.0041691 | 0.0041691 | 0.98756 | -0.42959 | 0.98756 | -0.42953 | 1.895
31 | -4.8315 | -2.1534 | 4.8416 | 2.1648 | 0.010061 | 0.011466 | 0.15323 | 0.15319 | 0.15323 | 0.99654 | -0.11108 | 0.99939 | -0.011567 | 18.6865
32 | -0.28503 | -0.13805 | 0.28503 | 0.13743 | 3.0756e-06 | -0.00061835 | 0.0092845 | 0.0092766 | 0.0092845 | 0.98469 | -0.46563 | 0.9847 | -0.46572 | 4.2202
33 | 2.974 | 1.2905 | -2.9725 | -1.301 | 0.0015276 | -0.010514 | 0.095041 | 0.095177 | 0.095177 | 0.9847 | -0.46572 | 0.98414 | -0.47292 | 26.2921
34 | -0.26163 | -0.12671 | 0.26163 | 0.12637 | 1.458e-06 | -0.00034504 | 0.0085396 | 0.0085352 | 0.0085396 | 0.98267 | -0.49212 | 0.98268 | -0.49217 | 3.8816
35 | 1.0039 | 0.42163 | -1.0034 | -0.45501 | 0.00050985 | -0.033376 | 0.031986 | 0.032383 | 0.032383 | 0.98268 | -0.49217 | 0.98213 | -0.49926 | 8.9456
36 | -1.2655 | -0.548 | 1.2663 | 0.51629 | 0.00076449 | -0.031709 | 0.040512 | 0.040145 | 0.040512 | 0.98268 | -0.49217 | 0.98334 | -0.48316 | 11.1913
37 | 0.28105 | 0.13196 | -0.28104 | -0.13282 | 3.9075e-06 | -0.00086561 | 0.0089684 | 0.0089791 | 0.0089791 | 0.99939 | -0.011567 | 0.99938 | -0.011453 | 4.0814
38 | 5.9547 | 2.6634 | -5.9544 | -2.6661 | 0.00025257 | -0.0027412 | 0.18831 | 0.18834 | 0.18834 | 1 | 0 | 0.99995 | -0.00095271 | 22.3685
39 | -0.91588 | -0.43147 | 0.9162 | 0.42527 | 0.00032131 | -0.0062055 | 0.029731 | 0.029653 | 0.029731 | 0.98302 | -0.48034 | 0.98334 | -0.48316 | 13.5142
40 | -2.6865 | -1.1841 | 2.6868 | 1.1812 | 0.00035137 | -0.0029952 | 0.086187 | 0.086149 | 0.086187 | 0.98334 | -0.48316 | 0.98348 | -0.48136 | 23.8086
41 | 0.50397 | 0.24259 | -0.50396 | -0.24329 | 1.0831e-05 | -0.00069111 | 0.01642 | 0.016429 | 0.016429 | 0.98334 | -0.48316 | 0.98332 | -0.48298 | 7.4675
42 | -2.6868 | -1.1812 | 2.6884 | 1.1672 | 0.0016273 | -0.013922 | 0.086149 | 0.085971 | 0.086149 | 0.98348 | -0.48136 | 0.98414 | -0.47292 | 23.798
43 | 0.41126 | 0.19839 | -0.41125 | -0.1991 | 7.4378e-06 | -0.00071309 | 0.013405 | 0.013414 | 0.013414 | 0.98332 | -0.48298 | 0.9833 | -0.48282 | 6.0973
44 | 0.36004 | 0.17431 | -0.36002 | -0.17437 | 1.3686e-05 | -5.5404e-05 | 0.011758 | 0.011758 | 0.011758 | 0.98213 | -0.49926 | 0.98209 | -0.49951 | 5.5992
45 | 0.084287 | 0.039201 | -0.084286 | -0.040822 | 7.0075e-07 | -0.0016203 | 0.0027267 | 0.0027471 | 0.0027471 | 0.98414 | -0.47292 | 0.98413 | -0.47285 | 1.2487
46 | 0.19976 | 0.094603 | -0.19974 | -0.094843 | 1.6206e-05 | -0.00023991 | 0.0064833 | 0.0064865 | 0.0064865 | 0.98414 | -0.47292 | 0.98405 | -0.4735 | 3.0888
47 | 0.085905 | 0.03971 | -0.085904 | -0.041605 | 8.5087e-07 | -0.0018955 | 0.0027763 | 0.0028001 | 0.0028001 | 0.98405 | -0.4735 | 0.98405 | -0.47342 | 1.2728
48 | -0.33959 | -0.16447 | 0.33961 | 0.1644 | 1.4914e-05 | -6.9394e-05 | 0.011078 | 0.011077 | 0.011078 | 0.98326 | -0.48311 | 0.9833 | -0.48282 | 5.2752
49 | 0.075676 | 0.036292 | -0.075676 | -0.036651 | 1.2569e-07 | -0.00035908 | 0.0024609 | 0.0024655 | 0.0024655 | 0.98452 | -0.46407 | 0.98452 | -0.46406 | 1.1207
50 | -0.55586 | -0.26883 | 0.55588 | 0.26765 | 2.2538e-05 | -0.0011863 | 0.018105 | 0.01809 | 0.018105 | 0.98452 | -0.46407 | 0.98456 | -0.46442 | 8.2294
51 | 0.068968 | 0.033379 | -0.068968 | -0.033403 | 1.8036e-07 | -2.3091e-05 | 0.0022466 | 0.0022469 | 0.0022469 | 0.98452 | -0.46407 | 0.98452 | -0.46409 | 1.07
52 | 0.13656 | 0.052053 | -0.13656 | -0.052476 | 4.5399e-07 | -0.00042292 | 0.004298 | 0.0043024 | 0.0043024 | 0.98159 | -0.49511 | 0.98158 | -0.4951 | 1.9556
53 | -0.44727 | -0.20254 | 0.44728 | 0.20186 | 8.1717e-06 | -0.00067333 | 0.01444 | 0.014431 | 0.01444 | 0.98159 | -0.49511 | 0.9816 | -0.49525 | 6.5635
54 | 0.12127 | 0.055443 | -0.12127 | -0.057401 | 1.6369e-06 | -0.0019582 | 0.0038518 | 0.0038757 | 0.0038757 | 0.99938 | -0.011453 | 0.99937 | -0.011346 | 1.7617
55 | 0.12127 | 0.057401 | -0.12127 | -0.058734 | 1.1262e-06 | -0.0013332 | 0.0038757 | 0.0038923 | 0.0038923 | 0.99937 | -0.011346 | 0.99936 | -0.011267 | 1.7692

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 6.2496 | 2.8099

## res_load
| p_mw | q_mvar
0 | 0.35813 | 0.17345
1 | 0.30273 | 0.14662
2 | 0.3299 | 0.15978
3 | 0.44487 | 0.21546
4 | 0.16817 | 0.08145
5 | 0.12445 | 0.060275
6 | 0.071738 | 0.034744
7 | 0.19574 | 0.094799
8 | 0.13654 | 0.066132
9 | 0.24872 | 0.12046
10 | 0.18889 | 0.091483
11 | 0.21458 | 0.10392
12 | 0.14076 | 0.068171
13 | 0.28503 | 0.13805
14 | 0.26163 | 0.12671
15 | 0.28095 | 0.13607
16 | 0.092698 | 0.044896
17 | 0.12836 | 0.062169
18 | 0.084286 | 0.040822
19 | 0.11384 | 0.055133
20 | 0.33959 | 0.16447
21 | 0.071646 | 0.0347
22 | 0.085904 | 0.041605
23 | 0.41122 | 0.19916
24 | 0.075676 | 0.036651
25 | 0.068968 | 0.033403
26 | 0.36002 | 0.17437
27 | 0.31071 | 0.15049
28 | 0.15977 | 0.07738
29 | 0.12127 | 0.058734

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1