## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_90_2_node_156 | 20 | n |  | TRUE
1 | bus_MV_90_2_node_157 | 20 | n |  | TRUE
2 | bus_MV_90_2_node_163 | 20 | n |  | TRUE
3 | bus_MV_90_2_node_158 | 20 | n |  | TRUE
4 | bus_MV_90_2_node_159 | 20 | n |  | TRUE
5 | bus_MV_90_2_node_161 | 20 | n |  | TRUE
6 | bus_MV_90_2_node_160 | 20 | n |  | TRUE
7 | bus_MV_90_2_node_123 | 20 | n |  | TRUE
8 | bus_MV_90_2_node_162 | 20 | n |  | TRUE
9 | bus_MV_90_2_node_164 | 20 | n |  | TRUE
10 | bus_MV_90_2_node_189 | 20 | n |  | TRUE
11 | bus_MV_90_2_node_165 | 20 | n |  | TRUE
12 | bus_MV_90_2_node_103 | 20 | n |  | TRUE
13 | bus_MV_90_2_node_96 | 20 | n |  | TRUE
14 | bus_MV_90_2_node_170 | 20 | n |  | TRUE
15 | bus_MV_90_2_node_98 | 20 | n |  | TRUE
16 | bus_MV_90_2_node_97 | 20 | n |  | TRUE
17 | bus_MV_90_2_node_178 | 20 | n |  | TRUE
18 | bus_MV_90_2_node_95 | 20 | n |  | TRUE
19 | bus_MV_90_2_node_197 | 20 | n |  | TRUE
20 | bus_MV_90_2_node_179 | 20 | n |  | TRUE
21 | bus_MV_90_2_node_79 | 20 | n |  | TRUE
22 | bus_MV_90_2_node_180 | 20 | n |  | TRUE
23 | bus_MV_90_2_node_126 | 20 | n |  | TRUE
24 | bus_MV_90_2_node_184 | 20 | n |  | TRUE
25 | bus_MV_90_2_node_89 | 20 | n |  | TRUE
26 | bus_MV_90_2_node_99 | 20 | n |  | TRUE
27 | bus_MV_90_2_node_122 | 20 | n |  | TRUE
28 | bus_MV_90_2_node_198 | 20 | n |  | TRUE
29 | bus_MV_90_2_node_94 | 20 | n |  | TRUE
30 | bus_MV_90_2_node_199 | 20 | n |  | TRUE
31 | bus_MV_90_2_node_124 | 20 | n |  | TRUE
32 | bus_MV_90_2_node_75 | 20 | n |  | TRUE
33 | bus_MV_90_2_node_76 | 20 | n |  | TRUE
34 | bus_MV_90_2_node_77 | 20 | n |  | TRUE
35 | bus_MV_90_2_node_78 | 20 | n |  | TRUE
36 | bus_MV_90_2_node_119 | 20 | n |  | TRUE
37 | bus_MV_90_2_node_80 | 20 | n |  | TRUE
38 | bus_MV_90_2_node_82 | 20 | n |  | TRUE
39 | bus_MV_90_2_node_86 | 20 | n |  | TRUE
40 | bus_MV_90_2_node_83 | 20 | n |  | TRUE
41 | bus_MV_90_2_node_102 | 20 | n |  | TRUE
42 | bus_MV_90_2_node_85 | 20 | n |  | TRUE
43 | bus_MV_90_2_node_87 | 20 | n |  | TRUE
44 | bus_MV_90_2_node_88 | 20 | n |  | TRUE
45 | bus_MV_90_2_node_90 | 20 | n |  | TRUE
46 | bus_MV_90_2_node_92 | 20 | n |  | TRUE
47 | bus_MV_90_2_node_91 | 20 | n |  | TRUE
48 | bus_MV_90_2_node_93 | 20 | n |  | TRUE
49 | bus_MV_90_2_node_100 | 20 | n |  | TRUE
50 | bus_MV_90_2_node_101 | 20 | n |  | TRUE
51 | bus_MV_90_2_node_104 | 20 | n |  | TRUE
52 | bus_MV_90_2_node_120 | 20 | n |  | TRUE
53 | bus_MV_90_2_node_125 | 20 | n |  | TRUE
54 | bus_HV_90_2_node_87 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_90_2_load_156 | 0 | 0.37165 | 0.18 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_90_2_load_158 | 3 | 0.074978 | 0.036313 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_90_2_load_160 | 6 | 0.09234 | 0.044722 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_90_2_load_162 | 8 | 0.13763 | 0.066657 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_90_2_load_189 | 10 | 0.24593 | 0.11911 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_90_2_load_165 | 11 | 0.071807 | 0.034778 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_90_2_load_170 | 14 | 0.096852 | 0.046907 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_90_2_load_98 | 15 | 0.24563 | 0.11897 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_90_2_load_197 | 19 | 0.34424 | 0.16672 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_90_2_load_179 | 20 | 0.079298 | 0.038406 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_90_2_load_180 | 22 | 0.26468 | 0.12819 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_90_2_load_184 | 24 | 0.3898 | 0.18879 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_90_2_load_99 | 26 | 0.18155 | 0.087927 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_90_2_load_198 | 28 | 0.24234 | 0.11737 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_90_2_load_124 | 31 | 0.24445 | 0.11839 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_90_2_load_75 | 32 | 0.23524 | 0.11393 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_90_2_load_119 | 36 | 0.32975 | 0.15971 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_90_2_load_80 | 37 | 0.21576 | 0.1045 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_90_2_load_86 | 39 | 0.34738 | 0.16824 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_90_2_load_83 | 40 | 0.12803 | 0.06201 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_90_2_load_90 | 45 | 0.34307 | 0.16616 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_90_2_load_100 | 49 | 0.17831 | 0.086359 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_90_2_load_104 | 51 | 0.1851 | 0.089649 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_90_2_line_0 |  | 0 | 1 | 0.018512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_90_2_line_1 |  | 1 | 2 | 0.37068 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_90_2_line_2 |  | 2 | 9 | 0.34551 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_90_2_line_3 |  | 2 | 8 | 0.004569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_90_2_line_4 |  | 3 | 4 | 0.23205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_90_2_line_5 |  | 4 | 5 | 0.33197 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_90_2_line_6 |  | 5 | 7 | 1.3641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_90_2_line_7 |  | 5 | 6 | 0.11979 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_90_2_line_8 |  | 7 | 10 | 0.079132 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_90_2_line_9 |  | 7 | 52 | 0.93678 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_90_2_line_10 |  | 9 | 10 | 0.027822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_90_2_line_11 |  | 11 | 12 | 0.20694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_90_2_line_12 |  | 11 | 13 | 0.030266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_90_2_line_13 |  | 12 | 37 | 0.095241 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_90_2_line_14 |  | 12 | 41 | 0.47591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_90_2_line_15 |  | 13 | 44 | 0.015579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_90_2_line_16 |  | 14 | 15 | 0.066221 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_90_2_line_17 |  | 14 | 16 | 0.016013 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_90_2_line_18 |  | 15 | 42 | 0.010466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_90_2_line_19 |  | 16 | 46 | 0.18749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_90_2_line_20 |  | 17 | 18 | 0.10601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_90_2_line_21 |  | 17 | 19 | 0.025959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_90_2_line_22 |  | 18 | 45 | 0.16633 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_90_2_line_23 |  | 20 | 21 | 0.24284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_90_2_line_24 |  | 21 | 34 | 0.65351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_90_2_line_25 |  | 22 | 23 | 0.066049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_90_2_line_26 |  | 23 | 53 | 0.18562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_90_2_line_27 |  | 24 | 25 | 0.11587 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_90_2_line_28 |  | 24 | 26 | 0.50169 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_90_2_line_29 |  | 24 | 27 | 0.081799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_90_2_line_30 |  | 25 | 38 | 0.14977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_90_2_line_31 |  | 26 | 48 | 0.14042 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_90_2_line_32 |  | 27 | 52 | 0.89057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_90_2_line_33 |  | 28 | 29 | 0.11919 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_90_2_line_34 |  | 28 | 30 | 0.030701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_90_2_line_35 |  | 29 | 42 | 0.11994 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_90_2_line_36 |  | 30 | 31 | 2.2962 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_90_2_line_37 |  | 31 | 53 | 0.10686 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_90_2_line_38 |  | 32 | 33 | 0.011657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_90_2_line_39 |  | 32 | 34 | 0.023325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_90_2_line_40 |  | 33 | 35 | 0.17429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_90_2_line_41 |  | 35 | 36 | 0.24473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_90_2_line_42 |  | 36 | 52 | 0.26611 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_90_2_line_43 |  | 38 | 39 | 0.003139 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_90_2_line_44 |  | 40 | 41 | 0.35358 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_90_2_line_45 |  | 41 | 51 | 0.042172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_90_2_line_46 |  | 41 | 50 | 0.26148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_90_2_line_47 |  | 43 | 44 | 0.22256 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
48 | MV_90_2_line_48 |  | 44 | 45 | 0.015151 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
49 | MV_90_2_line_49 |  | 45 | 46 | 0.0306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_90_2_line_50 |  | 45 | 47 | 0.047982 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_90_2_line_51 |  | 47 | 48 | 0.37362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_90_2_line_52 |  | 49 | 50 | 0.076628 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_90_2_trafo_87 | 25 MVA 110/20 kV | 54 | 43 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2594916.235 | 1117707.7122
1 | 2594902.1172 | 1117695.8629
2 | 2594996.6425 | 1117337.4404
3 | 2594438.5181 | 1116373.4053
4 | 2594620.385 | 1116502.9691
5 | 2594821.1027 | 1116767.3882
6 | 2594938.994 | 1116788.6308
7 | 2595318.443 | 1117530.0181
8 | 2594992.4346 | 1117335.6319
9 | 2595221.6875 | 1117484.9394
10 | 2595245.3699 | 1117499.6499
11 | 2596805.0422 | 1117841.1192
12 | 2596766.4379 | 1118035.302
13 | 2596818.3955 | 1117816.3888
14 | 2596840.3144 | 1117985.2084
15 | 2596900.92 | 1118011.8964
16 | 2596834.6767 | 1117970.2666
17 | 2597052.7266 | 1117644.6388
18 | 2596986.2731 | 1117726.6124
19 | 2597032.8529 | 1117627.8738
20 | 2596494.5931 | 1116480.683
21 | 2596506.2807 | 1116246.161
22 | 2599552.5622 | 1117627.8334
23 | 2599515.4066 | 1117681.6519
24 | 2596611.6711 | 1117469.4778
25 | 2596604.2658 | 1117584.0493
26 | 2597094.5961 | 1117333.5322
27 | 2596579.6142 | 1117394.7596
28 | 2597062.1241 | 1117841.2193
29 | 2596961.0665 | 1117904.4236
30 | 2597084.429 | 1117860.2398
31 | 2599379.7207 | 1117925.93
32 | 2596056.3915 | 1116733.4707
33 | 2596050.4778 | 1116743.524
34 | 2596068.3346 | 1116713.4196
35 | 2595966.377 | 1116896.0442
36 | 2595793.6012 | 1117045.2259
37 | 2596671.8042 | 1118024.5603
38 | 2596618.0258 | 1117731.4248
39 | 2596620.1777 | 1117729.1336
40 | 2597051.9286 | 1118767.1002
41 | 2596988.27 | 1118419.2953
42 | 2596911.2851 | 1118013.5473
43 | 2596700.6633 | 1117672.7717
44 | 2596821.0886 | 1117801.4911
45 | 2596834.0342 | 1117793.6137
46 | 2596843.295 | 1117822.1894
47 | 2596876.4375 | 1117771.1579
48 | 2597047.8369 | 1117465.9425
49 | 2597059.1709 | 1118140.8565
50 | 2597092.2106 | 1118209.9962
51 | 2597022.3345 | 1118395.0106
52 | 2595888.2465 | 1117293.9373
53 | 2599444.2978 | 1117840.7924
54 | 2596700.6633 | 1117672.7717

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99147 | -0.0094127 | 0.37165 | 0.18
1 | 0.99148 | -0.0094962 | 0 | 0
2 | 0.99175 | -0.0077823 | 0 | 0
3 | 0.99175 | -0.0086304 | 0.074978 | 0.036313
4 | 0.99178 | -0.0088011 | 0 | 0
5 | 0.99182 | -0.0083332 | 0 | 0
6 | 0.9918 | -0.0084698 | 0.09234 | 0.044722
7 | 0.9921 | -0.0091644 | 0 | 0
8 | 0.99174 | -0.0077746 | 0.13763 | 0.066657
9 | 0.99197 | -0.0098102 | 0 | 0
10 | 0.99199 | -0.0099655 | 0.24593 | 0.11911
11 | 0.99935 | -0.0069226 | 0.071807 | 0.034778
12 | 0.99917 | -0.0054552 | 0 | 0
13 | 0.99938 | -0.0071577 | 0 | 0
14 | 0.99904 | -0.0048151 | 0.096852 | 0.046907
15 | 0.99891 | -0.0056718 | 0.24563 | 0.11897
16 | 0.99906 | -0.005015 | 0 | 0
17 | 0.99921 | -0.008012 | 0 | 0
18 | 0.99925 | -0.0084366 | 0 | 0
19 | 0.9992 | -0.0079055 | 0.34424 | 0.16672
20 | 0.99261 | -0.017785 | 0.079298 | 0.038406
21 | 0.99263 | -0.017974 | 0 | 0
22 | 0.99614 | -0.023098 | 0.26468 | 0.12819
23 | 0.99616 | -0.023306 | 0 | 0
24 | 0.99511 | -0.027429 | 0.3898 | 0.18879
25 | 0.99506 | -0.02698 | 0 | 0
26 | 0.9973 | -0.007632 | 0.18155 | 0.087927
27 | 0.99495 | -0.026533 | 0 | 0
28 | 0.99855 | -0.0079588 | 0.24234 | 0.11737
29 | 0.99873 | -0.0067756 | 0 | 0
30 | 0.99853 | -0.0077886 | 0 | 0
31 | 0.99628 | -0.023454 | 0.24445 | 0.11839
32 | 0.9927 | -0.018027 | 0.23524 | 0.11393
33 | 0.9927 | -0.018055 | 0 | 0
34 | 0.9927 | -0.018037 | 0 | 0
35 | 0.99277 | -0.018451 | 0 | 0
36 | 0.99287 | -0.018928 | 0.32975 | 0.15971
37 | 0.99913 | -0.0057044 | 0.21576 | 0.1045
38 | 0.99499 | -0.026369 | 0 | 0
39 | 0.99499 | -0.026356 | 0.34738 | 0.16824
40 | 0.99879 | -0.0036139 | 0.12803 | 0.06201
41 | 0.99887 | -0.0030592 | 0 | 0
42 | 0.9989 | -0.0055839 | 0 | 0
43 | 1 | 0 | -5.0798 | -2.2709
44 | 0.9994 | -0.0072782 | 0 | 0
45 | 0.99936 | -0.0076976 | 0.34307 | 0.16616
46 | 0.99932 | -0.0073257 | 0 | 0
47 | 0.99914 | -0.0097275 | 0 | 0
48 | 0.99797 | -0.0017925 | 0 | 0
49 | 0.99879 | -0.0027194 | 0.17831 | 0.086359
50 | 0.99881 | -0.0025536 | 0 | 0
51 | 0.99886 | -0.0029669 | 0.1851 | 0.089649
52 | 0.9932 | -0.016093 | 0 | 0
53 | 0.99623 | -0.023853 | 0 | 0
54 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.37165 | -0.18 | 0.37166 | 0.17957 | 3.571e-06 | -0.00043343 | 0.012023 | 0.012018 | 0.012023 | 0.99147 | -0.0094127 | 0.99148 | -0.0094962 | 5.4651
1 | -0.37166 | -0.17957 | 0.37175 | 0.17919 | 9.5342e-05 | -0.0003754 | 0.012018 | 0.012012 | 0.012018 | 0.99148 | -0.0094962 | 0.99175 | -0.0077823 | 5.7228
2 | -0.50938 | -0.24574 | 0.5095 | 0.23766 | 0.00012423 | -0.0080788 | 0.016462 | 0.016361 | 0.016462 | 0.99175 | -0.0077823 | 0.99197 | -0.0098102 | 7.4828
3 | 0.13763 | 0.066549 | -0.13763 | -0.066657 | 1.2082e-07 | -0.00010726 | 0.0044498 | 0.0044512 | 0.0044512 | 0.99175 | -0.0077823 | 0.99174 | -0.0077746 | 2.0233
4 | -0.074978 | -0.036313 | 0.07498 | 0.030864 | 1.7716e-06 | -0.0054491 | 0.0024249 | 0.0023601 | 0.0024249 | 0.99175 | -0.0086304 | 0.99178 | -0.0088011 | 1.1022
5 | -0.07498 | -0.030864 | 0.074983 | 0.030477 | 3.2885e-06 | -0.00038778 | 0.0023601 | 0.0023558 | 0.0023601 | 0.99178 | -0.0088011 | 0.99182 | -0.0083332 | 1.1239
6 | -0.16732 | -0.075059 | 0.16737 | 0.043026 | 4.8568e-05 | -0.032033 | 0.0053376 | 0.0050284 | 0.0053376 | 0.99182 | -0.0083332 | 0.9921 | -0.0091644 | 2.4262
7 | 0.092342 | 0.044583 | -0.09234 | -0.044722 | 1.9022e-06 | -0.00013948 | 0.0029845 | 0.0029863 | 0.0029863 | 0.99182 | -0.0083332 | 0.9918 | -0.0084698 | 1.422
8 | 0.75553 | 0.35608 | -0.75545 | -0.35612 | 8.3278e-05 | -4.0809e-05 | 0.024303 | 0.024304 | 0.024304 | 0.9921 | -0.0091644 | 0.99199 | -0.0099655 | 11.5734
9 | -0.9229 | -0.39911 | 0.92396 | 0.37738 | 0.0010613 | -0.021724 | 0.029257 | 0.029009 | 0.029257 | 0.9921 | -0.0091644 | 0.9932 | -0.016093 | 13.2988
10 | -0.5095 | -0.23766 | 0.50951 | 0.23701 | 9.9373e-06 | -0.00065072 | 0.016361 | 0.016353 | 0.016361 | 0.99197 | -0.0098102 | 0.99199 | -0.0099655 | 7.4368
11 | 0.70753 | 0.31849 | -0.70739 | -0.32338 | 0.00013914 | -0.0048923 | 0.022413 | 0.022472 | 0.022472 | 0.99935 | -0.0069226 | 0.99917 | -0.0054552 | 10.2145
12 | -0.77934 | -0.35326 | 0.77936 | 0.35255 | 2.4676e-05 | -0.0007144 | 0.024717 | 0.024708 | 0.024717 | 0.99935 | -0.0069226 | 0.99938 | -0.0071577 | 11.235
13 | 0.21577 | 0.10439 | -0.21576 | -0.1045 | 8.1394e-06 | -0.00010841 | 0.006925 | 0.0069265 | 0.0069265 | 0.99917 | -0.0054552 | 0.99913 | -0.0057044 | 3.2983
14 | 0.49163 | 0.21899 | -0.49147 | -0.23029 | 0.00015495 | -0.011295 | 0.015549 | 0.015686 | 0.015686 | 0.99917 | -0.0054552 | 0.99887 | -0.0030592 | 7.1298
15 | -0.77936 | -0.35255 | 0.77938 | 0.35218 | 1.2695e-05 | -0.00036775 | 0.024708 | 0.024704 | 0.024708 | 0.99938 | -0.0071577 | 0.9994 | -0.0072782 | 11.2311
16 | 0.99862 | 0.47369 | -0.9985 | -0.4737 | 0.00012035 | -3.5112e-06 | 0.031937 | 0.031938 | 0.031938 | 0.99904 | -0.0048151 | 0.99891 | -0.0056718 | 15.2086
17 | -1.0955 | -0.5206 | 1.0955 | 0.52023 | 2.6253e-05 | -0.00037381 | 0.035047 | 0.035042 | 0.035047 | 0.99904 | -0.0048151 | 0.99906 | -0.005015 | 15.9303
18 | 0.75287 | 0.35473 | -0.75286 | -0.35498 | 8.0833e-06 | -0.00024694 | 0.024051 | 0.024054 | 0.024054 | 0.99891 | -0.0056718 | 0.9989 | -0.0055839 | 10.9338
19 | -1.0955 | -0.52023 | 1.0958 | 0.51585 | 0.00030687 | -0.0043783 | 0.035042 | 0.034987 | 0.035042 | 0.99906 | -0.005015 | 0.99932 | -0.0073257 | 15.9281
20 | -0.34424 | -0.1661 | 0.34426 | 0.16358 | 1.7208e-05 | -0.0025221 | 0.011043 | 0.011011 | 0.011043 | 0.99921 | -0.008012 | 0.99925 | -0.0084366 | 5.0193
21 | 0.34424 | 0.1661 | -0.34424 | -0.16672 | 4.2287e-06 | -0.00061756 | 0.011043 | 0.01105 | 0.01105 | 0.99921 | -0.008012 | 0.9992 | -0.0079055 | 5.0229
22 | -0.34426 | -0.16358 | 0.34429 | 0.16341 | 3.5922e-05 | -0.00017579 | 0.011011 | 0.011009 | 0.011011 | 0.99925 | -0.0084366 | 0.99936 | -0.0076976 | 5.2433
23 | -0.079298 | -0.038406 | 0.0793 | 0.032694 | 2.0707e-06 | -0.0057121 | 0.0025624 | 0.0024945 | 0.0025624 | 0.99261 | -0.017785 | 0.99263 | -0.017974 | 1.1647
24 | -0.0793 | -0.032694 | 0.079305 | 0.01732 | 5.1014e-06 | -0.015374 | 0.0024945 | 0.0023605 | 0.0024945 | 0.99263 | -0.017974 | 0.9927 | -0.018037 | 1.1339
25 | -0.26468 | -0.12819 | 0.26469 | 0.12663 | 6.3898e-06 | -0.001563 | 0.0085226 | 0.008503 | 0.0085226 | 0.99614 | -0.023098 | 0.99616 | -0.023306 | 3.8739
26 | -0.26469 | -0.12663 | 0.26471 | 0.12224 | 1.7802e-05 | -0.004393 | 0.008503 | 0.0084487 | 0.008503 | 0.99616 | -0.023306 | 0.99623 | -0.023853 | 3.865
27 | 0.34743 | 0.1619 | -0.34741 | -0.16464 | 1.9184e-05 | -0.0027338 | 0.011119 | 0.011153 | 0.011153 | 0.99511 | -0.027429 | 0.99506 | -0.02698 | 5.0696
28 | -2.3089 | -0.98617 | 2.3136 | 0.98854 | 0.0047412 | 0.0023754 | 0.072833 | 0.072826 | 0.072833 | 0.99511 | -0.027429 | 0.9973 | -0.007632 | 34.6824
29 | 1.5717 | 0.63547 | -1.5714 | -0.63733 | 0.00026422 | -0.0018553 | 0.049179 | 0.0492 | 0.0492 | 0.99511 | -0.027429 | 0.99495 | -0.026533 | 22.3636
30 | 0.34741 | 0.16464 | -0.34738 | -0.16817 | 2.4969e-05 | -0.003533 | 0.011153 | 0.011197 | 0.011197 | 0.99506 | -0.02698 | 0.99499 | -0.026369 | 5.0897
31 | -2.4952 | -1.0765 | 2.4967 | 1.0773 | 0.001548 | 0.00080275 | 0.078659 | 0.078657 | 0.078659 | 0.9973 | -0.007632 | 0.99797 | -0.0017925 | 37.4567
32 | 1.5714 | 0.63733 | -1.5685 | -0.65748 | 0.0028914 | -0.020154 | 0.0492 | 0.049432 | 0.049432 | 0.99495 | -0.026533 | 0.9932 | -0.016093 | 22.4693
33 | -0.75261 | -0.35511 | 0.75273 | 0.35504 | 0.00012291 | -6.4925e-05 | 0.024058 | 0.024056 | 0.024058 | 0.99855 | -0.0079588 | 0.99873 | -0.0067756 | 11.4561
34 | 0.51027 | 0.23774 | -0.51026 | -0.23846 | 1.0861e-05 | -0.00072767 | 0.016274 | 0.016283 | 0.016283 | 0.99855 | -0.0079588 | 0.99853 | -0.0077886 | 7.4013
35 | -0.75273 | -0.35504 | 0.75286 | 0.35498 | 0.00012366 | -6.5393e-05 | 0.024056 | 0.024054 | 0.024056 | 0.99873 | -0.0067756 | 0.9989 | -0.0055839 | 11.4553
36 | 0.51026 | 0.23846 | -0.50917 | -0.24051 | 0.0010869 | -0.0020462 | 0.016283 | 0.016316 | 0.016316 | 0.99853 | -0.0077886 | 0.99628 | -0.023454 | 7.7697
37 | 0.26472 | 0.12212 | -0.26471 | -0.12224 | 1.3588e-05 | -0.0001181 | 0.0084472 | 0.0084487 | 0.0084487 | 0.99628 | -0.023454 | 0.99623 | -0.023853 | 4.0232
38 | -0.31454 | -0.1307 | 0.31454 | 0.13043 | 1.5263e-06 | -0.00027382 | 0.0099051 | 0.009902 | 0.0099051 | 0.9927 | -0.018027 | 0.9927 | -0.018055 | 4.5023
39 | 0.079305 | 0.016771 | -0.079305 | -0.01732 | 1.7325e-07 | -0.00054876 | 0.0023572 | 0.0023605 | 0.0023605 | 0.9927 | -0.018027 | 0.9927 | -0.018037 | 1.073
40 | -0.31454 | -0.13043 | 0.31457 | 0.12633 | 2.271e-05 | -0.0040945 | 0.009902 | 0.009857 | 0.009902 | 0.9927 | -0.018055 | 0.99277 | -0.018451 | 4.5009
41 | -0.31457 | -0.12633 | 0.3146 | 0.12058 | 3.1545e-05 | -0.0057503 | 0.009857 | 0.0097958 | 0.009857 | 0.99277 | -0.018451 | 0.99287 | -0.018928 | 4.4804
42 | -0.64435 | -0.28029 | 0.64455 | 0.2801 | 0.00019786 | -0.00018934 | 0.02043 | 0.020426 | 0.02043 | 0.99287 | -0.018928 | 0.9932 | -0.016093 | 9.7286
43 | 0.34738 | 0.16817 | -0.34738 | -0.16824 | 5.2547e-07 | -7.4043e-05 | 0.011197 | 0.011198 | 0.011198 | 0.99499 | -0.026369 | 0.99499 | -0.026356 | 5.0902
44 | -0.12803 | -0.06201 | 0.12804 | 0.061595 | 1.0637e-05 | -0.00041446 | 0.0041117 | 0.0041064 | 0.0041117 | 0.99879 | -0.0036139 | 0.99887 | -0.0030592 | 1.9579
45 | 0.1851 | 0.088645 | -0.1851 | -0.089649 | 1.9849e-06 | -0.001004 | 0.0059313 | 0.0059439 | 0.0059439 | 0.99887 | -0.0030592 | 0.99886 | -0.0029669 | 2.7018
46 | 0.17832 | 0.080045 | -0.17831 | -0.08627 | 1.1288e-05 | -0.0062254 | 0.005649 | 0.005725 | 0.005725 | 0.99887 | -0.0030592 | 0.99881 | -0.0025536 | 2.6023
47 | 5.0658 | 2.2604 | -5.0631 | -2.266 | 0.0027582 | -0.0056263 | 0.16014 | 0.16023 | 0.16023 | 1 | 0 | 0.9994 | -0.0072782 | 44.2611
48 | 4.2837 | 1.9138 | -4.2836 | -1.9143 | 0.00013441 | -0.00042146 | 0.13552 | 0.13553 | 0.13553 | 0.9994 | -0.0072782 | 0.99936 | -0.0076976 | 37.4386
49 | 1.0959 | 0.51513 | -1.0958 | -0.51585 | 4.9992e-05 | -0.00071482 | 0.034978 | 0.034987 | 0.034987 | 0.99936 | -0.0076976 | 0.99932 | -0.0073257 | 15.903
50 | 2.5003 | 1.0696 | -2.4998 | -1.0693 | 0.00052755 | 0.00027325 | 0.078555 | 0.078556 | 0.078556 | 0.99936 | -0.0076976 | 0.99914 | -0.0097275 | 37.4075
51 | 2.4998 | 1.0693 | -2.4967 | -1.0773 | 0.003082 | -0.0079806 | 0.078556 | 0.078657 | 0.078657 | 0.99914 | -0.0097275 | 0.99797 | -0.0017925 | 35.7533
52 | -0.17831 | -0.086359 | 0.17831 | 0.08627 | 4.4758e-06 | -8.8457e-05 | 0.0057262 | 0.005725 | 0.0057262 | 0.99879 | -0.0027194 | 0.99881 | -0.0025536 | 2.7268

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 5.0798 | 2.2709

## res_load
| p_mw | q_mvar
0 | 0.37165 | 0.18
1 | 0.074978 | 0.036313
2 | 0.09234 | 0.044722
3 | 0.13763 | 0.066657
4 | 0.24593 | 0.11911
5 | 0.071807 | 0.034778
6 | 0.096852 | 0.046907
7 | 0.24563 | 0.11897
8 | 0.34424 | 0.16672
9 | 0.079298 | 0.038406
10 | 0.26468 | 0.12819
11 | 0.3898 | 0.18879
12 | 0.18155 | 0.087927
13 | 0.24234 | 0.11737
14 | 0.24445 | 0.11839
15 | 0.23524 | 0.11393
16 | 0.32975 | 0.15971
17 | 0.21576 | 0.1045
18 | 0.34738 | 0.16824
19 | 0.12803 | 0.06201
20 | 0.34307 | 0.16616
21 | 0.17831 | 0.086359
22 | 0.1851 | 0.089649

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1