## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_92_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_92_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_92_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_92_0_node_5 | 20 | n |  | TRUE
4 | bus_MV_92_0_node_6 | 20 | n |  | TRUE
5 | bus_MV_92_0_node_15 | 20 | n |  | TRUE
6 | bus_MV_92_0_node_14 | 20 | n |  | TRUE
7 | bus_MV_92_0_node_8 | 20 | n |  | TRUE
8 | bus_MV_92_0_node_138 | 20 | n |  | TRUE
9 | bus_MV_92_0_node_139 | 20 | n |  | TRUE
10 | bus_MV_92_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_92_0_node_9 | 20 | n |  | TRUE
12 | bus_MV_92_0_node_10 | 20 | n |  | TRUE
13 | bus_MV_92_0_node_162 | 20 | n |  | TRUE
14 | bus_MV_92_0_node_17 | 20 | n |  | TRUE
15 | bus_MV_92_0_node_149 | 20 | n |  | TRUE
16 | bus_MV_92_0_node_18 | 20 | n |  | TRUE
17 | bus_MV_92_0_node_19 | 20 | n |  | TRUE
18 | bus_MV_92_0_node_11 | 20 | n |  | TRUE
19 | bus_MV_92_0_node_12 | 20 | n |  | TRUE
20 | bus_MV_92_0_node_16 | 20 | n |  | TRUE
21 | bus_MV_92_0_node_20 | 20 | n |  | TRUE
22 | bus_MV_92_0_node_172 | 20 | n |  | TRUE
23 | bus_MV_92_0_node_164 | 20 | n |  | TRUE
24 | bus_MV_92_0_node_34 | 20 | n |  | TRUE
25 | bus_MV_92_0_node_173 | 20 | n |  | TRUE
26 | bus_MV_92_0_node_174 | 20 | n |  | TRUE
27 | bus_MV_92_0_node_21 | 20 | n |  | TRUE
28 | bus_MV_92_0_node_22 | 20 | n |  | TRUE
29 | bus_MV_92_0_node_23 | 20 | n |  | TRUE
30 | bus_MV_92_0_node_26 | 20 | n |  | TRUE
31 | bus_MV_92_0_node_61 | 20 | n |  | TRUE
32 | bus_MV_92_0_node_101 | 20 | n |  | TRUE
33 | bus_MV_92_0_node_25 | 20 | n |  | TRUE
34 | bus_MV_92_0_node_24 | 20 | n |  | TRUE
35 | bus_MV_92_0_node_103 | 20 | n |  | TRUE
36 | bus_MV_92_0_node_102 | 20 | n |  | TRUE
37 | bus_MV_92_0_node_104 | 20 | n |  | TRUE
38 | bus_MV_92_0_node_27 | 20 | n |  | TRUE
39 | bus_MV_92_0_node_28 | 20 | n |  | TRUE
40 | bus_MV_92_0_node_29 | 20 | n |  | TRUE
41 | bus_MV_92_0_node_31 | 20 | n |  | TRUE
42 | bus_MV_92_0_node_32 | 20 | n |  | TRUE
43 | bus_MV_92_0_node_30 | 20 | n |  | TRUE
44 | bus_MV_92_0_node_33 | 20 | n |  | TRUE
45 | bus_MV_92_0_node_166 | 20 | n |  | TRUE
46 | bus_MV_92_0_node_165 | 20 | n |  | TRUE
47 | bus_MV_92_0_node_169 | 20 | n |  | TRUE
48 | bus_MV_92_0_node_170 | 20 | n |  | TRUE
49 | bus_MV_92_0_node_35 | 20 | n |  | TRUE
50 | bus_MV_92_0_node_36 | 20 | n |  | TRUE
51 | bus_MV_92_0_node_39 | 20 | n |  | TRUE
52 | bus_MV_92_0_node_37 | 20 | n |  | TRUE
53 | bus_MV_92_0_node_49 | 20 | n |  | TRUE
54 | bus_MV_92_0_node_38 | 20 | n |  | TRUE
55 | bus_MV_92_0_node_112 | 20 | n |  | TRUE
56 | bus_MV_92_0_node_143 | 20 | n |  | TRUE
57 | bus_MV_92_0_node_163 | 20 | n |  | TRUE
58 | bus_MV_92_0_node_167 | 20 | n |  | TRUE
59 | bus_MV_92_0_node_111 | 20 | n |  | TRUE
60 | bus_MV_92_0_node_154 | 20 | n |  | TRUE
61 | bus_MV_92_0_node_110 | 20 | n |  | TRUE
62 | bus_MV_92_0_node_113 | 20 | n |  | TRUE
63 | bus_MV_92_0_node_74 | 20 | n |  | TRUE
64 | bus_MV_92_0_node_108 | 20 | n |  | TRUE
65 | bus_MV_92_0_node_72 | 20 | n |  | TRUE
66 | bus_MV_92_0_node_40 | 20 | n |  | TRUE
67 | bus_MV_92_0_node_41 | 20 | n |  | TRUE
68 | bus_MV_92_0_node_42 | 20 | n |  | TRUE
69 | bus_MV_92_0_node_43 | 20 | n |  | TRUE
70 | bus_MV_92_0_node_44 | 20 | n |  | TRUE
71 | bus_MV_92_0_node_70 | 20 | n |  | TRUE
72 | bus_MV_92_0_node_69 | 20 | n |  | TRUE
73 | bus_MV_92_0_node_45 | 20 | n |  | TRUE
74 | bus_MV_92_0_node_160 | 20 | n |  | TRUE
75 | bus_MV_92_0_node_168 | 20 | n |  | TRUE
76 | bus_MV_92_0_node_76 | 20 | n |  | TRUE
77 | bus_MV_92_0_node_148 | 20 | n |  | TRUE
78 | bus_MV_92_0_node_97 | 20 | n |  | TRUE
79 | bus_MV_92_0_node_99 | 20 | n |  | TRUE
80 | bus_MV_92_0_node_152 | 20 | n |  | TRUE
81 | bus_MV_92_0_node_46 | 20 | n |  | TRUE
82 | bus_MV_92_0_node_48 | 20 | n |  | TRUE
83 | bus_MV_92_0_node_50 | 20 | n |  | TRUE
84 | bus_MV_92_0_node_51 | 20 | n |  | TRUE
85 | bus_MV_92_0_node_145 | 20 | n |  | TRUE
86 | bus_MV_92_0_node_53 | 20 | n |  | TRUE
87 | bus_MV_92_0_node_66 | 20 | n |  | TRUE
88 | bus_MV_92_0_node_52 | 20 | n |  | TRUE
89 | bus_MV_92_0_node_59 | 20 | n |  | TRUE
90 | bus_MV_92_0_node_106 | 20 | n |  | TRUE
91 | bus_MV_92_0_node_64 | 20 | n |  | TRUE
92 | bus_MV_92_0_node_67 | 20 | n |  | TRUE
93 | bus_MV_92_0_node_60 | 20 | n |  | TRUE
94 | bus_MV_92_0_node_144 | 20 | n |  | TRUE
95 | bus_MV_92_0_node_81 | 20 | n |  | TRUE
96 | bus_MV_92_0_node_57 | 20 | n |  | TRUE
97 | bus_MV_92_0_node_78 | 20 | n |  | TRUE
98 | bus_MV_92_0_node_77 | 20 | n |  | TRUE
99 | bus_MV_92_0_node_58 | 20 | n |  | TRUE
100 | bus_MV_92_0_node_55 | 20 | n |  | TRUE
101 | bus_MV_92_0_node_107 | 20 | n |  | TRUE
102 | bus_MV_92_0_node_65 | 20 | n |  | TRUE
103 | bus_MV_92_0_node_79 | 20 | n |  | TRUE
104 | bus_MV_92_0_node_80 | 20 | n |  | TRUE
105 | bus_MV_92_0_node_82 | 20 | n |  | TRUE
106 | bus_MV_92_0_node_83 | 20 | n |  | TRUE
107 | bus_MV_92_0_node_159 | 20 | n |  | TRUE
108 | bus_MV_92_0_node_84 | 20 | n |  | TRUE
109 | bus_MV_92_0_node_85 | 20 | n |  | TRUE
110 | bus_MV_92_0_node_86 | 20 | n |  | TRUE
111 | bus_MV_92_0_node_89 | 20 | n |  | TRUE
112 | bus_MV_92_0_node_96 | 20 | n |  | TRUE
113 | bus_MV_92_0_node_88 | 20 | n |  | TRUE
114 | bus_MV_92_0_node_121 | 20 | n |  | TRUE
115 | bus_MV_92_0_node_118 | 20 | n |  | TRUE
116 | bus_MV_92_0_node_68 | 20 | n |  | TRUE
117 | bus_MV_92_0_node_147 | 20 | n |  | TRUE
118 | bus_MV_92_0_node_146 | 20 | n |  | TRUE
119 | bus_MV_92_0_node_71 | 20 | n |  | TRUE
120 | bus_MV_92_0_node_73 | 20 | n |  | TRUE
121 | bus_MV_92_0_node_75 | 20 | n |  | TRUE
122 | bus_MV_92_0_node_153 | 20 | n |  | TRUE
123 | bus_MV_92_0_node_134 | 20 | n |  | TRUE
124 | bus_MV_92_0_node_135 | 20 | n |  | TRUE
125 | bus_MV_92_0_node_120 | 20 | n |  | TRUE
126 | bus_MV_92_0_node_155 | 20 | n |  | TRUE
127 | bus_MV_92_0_node_122 | 20 | n |  | TRUE
128 | bus_MV_92_0_node_114 | 20 | n |  | TRUE
129 | bus_MV_92_0_node_93 | 20 | n |  | TRUE
130 | bus_MV_92_0_node_91 | 20 | n |  | TRUE
131 | bus_MV_92_0_node_92 | 20 | n |  | TRUE
132 | bus_MV_92_0_node_94 | 20 | n |  | TRUE
133 | bus_MV_92_0_node_87 | 20 | n |  | TRUE
134 | bus_MV_92_0_node_100 | 20 | n |  | TRUE
135 | bus_MV_92_0_node_161 | 20 | n |  | TRUE
136 | bus_MV_92_0_node_140 | 20 | n |  | TRUE
137 | bus_MV_92_0_node_141 | 20 | n |  | TRUE
138 | bus_MV_92_0_node_105 | 20 | n |  | TRUE
139 | bus_MV_92_0_node_142 | 20 | n |  | TRUE
140 | bus_MV_92_0_node_158 | 20 | n |  | TRUE
141 | bus_MV_92_0_node_156 | 20 | n |  | TRUE
142 | bus_MV_92_0_node_157 | 20 | n |  | TRUE
143 | bus_MV_92_0_node_175 | 20 | n |  | TRUE
144 | bus_MV_92_0_node_115 | 20 | n |  | TRUE
145 | bus_MV_92_0_node_116 | 20 | n |  | TRUE
146 | bus_MV_92_0_node_117 | 20 | n |  | TRUE
147 | bus_MV_92_0_node_131 | 20 | n |  | TRUE
148 | bus_MV_92_0_node_129 | 20 | n |  | TRUE
149 | bus_MV_92_0_node_123 | 20 | n |  | TRUE
150 | bus_MV_92_0_node_124 | 20 | n |  | TRUE
151 | bus_MV_92_0_node_151 | 20 | n |  | TRUE
152 | bus_MV_92_0_node_128 | 20 | n |  | TRUE
153 | bus_MV_92_0_node_130 | 20 | n |  | TRUE
154 | bus_MV_92_0_node_126 | 20 | n |  | TRUE
155 | bus_MV_92_0_node_125 | 20 | n |  | TRUE
156 | bus_MV_92_0_node_127 | 20 | n |  | TRUE
157 | bus_MV_92_0_node_133 | 20 | n |  | TRUE
158 | bus_MV_92_0_node_132 | 20 | n |  | TRUE
159 | bus_MV_92_0_node_136 | 20 | n |  | TRUE
160 | bus_MV_92_0_node_137 | 20 | n |  | TRUE
161 | bus_MV_92_0_node_150 | 20 | n |  | TRUE
162 | bus_HV_92_0_node_49 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_92_0_load_0 | 0 | 0.37759 | 0.18288 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_92_0_load_1 | 2 | 0.083896 | 0.040633 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_92_0_load_15 | 5 | 0.097006 | 0.046982 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_92_0_load_138 | 8 | 0.096766 | 0.046866 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_92_0_load_139 | 9 | 0.22191 | 0.10748 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_92_0_load_7 | 10 | 0.19056 | 0.092294 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_92_0_load_162 | 13 | 0.13669 | 0.066204 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_92_0_load_17 | 14 | 0.24755 | 0.11989 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_92_0_load_149 | 15 | 0.23353 | 0.1131 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_92_0_load_11 | 18 | 0.20924 | 0.10134 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_92_0_load_16 | 20 | 0.33486 | 0.16218 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_92_0_load_20 | 21 | 0.10761 | 0.052117 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_92_0_load_172 | 22 | 0.112 | 0.054243 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_92_0_load_164 | 23 | 0.059243 | 0.028693 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_92_0_load_174 | 26 | 0.088135 | 0.042685 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_92_0_load_21 | 27 | 0.093543 | 0.045305 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_92_0_load_22 | 28 | 0.12823 | 0.062104 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_92_0_load_23 | 29 | 0.068485 | 0.033169 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_92_0_load_61 | 31 | 0.062557 | 0.030298 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_92_0_load_101 | 32 | 0.21648 | 0.10485 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_92_0_load_24 | 34 | 0.10097 | 0.048903 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_92_0_load_27 | 38 | 0.0814 | 0.039424 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_92_0_load_31 | 41 | 0.13801 | 0.066844 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_92_0_load_30 | 43 | 0.13077 | 0.063333 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_92_0_load_33 | 44 | 0.12277 | 0.059459 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_92_0_load_165 | 46 | 0.13723 | 0.066466 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_92_0_load_170 | 48 | 0.050275 | 0.024349 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_92_0_load_35 | 49 | 0.38735 | 0.1876 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_92_0_load_143 | 56 | 0.07278 | 0.035249 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_92_0_load_163 | 57 | 0.40783 | 0.19752 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_92_0_load_167 | 58 | 0.16715 | 0.080957 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_92_0_load_154 | 60 | 0.26661 | 0.12913 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_92_0_load_110 | 61 | 0.32544 | 0.15762 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_92_0_load_113 | 62 | 0.3894 | 0.18859 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_92_0_load_108 | 64 | 0.099053 | 0.047974 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_92_0_load_40 | 66 | 0.3952 | 0.19141 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_92_0_load_69 | 72 | 0.1384 | 0.067029 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_92_0_load_160 | 74 | 0.33412 | 0.16182 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_92_0_load_168 | 75 | 0.37949 | 0.18379 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_92_0_load_76 | 76 | 0.17318 | 0.083875 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_92_0_load_148 | 77 | 0.071413 | 0.034587 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_92_0_load_97 | 78 | 0.31068 | 0.15047 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_92_0_load_152 | 80 | 0.15738 | 0.076223 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_92_0_load_46 | 81 | 0.40458 | 0.19595 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_92_0_load_145 | 85 | 0.091081 | 0.044112 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_92_0_load_66 | 87 | 0.25391 | 0.12297 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_92_0_load_106 | 90 | 0.27815 | 0.13472 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_92_0_load_64 | 91 | 0.25395 | 0.12299 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_92_0_load_144 | 94 | 0.41976 | 0.2033 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_92_0_load_77 | 98 | 0.25241 | 0.12225 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_92_0_load_55 | 100 | 0.31556 | 0.15283 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_92_0_load_107 | 101 | 0.17169 | 0.083153 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_92_0_load_65 | 102 | 0.2933 | 0.14205 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_92_0_load_79 | 103 | 0.093116 | 0.045098 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_92_0_load_159 | 107 | 0.12576 | 0.060908 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_92_0_load_84 | 108 | 0.24542 | 0.11886 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_92_0_load_96 | 112 | 0.22095 | 0.10701 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_92_0_load_118 | 115 | 0.1512 | 0.073227 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_92_0_load_147 | 117 | 0.12536 | 0.060714 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_92_0_load_146 | 118 | 0.08274 | 0.040073 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_92_0_load_71 | 119 | 0.074162 | 0.035918 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_92_0_load_153 | 122 | 0.24871 | 0.12046 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_92_0_load_134 | 123 | 0.14877 | 0.072053 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_92_0_load_155 | 126 | 0.39873 | 0.19311 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_92_0_load_122 | 127 | 0.19684 | 0.095335 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_92_0_load_114 | 128 | 0.37615 | 0.18218 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_92_0_load_91 | 130 | 0.36424 | 0.17641 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_92_0_load_87 | 133 | 0.21088 | 0.10213 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_92_0_load_100 | 134 | 0.29124 | 0.14105 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_92_0_load_161 | 135 | 0.19806 | 0.095924 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_92_0_load_140 | 136 | 0.072373 | 0.035052 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_92_0_load_105 | 138 | 0.16441 | 0.079629 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_92_0_load_157 | 142 | 0.40968 | 0.19842 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_92_0_load_175 | 143 | 0.10298 | 0.049874 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_92_0_load_115 | 144 | 0.18876 | 0.091421 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_92_0_load_131 | 147 | 0.32935 | 0.15951 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_92_0_load_151 | 151 | 0.39399 | 0.19082 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_92_0_load_125 | 155 | 0.23219 | 0.11246 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_92_0_load_133 | 157 | 0.2293 | 0.11106 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_92_0_load_132 | 158 | 0.16894 | 0.081821 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_92_0_load_137 | 160 | 0.15449 | 0.074821 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_92_0_line_0 |  | 0 | 1 | 0.07365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_92_0_line_1 |  | 0 | 2 | 0.054419 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_92_0_line_2 |  | 1 | 3 | 0.19194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_92_0_line_3 |  | 1 | 4 | 0.078359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_92_0_line_4 |  | 3 | 5 | 0.079083 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_92_0_line_5 |  | 4 | 7 | 0.28839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_92_0_line_6 |  | 4 | 8 | 0.040842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_92_0_line_7 |  | 5 | 6 | 0.066021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_92_0_line_8 |  | 6 | 20 | 0.037707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_92_0_line_9 |  | 6 | 19 | 0.24135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_92_0_line_10 |  | 7 | 10 | 0.20092 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
11 | MV_92_0_line_11 |  | 8 | 9 | 0.15287 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_92_0_line_12 |  | 10 | 11 | 0.042923 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
13 | MV_92_0_line_13 |  | 11 | 12 | 0.12956 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
14 | MV_92_0_line_14 |  | 12 | 13 | 1.2314 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
15 | MV_92_0_line_15 |  | 12 | 14 | 0.1233 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
16 | MV_92_0_line_16 |  | 13 | 15 | 1.1283 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
17 | MV_92_0_line_17 |  | 14 | 16 | 0.061044 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
18 | MV_92_0_line_18 |  | 15 | 161 | 0.082827 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
19 | MV_92_0_line_19 |  | 16 | 17 | 0.76308 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
20 | MV_92_0_line_20 |  | 17 | 23 | 0.34002 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
21 | MV_92_0_line_21 |  | 18 | 19 | 0.022205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_92_0_line_22 |  | 20 | 21 | 0.38303 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_92_0_line_23 |  | 21 | 22 | 1.2768 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_92_0_line_24 |  | 22 | 25 | 0.50701 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_92_0_line_25 |  | 23 | 24 | 0.16159 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
26 | MV_92_0_line_26 |  | 24 | 42 | 0.87566 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
27 | MV_92_0_line_27 |  | 25 | 26 | 0.05839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_92_0_line_28 |  | 27 | 28 | 0.15849 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_92_0_line_29 |  | 28 | 29 | 0.054729 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_92_0_line_30 |  | 29 | 30 | 0.024025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_92_0_line_31 |  | 30 | 31 | 1.1231 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_92_0_line_32 |  | 30 | 32 | 0.83015 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_92_0_line_33 |  | 30 | 33 | 0.77093 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_92_0_line_34 |  | 32 | 35 | 0.00387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_92_0_line_35 |  | 33 | 34 | 0.090098 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_92_0_line_36 |  | 35 | 36 | 0.14864 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_92_0_line_37 |  | 36 | 37 | 0.80441 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
38 | MV_92_0_line_38 |  | 37 | 138 | 0.2077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_92_0_line_39 |  | 37 | 79 | 0.92164 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
40 | MV_92_0_line_40 |  | 38 | 39 | 0.056433 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_92_0_line_41 |  | 39 | 40 | 0.37273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_92_0_line_42 |  | 40 | 41 | 0.02195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_92_0_line_43 |  | 40 | 42 | 0.70047 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_92_0_line_44 |  | 40 | 43 | 0.23402 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
45 | MV_92_0_line_45 |  | 42 | 44 | 0.059753 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_92_0_line_46 |  | 43 | 45 | 1.7078 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
47 | MV_92_0_line_47 |  | 45 | 47 | 1.9396 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
48 | MV_92_0_line_48 |  | 45 | 46 | 0.04849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_92_0_line_49 |  | 47 | 48 | 0.03638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_92_0_line_50 |  | 49 | 50 | 0.051988 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_92_0_line_51 |  | 50 | 51 | 0.18828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_92_0_line_52 |  | 51 | 57 | 0.069425 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_92_0_line_53 |  | 51 | 52 | 0.44148 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_92_0_line_54 |  | 51 | 54 | 0.31232 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
55 | MV_92_0_line_55 |  | 52 | 53 | 0.32822 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
56 | MV_92_0_line_56 |  | 53 | 58 | 0.011719 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
57 | MV_92_0_line_57 |  | 54 | 55 | 0.25522 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
58 | MV_92_0_line_58 |  | 54 | 56 | 0.059633 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_92_0_line_59 |  | 55 | 62 | 0.01798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_92_0_line_60 |  | 55 | 59 | 0.15841 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
61 | MV_92_0_line_61 |  | 58 | 72 | 0.32373 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
62 | MV_92_0_line_62 |  | 59 | 60 | 0.1303 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
63 | MV_92_0_line_63 |  | 59 | 61 | 0.008625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_92_0_line_64 |  | 60 | 139 | 0.062414 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
65 | MV_92_0_line_65 |  | 63 | 64 | 0.041225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_92_0_line_66 |  | 63 | 65 | 1.1394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_92_0_line_67 |  | 65 | 120 | 0.34151 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
68 | MV_92_0_line_68 |  | 65 | 121 | 0.62611 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
69 | MV_92_0_line_69 |  | 65 | 119 | 0.054163 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_92_0_line_70 |  | 66 | 67 | 0.008586 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_92_0_line_71 |  | 67 | 68 | 0.12153 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
72 | MV_92_0_line_72 |  | 67 | 69 | 0.23194 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
73 | MV_92_0_line_73 |  | 67 | 70 | 0.38747 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
74 | MV_92_0_line_74 |  | 68 | 71 | 0.18706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_92_0_line_75 |  | 68 | 72 | 0.070579 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
76 | MV_92_0_line_76 |  | 69 | 73 | 0.53209 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_92_0_line_77 |  | 69 | 74 | 0.037781 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_92_0_line_78 |  | 70 | 75 | 0.049738 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
79 | MV_92_0_line_79 |  | 71 | 77 | 0.058903 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_92_0_line_80 |  | 73 | 76 | 0.006374 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
81 | MV_92_0_line_81 |  | 75 | 78 | 0.80089 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_92_0_line_82 |  | 75 | 79 | 0.037206 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
83 | MV_92_0_line_83 |  | 76 | 80 | 1.0024 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
84 | MV_92_0_line_84 |  | 80 | 121 | 0.027787 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
85 | MV_92_0_line_85 |  | 81 | 82 | 0.003117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_92_0_line_86 |  | 82 | 83 | 0.098776 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_92_0_line_87 |  | 82 | 84 | 0.073497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_92_0_line_88 |  | 83 | 86 | 0.17696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_92_0_line_89 |  | 83 | 87 | 0.000743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_92_0_line_90 |  | 84 | 85 | 0.069136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_92_0_line_91 |  | 86 | 88 | 0.14226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_92_0_line_92 |  | 87 | 92 | 0.043143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_92_0_line_93 |  | 88 | 89 | 0.70457 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
94 | MV_92_0_line_94 |  | 88 | 90 | 0.1041 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
95 | MV_92_0_line_95 |  | 88 | 91 | 0.099797 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_92_0_line_96 |  | 89 | 93 | 0.46915 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
97 | MV_92_0_line_97 |  | 89 | 94 | 0.15175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_92_0_line_98 |  | 89 | 95 | 1.0029 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_92_0_line_99 |  | 89 | 96 | 0.67978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_92_0_line_100 |  | 90 | 101 | 0.2598 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
101 | MV_92_0_line_101 |  | 92 | 116 | 0.014678 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_92_0_line_102 |  | 93 | 97 | 1.3969 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
103 | MV_92_0_line_103 |  | 93 | 98 | 0.024472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_92_0_line_104 |  | 95 | 106 | 1.1224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_92_0_line_105 |  | 95 | 103 | 0.027321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_92_0_line_106 |  | 96 | 99 | 0.076788 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_92_0_line_107 |  | 96 | 100 | 0.01898 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_92_0_line_108 |  | 97 | 114 | 1.3634 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
109 | MV_92_0_line_109 |  | 97 | 115 | 0.10107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_92_0_line_110 |  | 99 | 102 | 0.045609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_92_0_line_111 |  | 101 | 131 | 0.063643 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
112 | MV_92_0_line_112 |  | 103 | 104 | 0.017969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_92_0_line_113 |  | 104 | 105 | 0.37962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_92_0_line_114 |  | 105 | 107 | 0.042356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_92_0_line_115 |  | 106 | 110 | 0.73934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_92_0_line_116 |  | 106 | 129 | 0.625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_92_0_line_117 |  | 106 | 130 | 0.078404 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_92_0_line_118 |  | 108 | 109 | 0.038081 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_92_0_line_119 |  | 109 | 110 | 0.26932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_92_0_line_120 |  | 110 | 133 | 0.30385 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
121 | MV_92_0_line_121 |  | 110 | 134 | 0.050501 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
122 | MV_92_0_line_122 |  | 111 | 112 | 0.049397 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_92_0_line_123 |  | 111 | 113 | 0.26369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_92_0_line_124 |  | 113 | 133 | 0.04789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_92_0_line_125 |  | 114 | 127 | 0.22287 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
126 | MV_92_0_line_126 |  | 114 | 128 | 0.38446 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
127 | MV_92_0_line_127 |  | 114 | 125 | 0.38811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_92_0_line_128 |  | 116 | 117 | 0.018458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_92_0_line_129 |  | 116 | 118 | 0.023277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_92_0_line_130 |  | 120 | 122 | 0.17636 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
131 | MV_92_0_line_131 |  | 120 | 123 | 1.4326 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
132 | MV_92_0_line_132 |  | 123 | 124 | 0.099873 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
133 | MV_92_0_line_133 |  | 124 | 159 | 0.51735 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
134 | MV_92_0_line_134 |  | 125 | 126 | 0.040118 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
135 | MV_92_0_line_135 |  | 127 | 149 | 0.10698 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
136 | MV_92_0_line_136 |  | 128 | 140 | 0.88692 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_92_0_line_137 |  | 129 | 135 | 0.047528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_92_0_line_138 |  | 131 | 132 | 0.27227 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
139 | MV_92_0_line_139 |  | 132 | 136 | 0.022282 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
140 | MV_92_0_line_140 |  | 136 | 137 | 0.044038 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
141 | MV_92_0_line_141 |  | 137 | 139 | 0.055956 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
142 | MV_92_0_line_142 |  | 140 | 143 | 0.007978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_92_0_line_143 |  | 140 | 141 | 0.43921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_92_0_line_144 |  | 141 | 142 | 0.012405 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_92_0_line_145 |  | 144 | 145 | 0.073866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_92_0_line_146 |  | 145 | 146 | 0.21998 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_92_0_line_147 |  | 146 | 147 | 0.003328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_92_0_line_148 |  | 147 | 148 | 0.029353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_92_0_line_149 |  | 148 | 153 | 0.61409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_92_0_line_150 |  | 149 | 150 | 0.10568 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
151 | MV_92_0_line_151 |  | 150 | 151 | 0.013131 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
152 | MV_92_0_line_152 |  | 151 | 152 | 0.14671 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
153 | MV_92_0_line_153 |  | 152 | 153 | 0.70491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_92_0_line_154 |  | 152 | 154 | 0.70867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_92_0_line_155 |  | 153 | 158 | 0.12763 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_92_0_line_156 |  | 154 | 156 | 0.26435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_92_0_line_157 |  | 154 | 155 | 0.23891 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
158 | MV_92_0_line_158 |  | 156 | 157 | 0.015137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_92_0_line_159 |  | 159 | 160 | 0.064428 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
160 | MV_92_0_line_160 |  | 160 | 161 | 1.9964 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_92_0_trafo_49 | 25 MVA 110/20 kV | 162 | 53 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2614506.8209 | 1197115.544
1 | 2614440.3339 | 1197145.7443
2 | 2614559.0624 | 1197100.304
3 | 2614540.8607 | 1197281.0926
4 | 2614389.1091 | 1197090.7919
5 | 2614590.2915 | 1197342.8234
6 | 2614603.416 | 1197404.5884
7 | 2614329.1924 | 1197294.4354
8 | 2614423.7669 | 1197074.3781
9 | 2614403.4925 | 1196922.8601
10 | 2614130.0526 | 1197321.1111
11 | 2614103.2153 | 1197287.997
12 | 2613980.8398 | 1197330.5336
13 | 2613083.1607 | 1196487.6388
14 | 2613901.6425 | 1197425.0336
15 | 2612903.0169 | 1195373.7783
16 | 2613888.8544 | 1197484.7137
17 | 2613523.8057 | 1198122.8669
18 | 2614404.054 | 1197521.6361
19 | 2614424.1598 | 1197512.0904
20 | 2614619.2149 | 1197437.5778
21 | 2614964.2043 | 1197603.9947
22 | 2616131.58 | 1198121.2297
23 | 2613626.741 | 1198446.9289
24 | 2613531.8877 | 1198577.7513
25 | 2615937.1571 | 1198589.484
26 | 2615980.5459 | 1198614.5574
27 | 2612387.0476 | 1198847.3593
28 | 2612233.567 | 1198807.8459
29 | 2612201.0526 | 1198763.8228
30 | 2612191.5023 | 1198742.3808
31 | 2611136.6431 | 1199127.9294
32 | 2612050.6508 | 1197924.2694
33 | 2612360.4928 | 1199171.3342
34 | 2612448.0365 | 1199192.6375
35 | 2612050.7271 | 1197920.4008
36 | 2611903.3488 | 1197901.0634
37 | 2611571.1378 | 1197553.5955
38 | 2613581.0467 | 1199415.4681
39 | 2613636.4014 | 1199409.7571
40 | 2613838.3155 | 1199667.5134
41 | 2613834.6731 | 1199645.8712
42 | 2613639.145 | 1199123.7984
43 | 2613884.9706 | 1199896.8336
44 | 2613625.8313 | 1199065.548
45 | 2614099.8395 | 1201591.0722
46 | 2614123.3782 | 1201633.495
47 | 2612161.6351 | 1201664.4614
48 | 2612155.1854 | 1201628.6623
49 | 2609850.1733 | 1197403.0395
50 | 2609807.529 | 1197432.7746
51 | 2609791.8865 | 1197329.5162
52 | 2610148.0151 | 1197395.2191
53 | 2610193.9291 | 1197720.2147
54 | 2609588.7365 | 1197257.9288
55 | 2609469.1605 | 1197434.0779
56 | 2609607.4264 | 1197310.807
57 | 2609727.5043 | 1197355.4924
58 | 2610205.4175 | 1197717.744
59 | 2609384.5301 | 1197484.5835
60 | 2609261.2874 | 1197442.2923
61 | 2609389.9039 | 1197491.3399
62 | 2609486.7594 | 1197430.1591
63 | 2608407.9238 | 1196032.3011
64 | 2608384.4256 | 1196065.9319
65 | 2609189.0569 | 1195706.9356
66 | 2610347.6222 | 1197297.3846
67 | 2610347.5236 | 1197305.9557
68 | 2610332.8103 | 1197371.91
69 | 2610147.2504 | 1197261.6576
70 | 2610653.8635 | 1197207.5601
71 | 2610446.8104 | 1197465.9015
72 | 2610268.1863 | 1197400.1589
73 | 2610009.1903 | 1196988.7364
74 | 2610115.8365 | 1197282.7604
75 | 2610694.8737 | 1197179.2511
76 | 2610003.605 | 1196985.6365
77 | 2610500.8528 | 1197442.4701
78 | 2610980.394 | 1196430.9888
79 | 2610715.9922 | 1197209.8828
80 | 2609593.622 | 1196070.8821
81 | 2609627.6498 | 1197727.486
82 | 2609626.0395 | 1197724.8153
83 | 2609589.7576 | 1197654.1641
84 | 2609673.1909 | 1197679.9336
85 | 2609706.4097 | 1197619.4147
86 | 2609472.2005 | 1197665.4396
87 | 2609590.2535 | 1197653.6091
88 | 2609450.2687 | 1197756.8873
89 | 2609039.9475 | 1198131.6575
90 | 2609348.6371 | 1197734.3499
91 | 2609459.2815 | 1197856.2768
92 | 2609618.666 | 1197621.0815
93 | 2609132.3302 | 1198504.5854
94 | 2609065.9313 | 1198035.6223
95 | 2608039.2027 | 1198198.0523
96 | 2609382.9142 | 1198154.5167
97 | 2609222.5896 | 1199395.745
98 | 2609108.5209 | 1198498.6461
99 | 2609445.8904 | 1198110.5806
100 | 2609378.0957 | 1198172.8746
101 | 2609088.8946 | 1197739.6662
102 | 2609490.0694 | 1198122.4008
103 | 2608014.7502 | 1198210.2485
104 | 2607998.2316 | 1198217.4304
105 | 2607761.2524 | 1198468.8884
106 | 2608026.9081 | 1197423.7336
107 | 2607734.7265 | 1198501.9609
108 | 2607729.8421 | 1197768.4293
109 | 2607691.7713 | 1197769.3145
110 | 2607576.1365 | 1197643.4898
111 | 2607090.8192 | 1197731.6359
112 | 2607123.9033 | 1197768.3166
113 | 2607239.0977 | 1197569.1475
114 | 2608712.4157 | 1200295.6909
115 | 2609306.7995 | 1199451.0377
116 | 2609627.0468 | 1197633.1458
117 | 2609637.7715 | 1197648.1689
118 | 2609642.7473 | 1197615.9617
119 | 2609140.7439 | 1195731.4195
120 | 2609111.4444 | 1195389.3602
121 | 2609568.625 | 1196058.747
122 | 2608935.1526 | 1195394.3655
123 | 2610404.4788 | 1194772.6842
124 | 2610501.5565 | 1194794.3198
125 | 2608595.3932 | 1200087.5219
126 | 2608615.3117 | 1200052.6983
127 | 2608518.9616 | 1200406.3515
128 | 2609079.6792 | 1200409.3726
129 | 2608213.9615 | 1196994.1454
130 | 2607954.3276 | 1197453.3865
131 | 2609075.669 | 1197677.413
132 | 2609148.706 | 1197569.8216
133 | 2607285.2193 | 1197555.7847
134 | 2607527.0764 | 1197631.5109
135 | 2608168.171 | 1197000.053
136 | 2609142.4364 | 1197549.3324
137 | 2609176.3699 | 1197522.4829
138 | 2611756.0368 | 1197648.9386
139 | 2609223.041 | 1197491.6155
140 | 2609291.3121 | 1201270.6709
141 | 2609396.2107 | 1201253.6024
142 | 2609402.7498 | 1201243.0513
143 | 2609295.7391 | 1201277.3147
144 | 2608219.8328 | 1200955.6316
145 | 2608224.287 | 1200887.6789
146 | 2608178.9744 | 1200687.0535
147 | 2608178.4841 | 1200683.7622
148 | 2608184.1095 | 1200655.4991
149 | 2608419.3576 | 1200438.8178
150 | 2608365.7946 | 1200354.5089
151 | 2608353.7901 | 1200349.1115
152 | 2608207.4139 | 1200339.2606
153 | 2607878.732 | 1200725.841
154 | 2607720.4933 | 1200321.452
155 | 2607496.2496 | 1200403.8688
156 | 2607897.8958 | 1200170.4117
157 | 2607902.5585 | 1200184.8145
158 | 2607796.3692 | 1200823.342
159 | 2610857.6839 | 1194763.0464
160 | 2610920.9433 | 1194751.769
161 | 2612825.2422 | 1195351.0108
162 | 2610193.9291 | 1197720.2147

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98457 | -0.51243 | 0.37759 | 0.18288
1 | 0.98461 | -0.51284 | 0 | 0
2 | 0.98456 | -0.51249 | 0.083896 | 0.040633
3 | 0.98438 | -0.51078 | 0 | 0
4 | 0.98476 | -0.51411 | 0 | 0
5 | 0.98423 | -0.5118 | 0.097006 | 0.046982
6 | 0.98416 | -0.51116 | 0 | 0
7 | 0.9854 | -0.51978 | 0 | 0
8 | 0.98474 | -0.51395 | 0.096766 | 0.046866
9 | 0.98467 | -0.51437 | 0.22191 | 0.10748
10 | 0.98564 | -0.50623 | 0.19056 | 0.092294
11 | 0.98566 | -0.50611 | 0 | 0
12 | 0.98575 | -0.50574 | 0 | 0
13 | 0.98744 | -0.44059 | 0.13669 | 0.066204
14 | 0.9857 | -0.50819 | 0.24755 | 0.11989
15 | 0.98907 | -0.37845 | 0.23353 | 0.1131
16 | 0.98569 | -0.50847 | 0 | 0
17 | 0.98558 | -0.51177 | 0 | 0
18 | 0.98409 | -0.51053 | 0.20924 | 0.10134
19 | 0.9841 | -0.51059 | 0 | 0
20 | 0.98413 | -0.51087 | 0.33486 | 0.16218
21 | 0.9839 | -0.51246 | 0.10761 | 0.052117
22 | 0.9834 | -0.51595 | 0.112 | 0.054243
23 | 0.98548 | -0.51673 | 0.059243 | 0.028693
24 | 0.98543 | -0.51893 | 0 | 0
25 | 0.98331 | -0.51658 | 0 | 0
26 | 0.98331 | -0.51652 | 0.088135 | 0.042685
27 | 0.99684 | -0.087361 | 0.093543 | 0.045305
28 | 0.99686 | -0.087179 | 0.12823 | 0.062104
29 | 0.99689 | -0.087031 | 0.068485 | 0.033169
30 | 0.9969 | -0.087114 | 0 | 0
31 | 0.99676 | -0.088032 | 0.062557 | 0.030298
32 | 0.99761 | -0.081042 | 0.21648 | 0.10485
33 | 0.9968 | -0.086634 | 0 | 0
34 | 0.99678 | -0.086745 | 0.10097 | 0.048903
35 | 0.99762 | -0.081068 | 0 | 0
36 | 0.99781 | -0.079582 | 0 | 0
37 | 0.99798 | -0.078393 | 0 | 0
38 | 0.98519 | -0.52351 | 0.0814 | 0.039424
39 | 0.9852 | -0.52357 | 0 | 0
40 | 0.98524 | -0.5238 | 0 | 0
41 | 0.98523 | -0.52377 | 0.13801 | 0.066844
42 | 0.98532 | -0.52203 | 0 | 0
43 | 0.9852 | -0.52511 | 0.13077 | 0.063333
44 | 0.9853 | -0.52212 | 0.12277 | 0.059459
45 | 0.98504 | -0.53079 | 0 | 0
46 | 0.98503 | -0.53071 | 0.13723 | 0.066466
47 | 0.985 | -0.53255 | 0 | 0
48 | 0.98499 | -0.53252 | 0.050275 | 0.024349
49 | 0.9974 | -0.074835 | 0.38735 | 0.1876
50 | 0.99743 | -0.07459 | 0 | 0
51 | 0.99753 | -0.075439 | 0 | 0
52 | 0.99845 | -0.056562 | 0 | 0
53 | 1 | 0 | -16.8674 | -6.9956
54 | 0.99693 | -0.087777 | 0 | 0
55 | 0.99644 | -0.097747 | 0 | 0
56 | 0.99692 | -0.087727 | 0.07278 | 0.035249
57 | 0.99747 | -0.075783 | 0.40783 | 0.19752
58 | 0.99998 | -0.0003687 | 0.16715 | 0.080957
59 | 0.99615 | -0.10368 | 0 | 0
60 | 0.99564 | -0.12264 | 0.26661 | 0.12913
61 | 0.99615 | -0.10365 | 0.32544 | 0.15762
62 | 0.99643 | -0.097663 | 0.3894 | 0.18859
63 | 0.99531 | -0.15041 | 0 | 0
64 | 0.9953 | -0.15036 | 0.099053 | 0.047974
65 | 0.99544 | -0.15072 | 0 | 0
66 | 0.99868 | -0.045498 | 0.3952 | 0.19141
67 | 0.99868 | -0.045539 | 0 | 0
68 | 0.99885 | -0.041895 | 0 | 0
69 | 0.99846 | -0.050558 | 0 | 0
70 | 0.99849 | -0.046767 | 0 | 0
71 | 0.99883 | -0.041778 | 0 | 0
72 | 0.99895 | -0.039752 | 0.1384 | 0.067029
73 | 0.99797 | -0.061265 | 0 | 0
74 | 0.99844 | -0.050407 | 0.33412 | 0.16182
75 | 0.99847 | -0.046914 | 0.37949 | 0.18379
76 | 0.99797 | -0.061392 | 0.17318 | 0.083875
77 | 0.99883 | -0.04173 | 0.071413 | 0.034587
78 | 0.99799 | -0.049964 | 0.31068 | 0.15047
79 | 0.99845 | -0.048136 | 0 | 0
80 | 0.99602 | -0.13706 | 0.15738 | 0.076223
81 | 0.99271 | -0.19947 | 0.40458 | 0.19595
82 | 0.99271 | -0.19949 | 0 | 0
83 | 0.99277 | -0.20005 | 0 | 0
84 | 0.9927 | -0.19942 | 0 | 0
85 | 0.99269 | -0.19934 | 0.091081 | 0.044112
86 | 0.99299 | -0.20199 | 0 | 0
87 | 0.99277 | -0.20005 | 0.25391 | 0.12297
88 | 0.99316 | -0.20352 | 0 | 0
89 | 0.99223 | -0.22335 | 0 | 0
90 | 0.99353 | -0.18972 | 0.27815 | 0.13472
91 | 0.99311 | -0.20383 | 0.25395 | 0.12299
92 | 0.99276 | -0.19994 | 0 | 0
93 | 0.9919 | -0.2309 | 0 | 0
94 | 0.99215 | -0.22259 | 0.41976 | 0.2033
95 | 0.98887 | -0.25244 | 0 | 0
96 | 0.9917 | -0.21874 | 0 | 0
97 | 0.99096 | -0.2512 | 0 | 0
98 | 0.99189 | -0.23083 | 0.25241 | 0.12225
99 | 0.99166 | -0.21902 | 0 | 0
100 | 0.9917 | -0.21866 | 0.31556 | 0.15283
101 | 0.99449 | -0.15412 | 0.17169 | 0.083153
102 | 0.99164 | -0.21886 | 0.2933 | 0.14205
103 | 0.98886 | -0.25239 | 0.093116 | 0.045098
104 | 0.98886 | -0.25237 | 0 | 0
105 | 0.9888 | -0.25192 | 0 | 0
106 | 0.98668 | -0.23576 | 0 | 0
107 | 0.98879 | -0.25186 | 0.12576 | 0.060908
108 | 0.98565 | -0.22741 | 0.24542 | 0.11886
109 | 0.98567 | -0.22729 | 0 | 0
110 | 0.98576 | -0.22805 | 0 | 0
111 | 0.98541 | -0.22911 | 0 | 0
112 | 0.98539 | -0.22924 | 0.22095 | 0.10701
113 | 0.98549 | -0.22977 | 0 | 0
114 | 0.99007 | -0.26896 | 0 | 0
115 | 0.99094 | -0.25102 | 0.1512 | 0.073227
116 | 0.99275 | -0.19991 | 0 | 0
117 | 0.99275 | -0.19988 | 0.12536 | 0.060714
118 | 0.99275 | -0.19988 | 0.08274 | 0.040073
119 | 0.99544 | -0.15077 | 0.074162 | 0.035918
120 | 0.99517 | -0.15664 | 0 | 0
121 | 0.99597 | -0.13909 | 0 | 0
122 | 0.99508 | -0.15718 | 0.24871 | 0.12046
123 | 0.99274 | -0.24905 | 0.14877 | 0.072053
124 | 0.99267 | -0.25062 | 0 | 0
125 | 0.98987 | -0.26718 | 0 | 0
126 | 0.98984 | -0.26738 | 0.39873 | 0.19311
127 | 0.98988 | -0.27574 | 0.19684 | 0.095335
128 | 0.9894 | -0.27357 | 0.37615 | 0.18218
129 | 0.98652 | -0.23459 | 0 | 0
130 | 0.98662 | -0.23612 | 0.36424 | 0.17641
131 | 0.99474 | -0.14523 | 0 | 0
132 | 0.99519 | -0.13575 | 0 | 0
133 | 0.9855 | -0.22988 | 0.21088 | 0.10213
134 | 0.98573 | -0.22823 | 0.29124 | 0.14105
135 | 0.98651 | -0.23447 | 0.19806 | 0.095924
136 | 0.99523 | -0.13497 | 0.072373 | 0.035052
137 | 0.99531 | -0.13342 | 0 | 0
138 | 0.99793 | -0.078016 | 0.16441 | 0.079629
139 | 0.9954 | -0.13145 | 0 | 0
140 | 0.98852 | -0.28006 | 0 | 0
141 | 0.98829 | -0.27801 | 0 | 0
142 | 0.98828 | -0.27795 | 0.40968 | 0.19842
143 | 0.98852 | -0.28005 | 0.10298 | 0.049874
144 | 0.98854 | -0.2744 | 0.18876 | 0.091421
145 | 0.98856 | -0.27456 | 0 | 0
146 | 0.98861 | -0.27501 | 0 | 0
147 | 0.98861 | -0.27502 | 0.32935 | 0.15951
148 | 0.98863 | -0.27519 | 0 | 0
149 | 0.98982 | -0.27605 | 0 | 0
150 | 0.98977 | -0.27635 | 0 | 0
151 | 0.98976 | -0.27639 | 0.39399 | 0.19082
152 | 0.98965 | -0.28302 | 0 | 0
153 | 0.98904 | -0.27849 | 0 | 0
154 | 0.98924 | -0.27972 | 0 | 0
155 | 0.98913 | -0.28041 | 0.23219 | 0.11246
156 | 0.98916 | -0.27904 | 0 | 0
157 | 0.98915 | -0.27899 | 0.2293 | 0.11106
158 | 0.989 | -0.27876 | 0.16894 | 0.081821
159 | 0.99229 | -0.25868 | 0 | 0
160 | 0.99225 | -0.25967 | 0.15449 | 0.074821
161 | 0.98913 | -0.37722 | 0 | 0
162 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.46149 | -0.22345 | 0.46151 | 0.22175 | 2.2189e-05 | -0.0016981 | 0.015034 | 0.015012 | 0.015034 | 0.98457 | -0.51243 | 0.98461 | -0.51284 | 6.8334
1 | 0.083897 | 0.04057 | -0.083896 | -0.040633 | 7.2409e-07 | -6.2522e-05 | 0.0027324 | 0.0027332 | 0.0027332 | 0.98457 | -0.51243 | 0.98456 | -0.51249 | 1.3015
2 | 0.94949 | 0.44296 | -0.94925 | -0.44733 | 0.00024222 | -0.0043699 | 0.030718 | 0.030773 | 0.030773 | 0.98461 | -0.51284 | 0.98438 | -0.51078 | 13.9879
3 | -1.411 | -0.66471 | 1.4112 | 0.66296 | 0.00021865 | -0.0017492 | 0.045729 | 0.045707 | 0.045729 | 0.98461 | -0.51284 | 0.98476 | -0.51411 | 20.786
4 | 0.94925 | 0.44733 | -0.94912 | -0.44734 | 0.00013344 | -7.8875e-06 | 0.030773 | 0.030775 | 0.030775 | 0.98438 | -0.51078 | 0.98423 | -0.5118 | 14.6545
5 | -1.7299 | -0.81619 | 1.7311 | 0.80987 | 0.0012087 | -0.0063231 | 0.056072 | 0.055989 | 0.056072 | 0.98476 | -0.51411 | 0.9854 | -0.51978 | 25.4874
6 | 0.3187 | 0.15323 | -0.31869 | -0.15417 | 5.8657e-06 | -0.00094389 | 0.010366 | 0.010378 | 0.010378 | 0.98476 | -0.51411 | 0.98474 | -0.51395 | 4.7173
7 | 0.85211 | 0.40036 | -0.85204 | -0.40186 | 6.7252e-05 | -0.0015069 | 0.027613 | 0.027632 | 0.027632 | 0.98423 | -0.5118 | 0.98416 | -0.51116 | 12.5602
8 | 0.64279 | 0.30661 | -0.64277 | -0.30748 | 2.1978e-05 | -0.00086546 | 0.02089 | 0.020901 | 0.020901 | 0.98416 | -0.51116 | 0.98413 | -0.51087 | 9.5003
9 | 0.20925 | 0.095248 | -0.20924 | -0.10082 | 1.4803e-05 | -0.0055767 | 0.0067438 | 0.0068132 | 0.0068132 | 0.98416 | -0.51116 | 0.9841 | -0.51059 | 3.0969
10 | -1.7311 | -0.80987 | 1.7314 | 0.8102 | 0.00022484 | 0.00033486 | 0.055989 | 0.055986 | 0.055989 | 0.9854 | -0.51978 | 0.98564 | -0.50623 | 8.6805
11 | 0.22192 | 0.10731 | -0.22191 | -0.10748 | 1.4227e-05 | -0.00016804 | 0.0072263 | 0.0072285 | 0.0072285 | 0.98474 | -0.51395 | 0.98467 | -0.51437 | 3.4422
12 | -1.9219 | -0.9025 | 1.922 | 0.8999 | 5.1264e-05 | -0.0025912 | 0.062187 | 0.062154 | 0.062187 | 0.98564 | -0.50623 | 0.98566 | -0.50611 | 9.7471
13 | -1.922 | -0.8999 | 1.9221 | 0.89208 | 0.00015441 | -0.0078225 | 0.062154 | 0.062056 | 0.062154 | 0.98566 | -0.50611 | 0.98575 | -0.50574 | 9.742
14 | -2.8897 | -1.159 | 2.8934 | 1.1612 | 0.0036471 | 0.0021776 | 0.091178 | 0.091144 | 0.091178 | 0.98575 | -0.50574 | 0.98744 | -0.44059 | 11.1193
15 | 0.96759 | 0.26695 | -0.96755 | -0.2672 | 3.7971e-05 | -0.00025515 | 0.029394 | 0.029397 | 0.029397 | 0.98575 | -0.50574 | 0.9857 | -0.50819 | 3.585
16 | -3.03 | -1.2274 | 3.0337 | 1.2299 | 0.0036721 | 0.0024638 | 0.095574 | 0.095543 | 0.095574 | 0.98744 | -0.44059 | 0.98907 | -0.37845 | 11.6554
17 | 0.72 | 0.14731 | -0.71999 | -0.15183 | 5.1813e-06 | -0.0045267 | 0.021523 | 0.02155 | 0.02155 | 0.9857 | -0.50819 | 0.98569 | -0.50847 | 2.5594
18 | -3.2673 | -1.343 | 3.2674 | 1.3369 | 0.00016101 | -0.0060433 | 0.1031 | 0.10303 | 0.1031 | 0.98907 | -0.37845 | 0.98913 | -0.37722 | 12.2448
19 | 0.71999 | 0.15183 | -0.71993 | -0.20841 | 6.5977e-05 | -0.056579 | 0.02155 | 0.021952 | 0.021952 | 0.98569 | -0.50847 | 0.98558 | -0.51177 | 2.6072
20 | 0.71993 | 0.20841 | -0.71987 | -0.20918 | 5.8417e-05 | -0.00077033 | 0.021952 | 0.021959 | 0.021959 | 0.98558 | -0.51177 | 0.98548 | -0.51673 | 2.678
21 | -0.20924 | -0.10134 | 0.20924 | 0.10082 | 1.3774e-06 | -0.00051303 | 0.0068198 | 0.0068132 | 0.0068198 | 0.98409 | -0.51053 | 0.9841 | -0.51059 | 3.0999
22 | 0.30791 | 0.1453 | -0.30784 | -0.1457 | 6.8107e-05 | -0.0004001 | 0.0099871 | 0.0099927 | 0.0099927 | 0.98413 | -0.51087 | 0.9839 | -0.51246 | 4.7584
23 | 0.20024 | 0.093585 | -0.20014 | -0.095 | 9.5942e-05 | -0.0014148 | 0.0064849 | 0.0065034 | 0.0065034 | 0.9839 | -0.51246 | 0.9834 | -0.51595 | 3.0968
24 | 0.088143 | 0.040757 | -0.088135 | -0.041338 | 7.3593e-06 | -0.00058068 | 0.0028506 | 0.0028579 | 0.0028579 | 0.9834 | -0.51595 | 0.98331 | -0.51658 | 1.3609
25 | 0.66062 | 0.18049 | -0.6606 | -0.18086 | 2.318e-05 | -0.00037267 | 0.020061 | 0.020064 | 0.020064 | 0.98548 | -0.51673 | 0.98543 | -0.51893 | 2.4468
26 | 0.6606 | 0.18086 | -0.66053 | -0.24576 | 6.627e-05 | -0.0649 | 0.020064 | 0.020648 | 0.020648 | 0.98543 | -0.51893 | 0.98532 | -0.52203 | 2.4523
27 | 0.088135 | 0.041338 | -0.088135 | -0.042685 | 6.4044e-07 | -0.0013478 | 0.0028579 | 0.0028749 | 0.0028749 | 0.98331 | -0.51658 | 0.98331 | -0.51652 | 1.3068
28 | -0.093543 | -0.045305 | 0.093545 | 0.045118 | 2.5562e-06 | -0.00018641 | 0.0030099 | 0.0030075 | 0.0030099 | 0.99684 | -0.087361 | 0.99686 | -0.087179 | 1.4333
29 | -0.22177 | -0.10722 | 0.22178 | 0.10716 | 4.9613e-06 | -6.182e-05 | 0.0071334 | 0.0071326 | 0.0071334 | 0.99686 | -0.087179 | 0.99689 | -0.087031 | 3.3969
30 | -0.29026 | -0.14033 | 0.29027 | 0.13976 | 2.7934e-06 | -0.00056923 | 0.0093361 | 0.0093289 | 0.0093361 | 0.99689 | -0.087031 | 0.9969 | -0.087114 | 4.2437
31 | 0.062565 | 0.028971 | -0.062557 | -0.030298 | 8.0419e-06 | -0.0013272 | 0.0019965 | 0.002013 | 0.002013 | 0.9969 | -0.087114 | 0.99676 | -0.088032 | 0.95859
32 | -0.45382 | -0.19924 | 0.45412 | 0.19845 | 0.00030442 | -0.00079492 | 0.014352 | 0.014341 | 0.014352 | 0.9969 | -0.087114 | 0.99761 | -0.081042 | 6.8343
33 | 0.10098 | 0.030509 | -0.10097 | -0.048797 | 1.0158e-05 | -0.018288 | 0.0030548 | 0.0032478 | 0.0032478 | 0.9969 | -0.087114 | 0.9968 | -0.086634 | 1.4763
34 | -0.6706 | -0.30329 | 0.67061 | 0.3032 | 2.3433e-06 | -9.1265e-05 | 0.021297 | 0.021296 | 0.021297 | 0.99761 | -0.081042 | 0.99762 | -0.081068 | 9.6806
35 | 0.10097 | 0.048797 | -0.10097 | -0.048903 | 1.694e-06 | -0.00010581 | 0.0032478 | 0.0032491 | 0.0032491 | 0.9968 | -0.086634 | 0.99678 | -0.086745 | 1.5472
36 | -0.67061 | -0.3032 | 0.67073 | 0.3031 | 0.0001201 | -0.00010141 | 0.021296 | 0.021294 | 0.021296 | 0.99762 | -0.081068 | 0.99781 | -0.079582 | 10.1411
37 | -0.67073 | -0.3031 | 0.67084 | 0.25283 | 0.00010967 | -0.050268 | 0.021294 | 0.020737 | 0.021294 | 0.99781 | -0.079582 | 0.99798 | -0.078393 | 3.3376
38 | 0.16442 | 0.074692 | -0.16441 | -0.079629 | 7.6533e-06 | -0.0049365 | 0.0052238 | 0.0052845 | 0.0052845 | 0.99798 | -0.078393 | 0.99793 | -0.078016 | 2.402
39 | -0.83526 | -0.32752 | 0.83548 | 0.32685 | 0.00022148 | -0.00067385 | 0.025952 | 0.025938 | 0.025952 | 0.99798 | -0.078393 | 0.99845 | -0.048136 | 4.0235
40 | -0.0814 | -0.039424 | 0.0814 | 0.038116 | 5.2581e-07 | -0.0013076 | 0.0026501 | 0.0026337 | 0.0026501 | 0.98519 | -0.52351 | 0.9852 | -0.52357 | 1.2046
41 | -0.0814 | -0.038116 | 0.081404 | 0.029479 | 3.3187e-06 | -0.0086372 | 0.0026337 | 0.0025367 | 0.0026337 | 0.9852 | -0.52357 | 0.98524 | -0.5238 | 1.1971
42 | 0.13802 | 0.066335 | -0.13801 | -0.066844 | 5.9074e-07 | -0.00050854 | 0.0044867 | 0.0044932 | 0.0044932 | 0.98524 | -0.5238 | 0.98523 | -0.52377 | 2.0424
43 | -0.53773 | -0.23829 | 0.53777 | 0.18637 | 3.6781e-05 | -0.051921 | 0.017233 | 0.016675 | 0.017233 | 0.98524 | -0.5238 | 0.98532 | -0.52203 | 2.0467
44 | 0.31831 | 0.14248 | -0.3183 | -0.14305 | 8.7143e-06 | -0.0005754 | 0.010218 | 0.010225 | 0.010225 | 0.98524 | -0.5238 | 0.9852 | -0.52511 | 1.247
45 | 0.12277 | 0.059391 | -0.12277 | -0.059459 | 1.7e-06 | -6.8188e-05 | 0.0039956 | 0.0039965 | 0.0039965 | 0.98532 | -0.52203 | 0.9853 | -0.52212 | 1.9031
46 | 0.18754 | 0.079722 | -0.18751 | -0.083981 | 2.1881e-05 | -0.0042587 | 0.0059709 | 0.0060212 | 0.0060212 | 0.9852 | -0.52511 | 0.98504 | -0.53079 | 0.73429
47 | 0.050277 | 0.018638 | -0.050275 | -0.023507 | 1.7644e-06 | -0.0048691 | 0.0015714 | 0.0016265 | 0.0016265 | 0.98504 | -0.53079 | 0.985 | -0.53255 | 0.19836
48 | 0.13724 | 0.065343 | -0.13723 | -0.066466 | 1.2886e-06 | -0.001123 | 0.0044544 | 0.0044687 | 0.0044687 | 0.98504 | -0.53079 | 0.98503 | -0.53071 | 2.0312
49 | 0.050275 | 0.023507 | -0.050275 | -0.024349 | 1.2932e-07 | -0.0008427 | 0.0016265 | 0.0016371 | 0.0016371 | 0.985 | -0.53255 | 0.98499 | -0.53252 | 0.74416
50 | -0.38735 | -0.1876 | 0.38736 | 0.18755 | 1.4372e-05 | -5.2741e-05 | 0.012457 | 0.012456 | 0.012457 | 0.9974 | -0.074835 | 0.99743 | -0.07459 | 5.9317
51 | -0.38736 | -0.18755 | 0.3874 | 0.18309 | 3.8822e-05 | -0.0044613 | 0.012456 | 0.0124 | 0.012456 | 0.99743 | -0.07459 | 0.99753 | -0.075439 | 5.6617
52 | 0.40786 | 0.19745 | -0.40783 | -0.19752 | 2.1272e-05 | -6.9142e-05 | 0.013113 | 0.013114 | 0.013114 | 0.99753 | -0.075439 | 0.99747 | -0.075783 | 6.245
53 | -9.8452 | -4.1809 | 9.8529 | 4.1544 | 0.0077314 | -0.026498 | 0.30954 | 0.30916 | 0.30954 | 0.99753 | -0.075439 | 0.99845 | -0.056562 | 36.7621
54 | 9.0499 | 3.8004 | -9.0453 | -3.8199 | 0.0046159 | -0.019493 | 0.28405 | 0.28432 | 0.28432 | 0.99753 | -0.075439 | 0.99693 | -0.087777 | 33.767
55 | -9.8529 | -4.1544 | 9.8641 | 4.1698 | 0.01118 | 0.015339 | 0.30916 | 0.30915 | 0.30916 | 0.99845 | -0.056562 | 1 | 0 | 37.7022
56 | 6.9893 | 2.8153 | -6.9892 | -2.8161 | 0.00010147 | -0.0008022 | 0.21752 | 0.21753 | 0.21753 | 1 | 0 | 0.99998 | -0.0003687 | 25.8346
57 | 8.9725 | 3.7861 | -8.9688 | -3.802 | 0.003717 | -0.015959 | 0.282 | 0.28221 | 0.28221 | 0.99693 | -0.087777 | 0.99644 | -0.097747 | 33.5172
58 | 0.07278 | 0.033834 | -0.07278 | -0.035249 | 4.3321e-07 | -0.0014149 | 0.002324 | 0.0023416 | 0.0023416 | 0.99693 | -0.087777 | 0.99692 | -0.087727 | 1.0644
59 | 0.3894 | 0.18817 | -0.3894 | -0.18859 | 3.7697e-06 | -0.00042512 | 0.012529 | 0.012535 | 0.012535 | 0.99644 | -0.097747 | 0.99643 | -0.097663 | 5.6975
60 | 8.5794 | 3.6138 | -8.5773 | -3.6239 | 0.0021097 | -0.010077 | 0.2697 | 0.26984 | 0.26984 | 0.99644 | -0.097747 | 0.99615 | -0.10368 | 32.0471
61 | 6.8221 | 2.7352 | -6.8169 | -2.7285 | 0.0051945 | 0.0066835 | 0.21218 | 0.21219 | 0.21219 | 0.99998 | -0.0003687 | 0.99895 | -0.039752 | 25.8766
62 | 8.2519 | 3.4665 | -8.2487 | -3.4623 | 0.0031241 | 0.0041886 | 0.25937 | 0.25938 | 0.25938 | 0.99615 | -0.10368 | 0.99564 | -0.12264 | 31.6315
63 | 0.32544 | 0.15742 | -0.32544 | -0.15762 | 1.2641e-06 | -0.00020397 | 0.010476 | 0.010479 | 0.010479 | 0.99615 | -0.10368 | 0.99615 | -0.10365 | 4.7632
64 | 7.9821 | 3.3332 | -7.9807 | -3.3313 | 0.0013992 | 0.0018657 | 0.2508 | 0.2508 | 0.2508 | 0.99564 | -0.12264 | 0.9954 | -0.13145 | 30.5858
65 | 0.099054 | 0.046999 | -0.099053 | -0.047974 | 5.5864e-07 | -0.0009749 | 0.0031799 | 0.0031921 | 0.0031921 | 0.99531 | -0.15041 | 0.9953 | -0.15036 | 1.451
66 | -0.099054 | -0.046999 | 0.099068 | 0.02005 | 1.3993e-05 | -0.026949 | 0.0031799 | 0.0029312 | 0.0031799 | 0.99531 | -0.15041 | 0.99544 | -0.15072 | 1.4454
67 | 3.8357 | 1.5406 | -3.8348 | -1.5656 | 0.00090012 | -0.025022 | 0.11987 | 0.12015 | 0.12015 | 0.99544 | -0.15072 | 0.99517 | -0.15664 | 14.2699
68 | -4.009 | -1.5965 | 4.0107 | 1.5507 | 0.001787 | -0.045787 | 0.12514 | 0.12464 | 0.12514 | 0.99544 | -0.15072 | 0.99597 | -0.13909 | 14.8619
69 | 0.074162 | 0.035854 | -0.074162 | -0.035918 | 5.5088e-07 | -6.3726e-05 | 0.0023888 | 0.0023896 | 0.0023896 | 0.99544 | -0.15072 | 0.99544 | -0.15077 | 1.1379
70 | -0.3952 | -0.19141 | 0.39521 | 0.1912 | 1.8463e-06 | -0.00020391 | 0.012693 | 0.01269 | 0.012693 | 0.99868 | -0.045498 | 0.99868 | -0.045539 | 5.7695
71 | -6.6056 | -2.646 | 6.6065 | 2.6376 | 0.00094043 | -0.0083988 | 0.20569 | 0.20559 | 0.20569 | 0.99868 | -0.045539 | 0.99885 | -0.041895 | 24.4285
72 | 4.6843 | 1.8218 | -4.6834 | -1.8386 | 0.000897 | -0.016846 | 0.14528 | 0.14547 | 0.14547 | 0.99868 | -0.045539 | 0.99846 | -0.050558 | 17.2764
73 | 1.5261 | 0.633 | -1.5258 | -0.65712 | 0.00027462 | -0.024122 | 0.047757 | 0.04803 | 0.04803 | 0.99868 | -0.045539 | 0.99849 | -0.046767 | 7.5283
74 | 0.071415 | 0.028728 | -0.071414 | -0.033184 | 1.2637e-06 | -0.0044556 | 0.0022247 | 0.0022759 | 0.0022759 | 0.99885 | -0.041895 | 0.99883 | -0.041778 | 1.0345
75 | -6.6779 | -2.6663 | 6.6785 | 2.6614 | 0.00055764 | -0.0048687 | 0.20781 | 0.20776 | 0.20781 | 0.99885 | -0.041895 | 0.99895 | -0.039752 | 24.6809
76 | 4.3493 | 1.6777 | -4.3475 | -1.7166 | 0.0017743 | -0.03888 | 0.13478 | 0.1352 | 0.1352 | 0.99846 | -0.050558 | 0.99797 | -0.061265 | 16.0574
77 | 0.33412 | 0.16092 | -0.33412 | -0.16182 | 5.8047e-06 | -0.00089754 | 0.010722 | 0.010734 | 0.010734 | 0.99846 | -0.050558 | 0.99844 | -0.050407 | 4.8789
78 | 1.5258 | 0.65712 | -1.5258 | -0.66022 | 3.5481e-05 | -0.0030957 | 0.04803 | 0.048066 | 0.048066 | 0.99849 | -0.046767 | 0.99847 | -0.046914 | 7.5339
79 | 0.071414 | 0.033184 | -0.071413 | -0.034587 | 4.104e-07 | -0.001403 | 0.0022759 | 0.0022933 | 0.0022933 | 0.99883 | -0.041778 | 0.99883 | -0.04173 | 1.0424
80 | 4.3475 | 1.7166 | -4.3475 | -1.7171 | 2.1323e-05 | -0.00046545 | 0.1352 | 0.13521 | 0.13521 | 0.99797 | -0.061265 | 0.99797 | -0.061392 | 16.058
81 | 0.31082 | 0.1496 | -0.31068 | -0.15047 | 0.0001421 | -0.00086371 | 0.0099731 | 0.0099851 | 0.0099851 | 0.99847 | -0.046914 | 0.99799 | -0.049964 | 4.7548
82 | 0.83549 | 0.32682 | -0.83548 | -0.32685 | 8.9363e-06 | -2.7241e-05 | 0.025938 | 0.025938 | 0.025938 | 0.99847 | -0.046914 | 0.99845 | -0.048136 | 4.0215
83 | 4.1743 | 1.6332 | -4.1683 | -1.6271 | 0.0060074 | 0.0061182 | 0.12966 | 0.12969 | 0.12969 | 0.99797 | -0.061392 | 0.99602 | -0.13706 | 15.8154
84 | 4.0109 | 1.5508 | -4.0107 | -1.5507 | 0.00015384 | 0.00015137 | 0.12463 | 0.12464 | 0.12464 | 0.99602 | -0.13706 | 0.99597 | -0.13909 | 15.1994
85 | -0.40458 | -0.19595 | 0.40458 | 0.19587 | 7.1098e-07 | -7.3129e-05 | 0.013072 | 0.013071 | 0.013072 | 0.99271 | -0.19947 | 0.99271 | -0.19949 | 5.9419
86 | -0.49566 | -0.23663 | 0.4957 | 0.23432 | 3.3578e-05 | -0.0023143 | 0.015972 | 0.015943 | 0.015972 | 0.99271 | -0.19949 | 0.99277 | -0.20005 | 7.26
87 | 0.091082 | 0.040757 | -0.091081 | -0.042486 | 8.3206e-07 | -0.0017291 | 0.0029017 | 0.0029226 | 0.0029226 | 0.99271 | -0.19949 | 0.9927 | -0.19942 | 1.3285
88 | -0.95771 | -0.45572 | 0.95793 | 0.45162 | 0.00022431 | -0.0040986 | 0.03084 | 0.030788 | 0.03084 | 0.99277 | -0.20005 | 0.99299 | -0.20199 | 14.0182
89 | 0.46201 | 0.2214 | -0.46201 | -0.22142 | 2.2011e-07 | -1.7419e-05 | 0.014897 | 0.014897 | 0.014897 | 0.99277 | -0.20005 | 0.99277 | -0.20005 | 6.7715
90 | 0.091081 | 0.042486 | -0.091081 | -0.044112 | 7.9382e-07 | -0.0016264 | 0.0029226 | 0.0029429 | 0.0029429 | 0.9927 | -0.19942 | 0.99269 | -0.19934 | 1.3377
91 | -0.95793 | -0.45162 | 0.95811 | 0.44832 | 0.00017979 | -0.0032965 | 0.030788 | 0.030747 | 0.030788 | 0.99299 | -0.20199 | 0.99316 | -0.20352 | 13.9946
92 | 0.2081 | 0.098446 | -0.2081 | -0.09946 | 2.5858e-06 | -0.0010145 | 0.0066941 | 0.0067068 | 0.0067068 | 0.99277 | -0.20005 | 0.99276 | -0.19994 | 3.0485
93 | 6.233 | 2.5211 | -6.2281 | -2.5696 | 0.0049392 | -0.048514 | 0.19543 | 0.19601 | 0.19601 | 0.99316 | -0.20352 | 0.99223 | -0.22335 | 23.2796
94 | -7.4451 | -3.0923 | 7.4472 | 3.095 | 0.0020372 | 0.0026835 | 0.23433 | 0.23432 | 0.23433 | 0.99316 | -0.20352 | 0.99353 | -0.18972 | 28.5763
95 | 0.25396 | 0.12288 | -0.25395 | -0.12299 | 1.1959e-05 | -0.00011002 | 0.0082004 | 0.0082019 | 0.0082019 | 0.99316 | -0.20352 | 0.99311 | -0.20383 | 3.9056
96 | 3.439 | 1.3252 | -3.438 | -1.3596 | 0.00099049 | -0.034369 | 0.10722 | 0.1076 | 0.1076 | 0.99223 | -0.22335 | 0.9919 | -0.2309 | 12.7788
97 | 0.4198 | 0.19974 | -0.41976 | -0.2033 | 3.7184e-05 | -0.0035559 | 0.013525 | 0.01357 | 0.01357 | 0.99223 | -0.22335 | 0.99215 | -0.22259 | 6.1683
98 | 1.7601 | 0.76726 | -1.7545 | -0.76495 | 0.0055773 | 0.0023186 | 0.05586 | 0.055874 | 0.055874 | 0.99223 | -0.22335 | 0.98887 | -0.25244 | 26.6065
99 | 0.60923 | 0.27742 | -0.60888 | -0.29329 | 0.00034768 | -0.015868 | 0.019476 | 0.019673 | 0.019673 | 0.99223 | -0.22335 | 0.9917 | -0.21874 | 8.9423
100 | -7.7253 | -3.2297 | 7.7308 | 3.237 | 0.0054803 | 0.0072699 | 0.24329 | 0.24328 | 0.24329 | 0.99353 | -0.18972 | 0.99449 | -0.15412 | 29.6694
101 | 0.2081 | 0.09946 | -0.2081 | -0.099805 | 8.8198e-07 | -0.00034513 | 0.0067068 | 0.0067111 | 0.0067111 | 0.99276 | -0.19994 | 0.99275 | -0.19991 | 3.0505
102 | 3.1856 | 1.2379 | -3.1831 | -1.3405 | 0.0025578 | -0.10256 | 0.099466 | 0.10061 | 0.10061 | 0.9919 | -0.2309 | 0.99096 | -0.2512 | 11.9492
103 | 0.25241 | 0.12167 | -0.25241 | -0.12225 | 2.1747e-06 | -0.00057421 | 0.0081551 | 0.0081623 | 0.0081623 | 0.9919 | -0.2309 | 0.99189 | -0.23083 | 3.7102
104 | 1.5356 | 0.66985 | -1.532 | -0.69492 | 0.0036065 | -0.025076 | 0.048907 | 0.049217 | 0.049217 | 0.98887 | -0.25244 | 0.98668 | -0.23576 | 22.3716
105 | 0.21889 | 0.095101 | -0.21888 | -0.095738 | 1.7722e-06 | -0.00063735 | 0.0069669 | 0.0069743 | 0.0069743 | 0.98887 | -0.25244 | 0.98886 | -0.25239 | 3.1701
106 | 0.29332 | 0.1409 | -0.29331 | -0.14098 | 1.2277e-05 | -8.2461e-05 | 0.0094723 | 0.0094734 | 0.0094734 | 0.9917 | -0.21874 | 0.99166 | -0.21902 | 4.5112
107 | 0.31556 | 0.15239 | -0.31556 | -0.15283 | 2.638e-06 | -0.00044489 | 0.010201 | 0.010206 | 0.010206 | 0.9917 | -0.21874 | 0.9917 | -0.21866 | 4.6392
108 | 3.0319 | 1.2696 | -3.0295 | -1.3697 | 0.0023156 | -0.10008 | 0.095752 | 0.096941 | 0.096941 | 0.99096 | -0.2512 | 0.99007 | -0.26896 | 11.5132
109 | 0.1512 | 0.070859 | -0.1512 | -0.073227 | 3.2119e-06 | -0.0023687 | 0.0048642 | 0.0048939 | 0.0048939 | 0.99096 | -0.2512 | 0.99094 | -0.25102 | 2.2245
110 | 0.29331 | 0.14098 | -0.2933 | -0.14205 | 5.4723e-06 | -0.0010692 | 0.0094734 | 0.009487 | 0.009487 | 0.99166 | -0.21902 | 0.99164 | -0.21886 | 4.3123
111 | -7.9025 | -3.3201 | 7.9039 | 3.322 | 0.0014042 | 0.00187 | 0.24881 | 0.24881 | 0.24881 | 0.99449 | -0.15412 | 0.99474 | -0.14523 | 30.3428
112 | 0.12577 | 0.05064 | -0.12577 | -0.051059 | 3.7623e-07 | -0.00041941 | 0.003958 | 0.0039626 | 0.0039626 | 0.98886 | -0.25239 | 0.98886 | -0.25237 | 1.8012
113 | 0.12577 | 0.051059 | -0.12576 | -0.05992 | 8.1617e-06 | -0.0088602 | 0.0039626 | 0.004067 | 0.004067 | 0.98886 | -0.25237 | 0.9888 | -0.25192 | 1.8486
114 | 0.12576 | 0.05992 | -0.12576 | -0.060908 | 9.3814e-07 | -0.00098848 | 0.004067 | 0.0040795 | 0.0040795 | 0.9888 | -0.25192 | 0.98879 | -0.25186 | 1.8543
115 | 0.96962 | 0.43828 | -0.96866 | -0.45517 | 0.00096306 | -0.016884 | 0.031132 | 0.031343 | 0.031343 | 0.98668 | -0.23576 | 0.98576 | -0.22805 | 14.2466
116 | 0.19809 | 0.080305 | -0.19806 | -0.09482 | 3.3504e-05 | -0.014515 | 0.0062538 | 0.0064256 | 0.0064256 | 0.98668 | -0.23576 | 0.98652 | -0.23459 | 2.9207
117 | 0.36426 | 0.17633 | -0.36424 | -0.17641 | 1.9586e-05 | -7.8848e-05 | 0.01184 | 0.011842 | 0.011842 | 0.98668 | -0.23576 | 0.98662 | -0.23612 | 5.6388
118 | -0.24542 | -0.11886 | 0.24543 | 0.11882 | 4.3275e-06 | -4.1457e-05 | 0.0079866 | 0.007986 | 0.0079866 | 0.98565 | -0.22741 | 0.98567 | -0.22729 | 3.8031
119 | -0.24543 | -0.11882 | 0.24545 | 0.11258 | 2.2705e-05 | -0.0062412 | 0.007986 | 0.007908 | 0.007986 | 0.98567 | -0.22729 | 0.98576 | -0.22805 | 3.63
120 | 0.43196 | 0.20159 | -0.43185 | -0.20187 | 0.00010553 | -0.00028629 | 0.013959 | 0.013964 | 0.013964 | 0.98576 | -0.22805 | 0.9855 | -0.22988 | 6.6494
121 | 0.29125 | 0.141 | -0.29124 | -0.14105 | 8.0803e-06 | -5.3521e-05 | 0.0094761 | 0.0094768 | 0.0094768 | 0.98576 | -0.22805 | 0.98573 | -0.22823 | 4.5128
122 | 0.22096 | 0.10696 | -0.22095 | -0.10701 | 4.552e-06 | -5.441e-05 | 0.0071914 | 0.0071921 | 0.0071921 | 0.98541 | -0.22911 | 0.98539 | -0.22924 | 3.4248
123 | -0.22096 | -0.10696 | 0.22097 | 0.10085 | 1.8011e-05 | -0.0061088 | 0.0071914 | 0.0071152 | 0.0071914 | 0.98541 | -0.22911 | 0.98549 | -0.22977 | 3.2688
124 | -0.22097 | -0.10085 | 0.22098 | 0.099739 | 3.2305e-06 | -0.0011095 | 0.0071152 | 0.0071017 | 0.0071152 | 0.98549 | -0.22977 | 0.9855 | -0.22988 | 3.2342
125 | 1.7408 | 0.76673 | -1.7406 | -0.76694 | 0.00024436 | -0.00021163 | 0.055462 | 0.055469 | 0.055469 | 0.99007 | -0.26896 | 0.98988 | -0.27574 | 6.7645
126 | 0.8899 | 0.41892 | -0.88934 | -0.41901 | 0.00056347 | -9.6652e-05 | 0.028678 | 0.028684 | 0.028684 | 0.99007 | -0.26896 | 0.9894 | -0.27357 | 13.659
127 | 0.39883 | 0.18402 | -0.39874 | -0.19307 | 8.5725e-05 | -0.0090561 | 0.012807 | 0.01292 | 0.01292 | 0.99007 | -0.26896 | 0.98987 | -0.26718 | 5.8727
128 | 0.12536 | 0.06028 | -0.12536 | -0.060714 | 4.0369e-07 | -0.00043423 | 0.0040448 | 0.0040503 | 0.0040503 | 0.99275 | -0.19991 | 0.99275 | -0.19988 | 1.841
129 | 0.08274 | 0.039525 | -0.08274 | -0.040073 | 2.2149e-07 | -0.00054766 | 0.0026664 | 0.0026733 | 0.0026733 | 0.99275 | -0.19991 | 0.99275 | -0.19988 | 1.2151
130 | 0.24873 | 0.12026 | -0.24871 | -0.12046 | 2.0188e-05 | -0.00019585 | 0.0080142 | 0.0080168 | 0.0080168 | 0.99517 | -0.15664 | 0.99508 | -0.15718 | 3.8175
131 | 3.5861 | 1.4453 | -3.5797 | -1.4397 | 0.0064246 | 0.0056378 | 0.11216 | 0.11219 | 0.11219 | 0.99517 | -0.15664 | 0.99274 | -0.24905 | 13.6823
132 | 3.4309 | 1.3676 | -3.4307 | -1.375 | 0.00021098 | -0.007326 | 0.1074 | 0.10748 | 0.10748 | 0.99274 | -0.24905 | 0.99267 | -0.25062 | 12.765
133 | 3.4307 | 1.375 | -3.4296 | -1.4129 | 0.001098 | -0.037928 | 0.10748 | 0.10791 | 0.10791 | 0.99267 | -0.25062 | 0.99229 | -0.25868 | 12.8156
134 | 0.39874 | 0.19307 | -0.39873 | -0.19311 | 1.1932e-05 | -3.9452e-05 | 0.01292 | 0.012921 | 0.012921 | 0.98987 | -0.26718 | 0.98984 | -0.26738 | 6.1527
135 | 1.5437 | 0.67161 | -1.5436 | -0.67815 | 7.9803e-05 | -0.0065411 | 0.049095 | 0.049172 | 0.049172 | 0.98988 | -0.27574 | 0.98982 | -0.27605 | 7.7073
136 | 0.51319 | 0.23683 | -0.51276 | -0.2376 | 0.00043006 | -0.00076618 | 0.016491 | 0.016503 | 0.016503 | 0.9894 | -0.27357 | 0.98852 | -0.28006 | 7.8588
137 | 0.19806 | 0.09482 | -0.19806 | -0.095924 | 2.6254e-06 | -0.0011036 | 0.0064256 | 0.0064396 | 0.0064396 | 0.98652 | -0.23459 | 0.98651 | -0.23447 | 2.9271
138 | -7.9039 | -3.322 | 7.907 | 3.3042 | 0.0030817 | -0.017765 | 0.24881 | 0.24858 | 0.24881 | 0.99474 | -0.14523 | 0.99519 | -0.13575 | 29.5498
139 | -7.907 | -3.3042 | 7.9072 | 3.3028 | 0.00025194 | -0.0014549 | 0.24858 | 0.24856 | 0.24858 | 0.99519 | -0.13575 | 0.99523 | -0.13497 | 29.5223
140 | -7.9796 | -3.3378 | 7.9801 | 3.335 | 0.00050719 | -0.0028672 | 0.25089 | 0.25085 | 0.25089 | 0.99523 | -0.13497 | 0.99531 | -0.13342 | 29.7967
141 | -7.9801 | -3.335 | 7.9807 | 3.3313 | 0.00064424 | -0.0036441 | 0.25085 | 0.2508 | 0.25085 | 0.99531 | -0.13342 | 0.9954 | -0.13145 | 29.7923
142 | 0.10298 | 0.049688 | -0.10298 | -0.049874 | 1.1883e-07 | -0.0001861 | 0.003339 | 0.0033414 | 0.0033414 | 0.98852 | -0.28006 | 0.98852 | -0.28005 | 1.5188
143 | 0.40978 | 0.18791 | -0.40968 | -0.19813 | 0.0001026 | -0.010214 | 0.013165 | 0.013292 | 0.013292 | 0.98852 | -0.28006 | 0.98829 | -0.27801 | 6.042
144 | 0.40968 | 0.19813 | -0.40968 | -0.19842 | 2.9269e-06 | -0.00028842 | 0.013292 | 0.013296 | 0.013296 | 0.98829 | -0.27801 | 0.98828 | -0.27795 | 6.0437
145 | -0.18876 | -0.091421 | 0.18876 | 0.089699 | 3.6859e-06 | -0.0017224 | 0.0061247 | 0.0061029 | 0.0061247 | 0.98854 | -0.2744 | 0.98856 | -0.27456 | 2.7839
146 | -0.18876 | -0.089699 | 0.18878 | 0.084569 | 1.0824e-05 | -0.0051297 | 0.0061029 | 0.0060401 | 0.0061029 | 0.98856 | -0.27456 | 0.98861 | -0.27501 | 2.7741
147 | -0.18878 | -0.084569 | 0.18878 | 0.084491 | 1.6208e-07 | -7.7612e-05 | 0.0060401 | 0.0060392 | 0.0060401 | 0.98861 | -0.27501 | 0.98861 | -0.27502 | 2.7455
148 | -0.51812 | -0.244 | 0.51813 | 0.24332 | 1.0953e-05 | -0.00068173 | 0.016723 | 0.016714 | 0.016723 | 0.98861 | -0.27502 | 0.98863 | -0.27519 | 7.6013
149 | -0.51813 | -0.24332 | 0.51836 | 0.22905 | 0.00022663 | -0.014269 | 0.016714 | 0.016541 | 0.016714 | 0.98863 | -0.27519 | 0.98904 | -0.27849 | 7.5975
150 | 1.5436 | 0.67815 | -1.5436 | -0.68461 | 7.9079e-05 | -0.0064606 | 0.049172 | 0.049249 | 0.049249 | 0.98982 | -0.27605 | 0.98977 | -0.27635 | 7.7193
151 | 1.5436 | 0.68461 | -1.5436 | -0.68541 | 9.8432e-06 | -0.0008027 | 0.049249 | 0.049258 | 0.049258 | 0.98977 | -0.27635 | 0.98976 | -0.27639 | 7.7208
152 | 1.1496 | 0.4946 | -1.1495 | -0.49461 | 6.978e-05 | -1.0996e-05 | 0.0365 | 0.036502 | 0.036502 | 0.98976 | -0.27639 | 0.98965 | -0.28302 | 5.6593
153 | 0.68776 | 0.29439 | -0.68731 | -0.31073 | 0.00045207 | -0.01634 | 0.021822 | 0.022016 | 0.022016 | 0.98965 | -0.28302 | 0.98904 | -0.27849 | 10.0071
154 | 0.46174 | 0.20022 | -0.46154 | -0.21672 | 0.00020662 | -0.016504 | 0.01468 | 0.014879 | 0.014879 | 0.98965 | -0.28302 | 0.98924 | -0.27972 | 6.7633
155 | 0.16895 | 0.081677 | -0.16894 | -0.081821 | 6.8243e-06 | -0.00014477 | 0.0054772 | 0.0054791 | 0.0054791 | 0.98904 | -0.27849 | 0.989 | -0.27876 | 2.6091
156 | 0.22932 | 0.10453 | -0.2293 | -0.1107 | 1.9284e-05 | -0.0061702 | 0.0073544 | 0.0074309 | 0.0074309 | 0.98924 | -0.27972 | 0.98916 | -0.27904 | 3.3777
157 | 0.23222 | 0.11219 | -0.23219 | -0.11246 | 2.4121e-05 | -0.00026397 | 0.0075259 | 0.0075294 | 0.0075294 | 0.98924 | -0.27972 | 0.98913 | -0.28041 | 3.5854
158 | 0.2293 | 0.1107 | -0.2293 | -0.11106 | 1.1165e-06 | -0.00035329 | 0.0074309 | 0.0074354 | 0.0074354 | 0.98916 | -0.27904 | 0.98915 | -0.27899 | 3.3797
159 | 3.4296 | 1.4129 | -3.4294 | -1.4176 | 0.00013736 | -0.0047206 | 0.10791 | 0.10796 | 0.10796 | 0.99229 | -0.25868 | 0.99225 | -0.25967 | 12.822
160 | 3.275 | 1.3428 | -3.2674 | -1.3369 | 0.007549 | 0.0058574 | 0.10298 | 0.10303 | 0.10303 | 0.99225 | -0.25967 | 0.98913 | -0.37722 | 12.5649

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.8674 | 6.9956

## res_load
| p_mw | q_mvar
0 | 0.37759 | 0.18288
1 | 0.083896 | 0.040633
2 | 0.097006 | 0.046982
3 | 0.096766 | 0.046866
4 | 0.22191 | 0.10748
5 | 0.19056 | 0.092294
6 | 0.13669 | 0.066204
7 | 0.24755 | 0.11989
8 | 0.23353 | 0.1131
9 | 0.20924 | 0.10134
10 | 0.33486 | 0.16218
11 | 0.10761 | 0.052117
12 | 0.112 | 0.054243
13 | 0.059243 | 0.028693
14 | 0.088135 | 0.042685
15 | 0.093543 | 0.045305
16 | 0.12823 | 0.062104
17 | 0.068485 | 0.033169
18 | 0.062557 | 0.030298
19 | 0.21648 | 0.10485
20 | 0.10097 | 0.048903
21 | 0.0814 | 0.039424
22 | 0.13801 | 0.066844
23 | 0.13077 | 0.063333
24 | 0.12277 | 0.059459
25 | 0.13723 | 0.066466
26 | 0.050275 | 0.024349
27 | 0.38735 | 0.1876
28 | 0.07278 | 0.035249
29 | 0.40783 | 0.19752
30 | 0.16715 | 0.080957
31 | 0.26661 | 0.12913
32 | 0.32544 | 0.15762
33 | 0.3894 | 0.18859
34 | 0.099053 | 0.047974
35 | 0.3952 | 0.19141
36 | 0.1384 | 0.067029
37 | 0.33412 | 0.16182
38 | 0.37949 | 0.18379
39 | 0.17318 | 0.083875
40 | 0.071413 | 0.034587
41 | 0.31068 | 0.15047
42 | 0.15738 | 0.076223
43 | 0.40458 | 0.19595
44 | 0.091081 | 0.044112
45 | 0.25391 | 0.12297
46 | 0.27815 | 0.13472
47 | 0.25395 | 0.12299
48 | 0.41976 | 0.2033
49 | 0.25241 | 0.12225
50 | 0.31556 | 0.15283
51 | 0.17169 | 0.083153
52 | 0.2933 | 0.14205
53 | 0.093116 | 0.045098
54 | 0.12576 | 0.060908
55 | 0.24542 | 0.11886
56 | 0.22095 | 0.10701
57 | 0.1512 | 0.073227
58 | 0.12536 | 0.060714
59 | 0.08274 | 0.040073
60 | 0.074162 | 0.035918
61 | 0.24871 | 0.12046
62 | 0.14877 | 0.072053
63 | 0.39873 | 0.19311
64 | 0.19684 | 0.095335
65 | 0.37615 | 0.18218
66 | 0.36424 | 0.17641
67 | 0.21088 | 0.10213
68 | 0.29124 | 0.14105
69 | 0.19806 | 0.095924
70 | 0.072373 | 0.035052
71 | 0.16441 | 0.079629
72 | 0.40968 | 0.19842
73 | 0.10298 | 0.049874
74 | 0.18876 | 0.091421
75 | 0.32935 | 0.15951
76 | 0.39399 | 0.19082
77 | 0.23219 | 0.11246
78 | 0.2293 | 0.11106
79 | 0.16894 | 0.081821
80 | 0.15449 | 0.074821

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1