## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_98_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_98_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_98_0_node_14 | 20 | n |  | TRUE
3 | bus_MV_98_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_98_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_98_0_node_5 | 20 | n |  | TRUE
6 | bus_MV_98_0_node_15 | 20 | n |  | TRUE
7 | bus_MV_98_0_node_6 | 20 | n |  | TRUE
8 | bus_MV_98_0_node_7 | 20 | n |  | TRUE
9 | bus_MV_98_0_node_9 | 20 | n |  | TRUE
10 | bus_MV_98_0_node_16 | 20 | n |  | TRUE
11 | bus_MV_98_0_node_170 | 20 | n |  | TRUE
12 | bus_MV_98_0_node_172 | 20 | n |  | TRUE
13 | bus_MV_98_0_node_11 | 20 | n |  | TRUE
14 | bus_MV_98_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_98_0_node_12 | 20 | n |  | TRUE
16 | bus_MV_98_0_node_17 | 20 | n |  | TRUE
17 | bus_MV_98_0_node_18 | 20 | n |  | TRUE
18 | bus_MV_98_0_node_171 | 20 | n |  | TRUE
19 | bus_MV_98_0_node_143 | 20 | n |  | TRUE
20 | bus_MV_98_0_node_10 | 20 | n |  | TRUE
21 | bus_MV_98_0_node_13 | 20 | n |  | TRUE
22 | bus_MV_98_0_node_136 | 20 | n |  | TRUE
23 | bus_MV_98_0_node_161 | 20 | n |  | TRUE
24 | bus_MV_98_0_node_177 | 20 | n |  | TRUE
25 | bus_MV_98_0_node_134 | 20 | n |  | TRUE
26 | bus_MV_98_0_node_133 | 20 | n |  | TRUE
27 | bus_MV_98_0_node_180 | 20 | n |  | TRUE
28 | bus_MV_98_0_node_153 | 20 | n |  | TRUE
29 | bus_MV_98_0_node_179 | 20 | n |  | TRUE
30 | bus_MV_98_0_node_135 | 20 | n |  | TRUE
31 | bus_MV_98_0_node_159 | 20 | n |  | TRUE
32 | bus_MV_98_0_node_154 | 20 | n |  | TRUE
33 | bus_MV_98_0_node_19 | 20 | n |  | TRUE
34 | bus_MV_98_0_node_21 | 20 | n |  | TRUE
35 | bus_MV_98_0_node_20 | 20 | n |  | TRUE
36 | bus_MV_98_0_node_24 | 20 | n |  | TRUE
37 | bus_MV_98_0_node_145 | 20 | n |  | TRUE
38 | bus_MV_98_0_node_22 | 20 | n |  | TRUE
39 | bus_MV_98_0_node_25 | 20 | n |  | TRUE
40 | bus_MV_98_0_node_142 | 20 | n |  | TRUE
41 | bus_MV_98_0_node_144 | 20 | n |  | TRUE
42 | bus_MV_98_0_node_26 | 20 | n |  | TRUE
43 | bus_MV_98_0_node_28 | 20 | n |  | TRUE
44 | bus_MV_98_0_node_27 | 20 | n |  | TRUE
45 | bus_MV_98_0_node_168 | 20 | n |  | TRUE
46 | bus_MV_98_0_node_29 | 20 | n |  | TRUE
47 | bus_MV_98_0_node_34 | 20 | n |  | TRUE
48 | bus_MV_98_0_node_30 | 20 | n |  | TRUE
49 | bus_MV_98_0_node_31 | 20 | n |  | TRUE
50 | bus_MV_98_0_node_32 | 20 | n |  | TRUE
51 | bus_MV_98_0_node_33 | 20 | n |  | TRUE
52 | bus_MV_98_0_node_164 | 20 | n |  | TRUE
53 | bus_MV_98_0_node_37 | 20 | n |  | TRUE
54 | bus_MV_98_0_node_35 | 20 | n |  | TRUE
55 | bus_MV_98_0_node_178 | 20 | n |  | TRUE
56 | bus_MV_98_0_node_38 | 20 | n |  | TRUE
57 | bus_MV_98_0_node_39 | 20 | n |  | TRUE
58 | bus_MV_98_0_node_165 | 20 | n |  | TRUE
59 | bus_MV_98_0_node_176 | 20 | n |  | TRUE
60 | bus_MV_98_0_node_40 | 20 | n |  | TRUE
61 | bus_MV_98_0_node_41 | 20 | n |  | TRUE
62 | bus_MV_98_0_node_103 | 20 | n |  | TRUE
63 | bus_MV_98_0_node_91 | 20 | n |  | TRUE
64 | bus_MV_98_0_node_102 | 20 | n |  | TRUE
65 | bus_MV_98_0_node_104 | 20 | n |  | TRUE
66 | bus_MV_98_0_node_105 | 20 | n |  | TRUE
67 | bus_MV_98_0_node_112 | 20 | n |  | TRUE
68 | bus_MV_98_0_node_100 | 20 | n |  | TRUE
69 | bus_MV_98_0_node_60 | 20 | n |  | TRUE
70 | bus_MV_98_0_node_163 | 20 | n |  | TRUE
71 | bus_MV_98_0_node_132 | 20 | n |  | TRUE
72 | bus_MV_98_0_node_158 | 20 | n |  | TRUE
73 | bus_MV_98_0_node_130 | 20 | n |  | TRUE
74 | bus_MV_98_0_node_42 | 20 | n |  | TRUE
75 | bus_MV_98_0_node_44 | 20 | n |  | TRUE
76 | bus_MV_98_0_node_152 | 20 | n |  | TRUE
77 | bus_MV_98_0_node_54 | 20 | n |  | TRUE
78 | bus_MV_98_0_node_63 | 20 | n |  | TRUE
79 | bus_MV_98_0_node_45 | 20 | n |  | TRUE
80 | bus_MV_98_0_node_48 | 20 | n |  | TRUE
81 | bus_MV_98_0_node_50 | 20 | n |  | TRUE
82 | bus_MV_98_0_node_51 | 20 | n |  | TRUE
83 | bus_MV_98_0_node_46 | 20 | n |  | TRUE
84 | bus_MV_98_0_node_47 | 20 | n |  | TRUE
85 | bus_MV_98_0_node_59 | 20 | n |  | TRUE
86 | bus_MV_98_0_node_151 | 20 | n |  | TRUE
87 | bus_MV_98_0_node_53 | 20 | n |  | TRUE
88 | bus_MV_98_0_node_146 | 20 | n |  | TRUE
89 | bus_MV_98_0_node_55 | 20 | n |  | TRUE
90 | bus_MV_98_0_node_147 | 20 | n |  | TRUE
91 | bus_MV_98_0_node_137 | 20 | n |  | TRUE
92 | bus_MV_98_0_node_64 | 20 | n |  | TRUE
93 | bus_MV_98_0_node_49 | 20 | n |  | TRUE
94 | bus_MV_98_0_node_162 | 20 | n |  | TRUE
95 | bus_MV_98_0_node_68 | 20 | n |  | TRUE
96 | bus_MV_98_0_node_88 | 20 | n |  | TRUE
97 | bus_MV_98_0_node_52 | 20 | n |  | TRUE
98 | bus_MV_98_0_node_87 | 20 | n |  | TRUE
99 | bus_MV_98_0_node_93 | 20 | n |  | TRUE
100 | bus_MV_98_0_node_56 | 20 | n |  | TRUE
101 | bus_MV_98_0_node_140 | 20 | n |  | TRUE
102 | bus_MV_98_0_node_141 | 20 | n |  | TRUE
103 | bus_MV_98_0_node_138 | 20 | n |  | TRUE
104 | bus_MV_98_0_node_149 | 20 | n |  | TRUE
105 | bus_MV_98_0_node_150 | 20 | n |  | TRUE
106 | bus_MV_98_0_node_62 | 20 | n |  | TRUE
107 | bus_MV_98_0_node_94 | 20 | n |  | TRUE
108 | bus_MV_98_0_node_97 | 20 | n |  | TRUE
109 | bus_MV_98_0_node_148 | 20 | n |  | TRUE
110 | bus_MV_98_0_node_57 | 20 | n |  | TRUE
111 | bus_MV_98_0_node_58 | 20 | n |  | TRUE
112 | bus_MV_98_0_node_86 | 20 | n |  | TRUE
113 | bus_MV_98_0_node_71 | 20 | n |  | TRUE
114 | bus_MV_98_0_node_72 | 20 | n |  | TRUE
115 | bus_MV_98_0_node_70 | 20 | n |  | TRUE
116 | bus_MV_98_0_node_75 | 20 | n |  | TRUE
117 | bus_MV_98_0_node_101 | 20 | n |  | TRUE
118 | bus_MV_98_0_node_65 | 20 | n |  | TRUE
119 | bus_MV_98_0_node_66 | 20 | n |  | TRUE
120 | bus_MV_98_0_node_67 | 20 | n |  | TRUE
121 | bus_MV_98_0_node_92 | 20 | n |  | TRUE
122 | bus_MV_98_0_node_166 | 20 | n |  | TRUE
123 | bus_MV_98_0_node_84 | 20 | n |  | TRUE
124 | bus_MV_98_0_node_108 | 20 | n |  | TRUE
125 | bus_MV_98_0_node_174 | 20 | n |  | TRUE
126 | bus_MV_98_0_node_106 | 20 | n |  | TRUE
127 | bus_MV_98_0_node_107 | 20 | n |  | TRUE
128 | bus_MV_98_0_node_175 | 20 | n |  | TRUE
129 | bus_MV_98_0_node_109 | 20 | n |  | TRUE
130 | bus_MV_98_0_node_127 | 20 | n |  | TRUE
131 | bus_MV_98_0_node_69 | 20 | n |  | TRUE
132 | bus_MV_98_0_node_110 | 20 | n |  | TRUE
133 | bus_MV_98_0_node_173 | 20 | n |  | TRUE
134 | bus_MV_98_0_node_85 | 20 | n |  | TRUE
135 | bus_MV_98_0_node_74 | 20 | n |  | TRUE
136 | bus_MV_98_0_node_76 | 20 | n |  | TRUE
137 | bus_MV_98_0_node_77 | 20 | n |  | TRUE
138 | bus_MV_98_0_node_123 | 20 | n |  | TRUE
139 | bus_MV_98_0_node_78 | 20 | n |  | TRUE
140 | bus_MV_98_0_node_79 | 20 | n |  | TRUE
141 | bus_MV_98_0_node_81 | 20 | n |  | TRUE
142 | bus_MV_98_0_node_80 | 20 | n |  | TRUE
143 | bus_MV_98_0_node_82 | 20 | n |  | TRUE
144 | bus_MV_98_0_node_167 | 20 | n |  | TRUE
145 | bus_MV_98_0_node_124 | 20 | n |  | TRUE
146 | bus_MV_98_0_node_83 | 20 | n |  | TRUE
147 | bus_MV_98_0_node_89 | 20 | n |  | TRUE
148 | bus_MV_98_0_node_98 | 20 | n |  | TRUE
149 | bus_MV_98_0_node_99 | 20 | n |  | TRUE
150 | bus_MV_98_0_node_96 | 20 | n |  | TRUE
151 | bus_MV_98_0_node_117 | 20 | n |  | TRUE
152 | bus_MV_98_0_node_126 | 20 | n |  | TRUE
153 | bus_MV_98_0_node_155 | 20 | n |  | TRUE
154 | bus_MV_98_0_node_156 | 20 | n |  | TRUE
155 | bus_MV_98_0_node_160 | 20 | n |  | TRUE
156 | bus_MV_98_0_node_157 | 20 | n |  | TRUE
157 | bus_MV_98_0_node_115 | 20 | n |  | TRUE
158 | bus_MV_98_0_node_116 | 20 | n |  | TRUE
159 | bus_MV_98_0_node_118 | 20 | n |  | TRUE
160 | bus_MV_98_0_node_122 | 20 | n |  | TRUE
161 | bus_MV_98_0_node_119 | 20 | n |  | TRUE
162 | bus_MV_98_0_node_120 | 20 | n |  | TRUE
163 | bus_MV_98_0_node_121 | 20 | n |  | TRUE
164 | bus_MV_98_0_node_128 | 20 | n |  | TRUE
165 | bus_MV_98_0_node_129 | 20 | n |  | TRUE
166 | bus_MV_98_0_node_139 | 20 | n |  | TRUE
167 | bus_HV_98_0_node_177 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_98_0_load_0 | 0 | 0.23646 | 0.11452 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_98_0_load_2 | 1 | 0.17055 | 0.082601 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_98_0_load_14 | 2 | 0.36214 | 0.17539 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_98_0_load_3 | 3 | 0.26142 | 0.12661 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_98_0_load_16 | 10 | 0.07206 | 0.0349 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_98_0_load_8 | 14 | 0.23027 | 0.11153 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_98_0_load_17 | 16 | 0.2582 | 0.12505 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_98_0_load_18 | 17 | 0.39561 | 0.1916 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_98_0_load_171 | 18 | 0.33707 | 0.16325 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_98_0_load_143 | 19 | 0.17033 | 0.082495 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_98_0_load_161 | 23 | 0.073246 | 0.035475 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_98_0_load_177 | 24 | 0.19099 | 0.092498 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_98_0_load_180 | 27 | 0.5419 | 0.26246 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_98_0_load_153 | 28 | 0.077294 | 0.037435 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_98_0_load_179 | 29 | 0.29869 | 0.14466 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_98_0_load_159 | 31 | 0.13434 | 0.065062 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_98_0_load_154 | 32 | 0.072449 | 0.035088 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_98_0_load_19 | 33 | 0.37046 | 0.17942 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_98_0_load_24 | 36 | 0.152 | 0.073619 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_98_0_load_145 | 37 | 0.28335 | 0.13723 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_98_0_load_25 | 39 | 0.33284 | 0.1612 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_98_0_load_144 | 41 | 0.15175 | 0.073497 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_98_0_load_168 | 45 | 0.12672 | 0.061375 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_98_0_load_29 | 46 | 0.40373 | 0.19554 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_98_0_load_34 | 47 | 0.23313 | 0.11291 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_98_0_load_30 | 48 | 0.37165 | 0.18 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_98_0_load_164 | 52 | 0.27715 | 0.13423 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_98_0_load_37 | 53 | 0.12699 | 0.061506 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_98_0_load_35 | 54 | 0.10214 | 0.049467 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_98_0_load_178 | 55 | 0.17388 | 0.084213 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_98_0_load_38 | 56 | 0.34459 | 0.16689 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_98_0_load_165 | 58 | 0.32121 | 0.15557 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_98_0_load_176 | 59 | 0.29601 | 0.14336 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_98_0_load_102 | 64 | 0.27647 | 0.1339 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_98_0_load_112 | 67 | 0.34514 | 0.16716 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_98_0_load_60 | 69 | 0.37005 | 0.17922 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_98_0_load_163 | 70 | 0.32024 | 0.1551 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_98_0_load_130 | 73 | 0.12775 | 0.061871 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_98_0_load_42 | 74 | 0.37628 | 0.18224 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_98_0_load_152 | 76 | 0.10035 | 0.048602 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_98_0_load_48 | 80 | 0.32035 | 0.15515 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_98_0_load_59 | 85 | 0.36278 | 0.1757 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_98_0_load_151 | 86 | 0.18993 | 0.091988 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_98_0_load_146 | 88 | 0.092548 | 0.044823 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_98_0_load_147 | 90 | 0.077552 | 0.03756 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_98_0_load_137 | 91 | 0.40357 | 0.19546 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_98_0_load_64 | 92 | 0.085368 | 0.041345 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_98_0_load_162 | 94 | 0.22402 | 0.1085 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_98_0_load_68 | 95 | 0.24189 | 0.11715 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_98_0_load_87 | 98 | 0.389 | 0.1884 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_98_0_load_93 | 99 | 0.33773 | 0.16357 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_98_0_load_56 | 100 | 0.25643 | 0.12419 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_98_0_load_141 | 102 | 0.12148 | 0.058836 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_98_0_load_94 | 107 | 0.26249 | 0.12713 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_98_0_load_97 | 108 | 0.17358 | 0.084067 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_98_0_load_86 | 112 | 0.2218 | 0.10742 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_98_0_load_65 | 118 | 0.34704 | 0.16808 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_98_0_load_92 | 121 | 0.35059 | 0.1698 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_98_0_load_166 | 122 | 0.31749 | 0.15377 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_98_0_load_174 | 125 | 0.13427 | 0.065031 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_98_0_load_175 | 128 | 0.30089 | 0.14573 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_98_0_load_109 | 129 | 0.22847 | 0.11065 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_98_0_load_127 | 130 | 0.29149 | 0.14118 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_98_0_load_69 | 131 | 0.26254 | 0.12715 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_98_0_load_110 | 132 | 0.35782 | 0.1733 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_98_0_load_173 | 133 | 0.37699 | 0.18259 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_98_0_load_85 | 134 | 0.25991 | 0.12588 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_98_0_load_76 | 136 | 0.088946 | 0.043078 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_98_0_load_123 | 138 | 0.40518 | 0.19624 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_98_0_load_78 | 139 | 0.075654 | 0.036641 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_98_0_load_81 | 141 | 0.30772 | 0.14904 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_98_0_load_167 | 144 | 0.23226 | 0.11249 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_98_0_load_124 | 145 | 0.21328 | 0.1033 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_98_0_load_89 | 147 | 0.35154 | 0.17026 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_98_0_load_98 | 148 | 0.21502 | 0.10414 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_98_0_load_126 | 152 | 0.32632 | 0.15805 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_98_0_load_155 | 153 | 0.085641 | 0.041478 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_98_0_load_156 | 154 | 0.11794 | 0.057121 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_98_0_load_160 | 155 | 0.23961 | 0.11605 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_98_0_load_115 | 157 | 0.33962 | 0.16448 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_98_0_load_118 | 159 | 0.28785 | 0.13941 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_98_0_load_128 | 164 | 0.20696 | 0.10024 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_98_0_load_129 | 165 | 0.069959 | 0.033883 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_98_0_load_139 | 166 | 0.14572 | 0.070576 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_98_0_line_0 |  | 0 | 1 | 1.1189 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_98_0_line_1 |  | 1 | 2 | 2.3214 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_98_0_line_2 |  | 2 | 6 | 0.095409 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_98_0_line_3 |  | 3 | 4 | 0.084746 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
4 | MV_98_0_line_4 |  | 3 | 5 | 0.10423 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
5 | MV_98_0_line_5 |  | 4 | 7 | 0.40293 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
6 | MV_98_0_line_6 |  | 5 | 8 | 0.8617 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
7 | MV_98_0_line_7 |  | 6 | 10 | 0.054021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_98_0_line_8 |  | 7 | 9 | 0.78039 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
9 | MV_98_0_line_9 |  | 7 | 10 | 0.038467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_98_0_line_10 |  | 8 | 11 | 0.33246 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_98_0_line_11 |  | 8 | 12 | 0.027703 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
12 | MV_98_0_line_12 |  | 9 | 13 | 0.38652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_98_0_line_13 |  | 9 | 14 | 0.12488 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
14 | MV_98_0_line_14 |  | 11 | 18 | 0.046324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_98_0_line_15 |  | 12 | 19 | 0.007737 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
16 | MV_98_0_line_16 |  | 13 | 15 | 0.39317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_98_0_line_17 |  | 13 | 16 | 0.14761 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_98_0_line_18 |  | 14 | 20 | 0.03942 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
19 | MV_98_0_line_19 |  | 15 | 17 | 0.067142 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_98_0_line_20 |  | 19 | 40 | 0.031367 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
21 | MV_98_0_line_21 |  | 20 | 21 | 1.2634 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
22 | MV_98_0_line_22 |  | 21 | 22 | 0.34768 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
23 | MV_98_0_line_23 |  | 21 | 23 | 0.087882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_98_0_line_24 |  | 22 | 24 | 0.010064 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
25 | MV_98_0_line_25 |  | 22 | 25 | 0.098805 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_98_0_line_26 |  | 25 | 29 | 0.097492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_98_0_line_27 |  | 25 | 30 | 0.11944 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
28 | MV_98_0_line_28 |  | 26 | 27 | 0.057515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_98_0_line_29 |  | 26 | 28 | 0.21823 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_98_0_line_30 |  | 28 | 32 | 0.030848 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_98_0_line_31 |  | 28 | 31 | 0.067221 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
32 | MV_98_0_line_32 |  | 30 | 31 | 0.01041 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_98_0_line_33 |  | 32 | 153 | 0.091912 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
34 | MV_98_0_line_34 |  | 33 | 34 | 0.077351 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_98_0_line_35 |  | 33 | 35 | 0.022699 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
36 | MV_98_0_line_36 |  | 34 | 36 | 0.011081 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
37 | MV_98_0_line_37 |  | 34 | 37 | 0.20746 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_98_0_line_38 |  | 35 | 38 | 0.37528 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
39 | MV_98_0_line_39 |  | 36 | 40 | 0.019665 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
40 | MV_98_0_line_40 |  | 37 | 41 | 0.0043954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_98_0_line_41 |  | 38 | 39 | 0.04659 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
42 | MV_98_0_line_42 |  | 39 | 42 | 0.10044 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
43 | MV_98_0_line_43 |  | 42 | 43 | 0.49539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_98_0_line_44 |  | 43 | 46 | 0.036166 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_98_0_line_45 |  | 43 | 44 | 0.44348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_98_0_line_46 |  | 44 | 45 | 0.10095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_98_0_line_47 |  | 46 | 47 | 0.95347 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_98_0_line_48 |  | 47 | 51 | 0.1243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_98_0_line_49 |  | 48 | 49 | 0.013029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_98_0_line_50 |  | 49 | 50 | 0.70723 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_98_0_line_51 |  | 49 | 51 | 1.0624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_98_0_line_52 |  | 50 | 52 | 0.02858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_98_0_line_53 |  | 50 | 53 | 0.93549 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_98_0_line_54 |  | 52 | 54 | 1.8713 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_98_0_line_55 |  | 53 | 55 | 1.4407 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_98_0_line_56 |  | 56 | 57 | 0.063489 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
57 | MV_98_0_line_57 |  | 56 | 58 | 0.37811 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
58 | MV_98_0_line_58 |  | 56 | 59 | 0.36036 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_98_0_line_59 |  | 57 | 60 | 0.29269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_98_0_line_60 |  | 57 | 61 | 0.34995 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_98_0_line_61 |  | 58 | 68 | 0.054415 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_98_0_line_62 |  | 59 | 65 | 0.030074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_98_0_line_63 |  | 60 | 69 | 0.07015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_98_0_line_64 |  | 61 | 70 | 0.014298 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
65 | MV_98_0_line_65 |  | 61 | 71 | 0.22011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_98_0_line_66 |  | 62 | 63 | 0.19036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_98_0_line_67 |  | 62 | 64 | 0.032323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_98_0_line_68 |  | 63 | 129 | 0.042716 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_98_0_line_69 |  | 65 | 66 | 0.30175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_98_0_line_70 |  | 66 | 67 | 0.040963 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_98_0_line_71 |  | 68 | 117 | 0.13581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_98_0_line_72 |  | 68 | 109 | 0.23785 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
73 | MV_98_0_line_73 |  | 70 | 72 | 0.008044 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
74 | MV_98_0_line_74 |  | 71 | 73 | 0.016324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_98_0_line_75 |  | 72 | 156 | 0.054167 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_98_0_line_76 |  | 74 | 75 | 0.054805 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_98_0_line_77 |  | 74 | 76 | 0.054312 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
78 | MV_98_0_line_78 |  | 75 | 77 | 0.13238 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_98_0_line_79 |  | 76 | 78 | 0.02184 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_98_0_line_80 |  | 77 | 89 | 0.1542 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_98_0_line_81 |  | 77 | 90 | 0.005895 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
82 | MV_98_0_line_82 |  | 77 | 87 | 0.048178 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_98_0_line_83 |  | 78 | 106 | 0.032429 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
84 | MV_98_0_line_84 |  | 79 | 80 | 0.0074297 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
85 | MV_98_0_line_85 |  | 79 | 81 | 0.30306 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
86 | MV_98_0_line_86 |  | 79 | 82 | 0.69936 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
87 | MV_98_0_line_87 |  | 80 | 92 | 0.037534 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
88 | MV_98_0_line_88 |  | 81 | 95 | 0.010857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_98_0_line_89 |  | 81 | 93 | 0.048392 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_98_0_line_90 |  | 82 | 96 | 0.56743 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
91 | MV_98_0_line_91 |  | 82 | 97 | 0.36039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_98_0_line_92 |  | 82 | 98 | 0.082462 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
93 | MV_98_0_line_93 |  | 83 | 84 | 0.14156 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_98_0_line_94 |  | 83 | 85 | 0.047716 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_98_0_line_95 |  | 84 | 86 | 0.23206 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
96 | MV_98_0_line_96 |  | 85 | 100 | 0.10554 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
97 | MV_98_0_line_97 |  | 86 | 105 | 0.028867 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_98_0_line_98 |  | 87 | 88 | 0.036852 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
99 | MV_98_0_line_99 |  | 89 | 91 | 0.014824 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_98_0_line_100 |  | 90 | 109 | 0.014325 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_98_0_line_101 |  | 91 | 103 | 0.078589 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
102 | MV_98_0_line_102 |  | 92 | 106 | 0.020665 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
103 | MV_98_0_line_103 |  | 93 | 94 | 0.069265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_98_0_line_104 |  | 96 | 107 | 0.098139 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
105 | MV_98_0_line_105 |  | 96 | 108 | 1.1058 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
106 | MV_98_0_line_106 |  | 97 | 99 | 0.036291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_98_0_line_107 |  | 100 | 110 | 0.030673 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
108 | MV_98_0_line_108 |  | 101 | 102 | 0.048894 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
109 | MV_98_0_line_109 |  | 101 | 103 | 0.073804 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
110 | MV_98_0_line_110 |  | 102 | 104 | 0.0037018 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
111 | MV_98_0_line_111 |  | 103 | 166 | 0.028141 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
112 | MV_98_0_line_112 |  | 104 | 105 | 0.016388 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
113 | MV_98_0_line_113 |  | 108 | 150 | 0.068289 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
114 | MV_98_0_line_114 |  | 110 | 111 | 0.033075 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
115 | MV_98_0_line_115 |  | 111 | 112 | 0.071607 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
116 | MV_98_0_line_116 |  | 112 | 116 | 0.030396 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
117 | MV_98_0_line_117 |  | 112 | 113 | 0.043785 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_98_0_line_118 |  | 113 | 114 | 0.64036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_98_0_line_119 |  | 113 | 115 | 0.29308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_98_0_line_120 |  | 114 | 132 | 0.041486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_98_0_line_121 |  | 115 | 131 | 0.055152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_98_0_line_122 |  | 116 | 135 | 0.005585 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
123 | MV_98_0_line_123 |  | 117 | 129 | 0.008779 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_98_0_line_124 |  | 117 | 149 | 0.16535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_98_0_line_125 |  | 118 | 119 | 0.025808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_98_0_line_126 |  | 119 | 120 | 0.26526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_98_0_line_127 |  | 120 | 122 | 0.060346 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_98_0_line_128 |  | 121 | 122 | 0.31524 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
129 | MV_98_0_line_129 |  | 121 | 123 | 0.083764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_98_0_line_130 |  | 123 | 146 | 0.28379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_98_0_line_131 |  | 124 | 125 | 0.05291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_98_0_line_132 |  | 124 | 126 | 0.24823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_98_0_line_133 |  | 124 | 127 | 0.077914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_98_0_line_134 |  | 125 | 154 | 0.1929 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
135 | MV_98_0_line_135 |  | 126 | 128 | 0.030539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_98_0_line_136 |  | 127 | 130 | 0.045595 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_98_0_line_137 |  | 130 | 155 | 0.084598 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
138 | MV_98_0_line_138 |  | 133 | 134 | 0.18404 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_98_0_line_139 |  | 134 | 145 | 0.83885 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
140 | MV_98_0_line_140 |  | 134 | 144 | 0.22628 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_98_0_line_141 |  | 135 | 136 | 0.048035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_98_0_line_142 |  | 135 | 137 | 0.55247 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
143 | MV_98_0_line_143 |  | 137 | 138 | 0.074019 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
144 | MV_98_0_line_144 |  | 139 | 140 | 0.026464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_98_0_line_145 |  | 139 | 141 | 0.60132 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_98_0_line_146 |  | 140 | 142 | 0.67604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_98_0_line_147 |  | 141 | 143 | 0.075639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_98_0_line_148 |  | 142 | 144 | 0.012985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_98_0_line_149 |  | 143 | 146 | 0.20306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_98_0_line_150 |  | 146 | 147 | 0.04391 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
151 | MV_98_0_line_151 |  | 146 | 148 | 0.27108 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
152 | MV_98_0_line_152 |  | 148 | 149 | 0.020394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_98_0_line_153 |  | 150 | 151 | 1.0407 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
154 | MV_98_0_line_154 |  | 151 | 152 | 0.059319 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
155 | MV_98_0_line_155 |  | 152 | 160 | 0.13629 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
156 | MV_98_0_line_156 |  | 153 | 154 | 0.0379 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
157 | MV_98_0_line_157 |  | 154 | 156 | 0.13453 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
158 | MV_98_0_line_158 |  | 157 | 158 | 0.055847 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
159 | MV_98_0_line_159 |  | 157 | 159 | 0.21036 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
160 | MV_98_0_line_160 |  | 158 | 160 | 0.23827 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
161 | MV_98_0_line_161 |  | 159 | 161 | 0.05336 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
162 | MV_98_0_line_162 |  | 161 | 162 | 0.16949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_98_0_line_163 |  | 162 | 163 | 0.24495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_98_0_line_164 |  | 163 | 164 | 0.020385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_98_0_line_165 |  | 164 | 165 | 0.030729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_98_0_trafo_177 | 25 MVA 110/20 kV | 167 | 24 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2612844.8657 | 1186440.0847
1 | 2612935.9994 | 1187555.2344
2 | 2610695.1642 | 1188161.6305
3 | 2610596.5244 | 1187662.0404
4 | 2610568.3349 | 1187741.8436
5 | 2610504.4906 | 1187612.6313
6 | 2610601.7435 | 1188142.2552
7 | 2610511.1815 | 1188123.4757
8 | 2609965.3994 | 1187791.4977
9 | 2610399.9957 | 1188876.2864
10 | 2610548.8474 | 1188131.2863
11 | 2610089.8862 | 1188099.7765
12 | 2609944.9479 | 1187810.1848
13 | 2610702.2253 | 1188767.8258
14 | 2610343.4652 | 1188987.6361
15 | 2610604.8973 | 1188928.3486
16 | 2610735.6818 | 1188624.0548
17 | 2610659.7765 | 1188964.4198
18 | 2610134.8247 | 1188111.5024
19 | 2609937.3836 | 1187808.4603
20 | 2610324.9261 | 1189022.4336
21 | 2609726.3683 | 1190102.5578
22 | 2609615.6846 | 1190424.7044
23 | 2609668.8159 | 1190062.9744
24 | 2609605.8982 | 1190422.2431
25 | 2609617.9274 | 1190505.1724
26 | 2609726.8349 | 1190569.0696
27 | 2609782.4723 | 1190573.5509
28 | 2609519.8171 | 1190638.1054
29 | 2609714.5313 | 1190520.2241
30 | 2609582.3908 | 1190599.5764
31 | 2609580.8189 | 1190609.8666
32 | 2609514.3751 | 1190668.4696
33 | 2609855.8891 | 1187698.2358
34 | 2609898.0359 | 1187763.0275
35 | 2609844.4711 | 1187678.6181
36 | 2609905.2241 | 1187771.4601
37 | 2609709.0804 | 1187848.6821
38 | 2609917.4063 | 1187363.0846
39 | 2609914.1108 | 1187316.6217
40 | 2609921.89 | 1187781.1873
41 | 2609708.6927 | 1187853.0604
42 | 2609825.1971 | 1187269.8963
43 | 2609649.1283 | 1187428.6723
44 | 2609551.2152 | 1187076.878
45 | 2609591.2399 | 1186984.2156
46 | 2609612.9715 | 1187431.5493
47 | 2608679.1086 | 1187623.9222
48 | 2608047.9239 | 1187712.3825
49 | 2608058.3698 | 1187704.5591
50 | 2607777.1532 | 1187337.1217
51 | 2608554.4884 | 1187620.498
52 | 2607778.3229 | 1187364.7153
53 | 2607522.4972 | 1186436.9545
54 | 2605974.432 | 1187862.445
55 | 2608954.6135 | 1186279.4824
56 | 2609317.8221 | 1191044.8728
57 | 2609380.6605 | 1191053.9417
58 | 2609021.0792 | 1191279.211
59 | 2609005.1995 | 1190865.6259
60 | 2609439.2304 | 1191252.0926
61 | 2609534.4705 | 1190936.5214
62 | 2608904.5316 | 1191111.3163
63 | 2608827.5481 | 1191270.52
64 | 2608873.9142 | 1191100.6989
65 | 2608978.1226 | 1190852.3786
66 | 2608892.9707 | 1190741.3497
67 | 2608922.0396 | 1190712.4887
68 | 2609004.6564 | 1191331.0914
69 | 2609441.0037 | 1191322.1322
70 | 2609530.8385 | 1190923.9091
71 | 2609726.7622 | 1191001.2071
72 | 2609523.0714 | 1190922.6628
73 | 2609736.9604 | 1190988.8171
74 | 2609365.8284 | 1191482.7214
75 | 2609318.0405 | 1191455.7109
76 | 2609401.7018 | 1191441.9433
77 | 2609217.5308 | 1191396.7477
78 | 2609402.3359 | 1191420.1121
79 | 2609449.3045 | 1191483.3632
80 | 2609446.5526 | 1191476.4619
81 | 2609657.2207 | 1191601.5327
82 | 2609815.1222 | 1191910.528
83 | 2609368.6966 | 1191697.2386
84 | 2609283.3111 | 1191780.0277
85 | 2609413.1963 | 1191714.7838
86 | 2609100.4644 | 1191637.125
87 | 2609230.8684 | 1191359.3373
88 | 2609264.161 | 1191364.2021
89 | 2609137.3559 | 1191435.4126
90 | 2609214.1553 | 1191391.9148
91 | 2609124.6434 | 1191443.0973
92 | 2609436.6865 | 1191440.6341
93 | 2609691.1715 | 1191584.7895
94 | 2609759.8362 | 1191574.6728
95 | 2609647.3482 | 1191596.9922
96 | 2610205.544 | 1191988.2178
97 | 2609877.7501 | 1192144.1311
98 | 2609848.87 | 1191835.288
99 | 2609898.1371 | 1192174.0803
100 | 2609382.912 | 1191815.8897
101 | 2609072.8269 | 1191584.4378
102 | 2609062.2666 | 1191632.1777
103 | 2609102.3908 | 1191518.4699
104 | 2609061.4671 | 1191635.7921
105 | 2609077.5318 | 1191639.2514
106 | 2609434.8428 | 1191420.0517
107 | 2610249.6237 | 1191900.5354
108 | 2611253.461 | 1191635.044
109 | 2609202.4295 | 1191391.1105
110 | 2609376.3553 | 1191845.8508
111 | 2609408.1952 | 1191851.6146
112 | 2609469.1201 | 1191889.2409
113 | 2609437.2864 | 1191918.5953
114 | 2609217.4887 | 1192266.2046
115 | 2609446.8265 | 1192047.3891
116 | 2609494.3787 | 1191906.2563
117 | 2608874.9302 | 1191290.9113
118 | 2608674.3281 | 1190786.9885
119 | 2608654.8691 | 1190804.0028
120 | 2608507.5486 | 1191022.2409
121 | 2608356.5218 | 1191361.208
122 | 2608465.2965 | 1191065.3263
123 | 2608342.2384 | 1191433.7593
124 | 2609253.7104 | 1190802.4358
125 | 2609301.4433 | 1190819.2291
126 | 2609158.9859 | 1190701.8161
127 | 2609257.6802 | 1190724.6233
128 | 2609128.3832 | 1190700.5802
129 | 2608866.5863 | 1191288.1087
130 | 2609259.8622 | 1190679.0806
131 | 2609483.5568 | 1192006.2029
132 | 2609255.9755 | 1192280.5155
133 | 2608709.1021 | 1192159.159
134 | 2608650.3787 | 1192333.5773
135 | 2609499.0161 | 1191909.3874
136 | 2609519.423 | 1191865.9024
137 | 2609589.3894 | 1192160.9851
138 | 2609527.6651 | 1192120.1324
139 | 2607920.9047 | 1191976.4876
140 | 2607911.9236 | 1192000.7663
141 | 2608412.8321 | 1191630.6607
142 | 2608475.1052 | 1192190.1864
143 | 2608455.8538 | 1191568.377
144 | 2608483.7552 | 1192180.4823
145 | 2609018.7458 | 1193087.2141
146 | 2608599.4222 | 1191447.2164
147 | 2608611.0628 | 1191404.8775
148 | 2608869.7738 | 1191427.3976
149 | 2608871.8392 | 1191407.1122
150 | 2611186.853 | 1191620.4122
151 | 2610228.7676 | 1191213.9725
152 | 2610246.2919 | 1191157.4615
153 | 2609499.1457 | 1190759.1088
154 | 2609493.0035 | 1190796.5082
155 | 2609261.5705 | 1190594.5
156 | 2609471.9788 | 1190929.3858
157 | 2610117.5362 | 1191354.4473
158 | 2610171.4787 | 1191369.4571
159 | 2609917.27 | 1191290.0804
160 | 2610111.2656 | 1191138.9236
161 | 2609868.2458 | 1191269.0111
162 | 2609798.8327 | 1191422.9231
163 | 2609775.0263 | 1191252.6283
164 | 2609785.2207 | 1191234.976
165 | 2609811.9078 | 1191250.2094
166 | 2609127.8483 | 1191528.914
167 | 2609605.8982 | 1190422.2431

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99479 | -0.05331 | 0.23646 | 0.11452
1 | 0.99531 | -0.050018 | 0.17055 | 0.082601
2 | 0.99714 | -0.037977 | 0.36214 | 0.17539
3 | 0.99697 | -0.04596 | 0.26142 | 0.12661
4 | 0.99704 | -0.044572 | 0 | 0
5 | 0.99689 | -0.047557 | 0 | 0
6 | 0.99728 | -0.037052 | 0 | 0
7 | 0.99738 | -0.037911 | 0 | 0
8 | 0.99621 | -0.060488 | 0 | 0
9 | 0.99816 | -0.022172 | 0 | 0
10 | 0.99733 | -0.037536 | 0.07206 | 0.0349
11 | 0.996 | -0.06189 | 0 | 0
12 | 0.99617 | -0.06204 | 0 | 0
13 | 0.99784 | -0.019525 | 0 | 0
14 | 0.99849 | -0.010475 | 0.23027 | 0.11153
15 | 0.99765 | -0.017813 | 0 | 0
16 | 0.99777 | -0.019989 | 0.2582 | 0.12505
17 | 0.99761 | -0.017497 | 0.39561 | 0.1916
18 | 0.99598 | -0.061703 | 0.33707 | 0.16325
19 | 0.99616 | -0.062144 | 0.17033 | 0.082495
20 | 0.99852 | -0.010259 | 0 | 0
21 | 0.99965 | -0.0025932 | 0 | 0
22 | 0.99997 | -0.00020688 | 0 | 0
23 | 0.99965 | -0.002522 | 0.073246 | 0.035475
24 | 1 | 0 | -20.4727 | -8.7437
25 | 0.99973 | -0.0015395 | 0 | 0
26 | 0.99889 | -0.023192 | 0 | 0
27 | 0.99885 | -0.02282 | 0.5419 | 0.26246
28 | 0.99912 | -0.021732 | 0.077294 | 0.037435
29 | 0.9997 | -0.0011982 | 0.29869 | 0.14466
30 | 0.99946 | -0.0031165 | 0 | 0
31 | 0.99943 | -0.0032534 | 0.13434 | 0.065062
32 | 0.99905 | -0.022124 | 0.072449 | 0.035088
33 | 0.99605 | -0.065009 | 0.37046 | 0.17942
34 | 0.9961 | -0.064198 | 0 | 0
35 | 0.99603 | -0.065854 | 0 | 0
36 | 0.9961 | -0.064063 | 0.152 | 0.073619
37 | 0.99592 | -0.065301 | 0.28335 | 0.13723
38 | 0.9956 | -0.071158 | 0 | 0
39 | 0.99554 | -0.071809 | 0.33284 | 0.1612
40 | 0.99612 | -0.063812 | 0 | 0
41 | 0.99592 | -0.065293 | 0.15175 | 0.073497
42 | 0.99533 | -0.077495 | 0 | 0
43 | 0.99419 | -0.068853 | 0 | 0
44 | 0.99412 | -0.068391 | 0 | 0
45 | 0.9941 | -0.068244 | 0.12672 | 0.061375
46 | 0.99411 | -0.068233 | 0.40373 | 0.19554
47 | 0.99176 | -0.087494 | 0.23313 | 0.11291
48 | 0.99016 | -0.075023 | 0.37165 | 0.18
49 | 0.99017 | -0.075082 | 0 | 0
50 | 0.98955 | -0.069844 | 0 | 0
51 | 0.99159 | -0.086296 | 0 | 0
52 | 0.98954 | -0.069716 | 0.27715 | 0.13423
53 | 0.98901 | -0.0735 | 0.12699 | 0.061506
54 | 0.98917 | -0.072253 | 0.10214 | 0.049467
55 | 0.98852 | -0.076702 | 0.17388 | 0.084213
56 | 0.99743 | -0.044347 | 0.34459 | 0.16689
57 | 0.99767 | -0.03013 | 0 | 0
58 | 0.99613 | -0.12206 | 0.32121 | 0.15557
59 | 0.99699 | -0.047406 | 0.29601 | 0.14336
60 | 0.99753 | -0.028925 | 0 | 0
61 | 0.99835 | -0.026227 | 0 | 0
62 | 0.99534 | -0.11647 | 0 | 0
63 | 0.99541 | -0.11707 | 0 | 0
64 | 0.99533 | -0.11636 | 0.27647 | 0.1339
65 | 0.99697 | -0.047295 | 0 | 0
66 | 0.99684 | -0.046112 | 0 | 0
67 | 0.99681 | -0.046284 | 0.34514 | 0.16716
68 | 0.99604 | -0.12261 | 0 | 0
69 | 0.9975 | -0.028616 | 0.37005 | 0.17922
70 | 0.99837 | -0.026064 | 0.32024 | 0.1551
71 | 0.99831 | -0.025932 | 0 | 0
72 | 0.99839 | -0.02597 | 0 | 0
73 | 0.99831 | -0.025907 | 0.12775 | 0.061871
74 | 0.99565 | -0.12527 | 0.37628 | 0.18224
75 | 0.99569 | -0.12505 | 0 | 0
76 | 0.9956 | -0.12885 | 0.10035 | 0.048602
77 | 0.99577 | -0.12452 | 0 | 0
78 | 0.99558 | -0.12893 | 0 | 0
79 | 0.99553 | -0.12928 | 0 | 0
80 | 0.99554 | -0.12925 | 0.32035 | 0.15515
81 | 0.99549 | -0.1295 | 0 | 0
82 | 0.99527 | -0.13106 | 0 | 0
83 | 0.99538 | -0.13828 | 0 | 0
84 | 0.99542 | -0.13798 | 0 | 0
85 | 0.99536 | -0.13837 | 0.36278 | 0.1757
86 | 0.99557 | -0.12911 | 0.18993 | 0.091988
87 | 0.99576 | -0.12452 | 0 | 0
88 | 0.99576 | -0.12452 | 0.092548 | 0.044823
89 | 0.9957 | -0.12496 | 0 | 0
90 | 0.99577 | -0.12447 | 0.077552 | 0.03756
91 | 0.99569 | -0.12501 | 0.40357 | 0.19546
92 | 0.99556 | -0.12912 | 0.085368 | 0.041345
93 | 0.99547 | -0.12937 | 0 | 0
94 | 0.99545 | -0.12919 | 0.22402 | 0.1085
95 | 0.99548 | -0.12947 | 0.24189 | 0.11715
96 | 0.99511 | -0.1319 | 0 | 0
97 | 0.99511 | -0.12971 | 0 | 0
98 | 0.99525 | -0.13159 | 0.389 | 0.1884
99 | 0.9951 | -0.12956 | 0.33773 | 0.16357
100 | 0.99531 | -0.14166 | 0.25643 | 0.12419
101 | 0.9956 | -0.12889 | 0 | 0
102 | 0.99558 | -0.129 | 0.12148 | 0.058836
103 | 0.99563 | -0.12871 | 0 | 0
104 | 0.99558 | -0.12901 | 0 | 0
105 | 0.99558 | -0.12905 | 0 | 0
106 | 0.99557 | -0.12904 | 0 | 0
107 | 0.9951 | -0.13232 | 0.26249 | 0.12713
108 | 0.99434 | -0.15821 | 0.17358 | 0.084067
109 | 0.99579 | -0.12437 | 0 | 0
110 | 0.9953 | -0.14171 | 0 | 0
111 | 0.9953 | -0.14176 | 0 | 0
112 | 0.99527 | -0.14363 | 0.2218 | 0.10742
113 | 0.99523 | -0.14338 | 0 | 0
114 | 0.99494 | -0.14096 | 0 | 0
115 | 0.99514 | -0.14254 | 0 | 0
116 | 0.99527 | -0.14366 | 0 | 0
117 | 0.99543 | -0.11724 | 0 | 0
118 | 0.99216 | -0.11893 | 0.34704 | 0.16808
119 | 0.99217 | -0.11904 | 0 | 0
120 | 0.99229 | -0.12009 | 0 | 0
121 | 0.99274 | -0.11704 | 0.35059 | 0.1698
122 | 0.99233 | -0.1198 | 0.31749 | 0.15377
123 | 0.99285 | -0.11802 | 0 | 0
124 | 0.99835 | -0.025687 | 0 | 0
125 | 0.99841 | -0.026184 | 0.13427 | 0.065031
126 | 0.99826 | -0.024848 | 0 | 0
127 | 0.9983 | -0.025195 | 0 | 0
128 | 0.99825 | -0.024739 | 0.30089 | 0.14573
129 | 0.99542 | -0.11719 | 0.22847 | 0.11065
130 | 0.99825 | -0.025489 | 0.29149 | 0.14118
131 | 0.99512 | -0.14236 | 0.26254 | 0.12715
132 | 0.99492 | -0.14078 | 0.35782 | 0.1733
133 | 0.98984 | -0.12053 | 0.37699 | 0.18259
134 | 0.98997 | -0.11967 | 0.25991 | 0.12588
135 | 0.99526 | -0.14366 | 0 | 0
136 | 0.99526 | -0.14361 | 0.088946 | 0.043078
137 | 0.99523 | -0.14394 | 0 | 0
138 | 0.99521 | -0.14443 | 0.40518 | 0.19624
139 | 0.99134 | -0.12626 | 0.075654 | 0.036641
140 | 0.9913 | -0.12594 | 0 | 0
141 | 0.99269 | -0.11672 | 0.30772 | 0.14904
142 | 0.99037 | -0.11744 | 0 | 0
143 | 0.99283 | -0.11797 | 0 | 0
144 | 0.99035 | -0.11727 | 0.23226 | 0.11249
145 | 0.98962 | -0.12191 | 0.21328 | 0.1033
146 | 0.99321 | -0.12129 | 0 | 0
147 | 0.99318 | -0.12148 | 0.35154 | 0.17026
148 | 0.9947 | -0.11091 | 0.21502 | 0.10414
149 | 0.99478 | -0.11161 | 0 | 0
150 | 0.99432 | -0.15855 | 0 | 0
151 | 0.99368 | -0.18021 | 0 | 0
152 | 0.99366 | -0.1805 | 0.32632 | 0.15805
153 | 0.99885 | -0.023285 | 0.085641 | 0.041478
154 | 0.99877 | -0.023759 | 0.11794 | 0.057121
155 | 0.99821 | -0.025736 | 0.23961 | 0.11605
156 | 0.9985 | -0.025339 | 0 | 0
157 | 0.99348 | -0.18643 | 0.33962 | 0.16448
158 | 0.99349 | -0.18623 | 0 | 0
159 | 0.99342 | -0.18844 | 0.28785 | 0.13941
160 | 0.9936 | -0.18258 | 0 | 0
161 | 0.9934 | -0.1889 | 0 | 0
162 | 0.99334 | -0.18843 | 0 | 0
163 | 0.99326 | -0.18767 | 0 | 0
164 | 0.99325 | -0.18761 | 0.20696 | 0.10024
165 | 0.99325 | -0.18758 | 0.069959 | 0.033883
166 | 0.99563 | -0.12871 | 0.14572 | 0.070576
167 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.23646 | -0.11452 | 0.23657 | 0.11327 | 0.00011562 | -0.0012501 | 0.007624 | 0.0076073 | 0.007624 | 0.99479 | -0.05331 | 0.99531 | -0.050018 | 3.6305
1 | -0.40712 | -0.19587 | 0.40783 | 0.19356 | 0.00070831 | -0.0023068 | 0.013104 | 0.013069 | 0.013104 | 0.99531 | -0.050018 | 0.99714 | -0.037977 | 6.2398
2 | -0.76997 | -0.36896 | 0.77007 | 0.36891 | 0.00010385 | -4.8214e-05 | 0.024718 | 0.024717 | 0.024718 | 0.99714 | -0.037977 | 0.99728 | -0.037052 | 11.7705
3 | -3.8865 | -1.7083 | 3.8868 | 1.702 | 0.0002342 | -0.0062212 | 0.12293 | 0.12285 | 0.12293 | 0.99697 | -0.04596 | 0.99704 | -0.044572 | 14.5993
4 | 3.6251 | 1.5816 | -3.6249 | -1.5893 | 0.00025036 | -0.0076846 | 0.11452 | 0.11461 | 0.11461 | 0.99697 | -0.04596 | 0.99689 | -0.047557 | 13.6121
5 | -3.8868 | -1.702 | 3.8879 | 1.6724 | 0.0011096 | -0.029595 | 0.12285 | 0.1225 | 0.12285 | 0.99704 | -0.044572 | 0.99738 | -0.037911 | 14.5904
6 | 3.6249 | 1.5893 | -3.6228 | -1.6528 | 0.0020854 | -0.063469 | 0.11461 | 0.11539 | 0.11539 | 0.99689 | -0.047557 | 0.99621 | -0.060488 | 13.7039
7 | -0.77007 | -0.36891 | 0.77012 | 0.36764 | 4.4029e-05 | -0.0012698 | 0.024717 | 0.024701 | 0.024717 | 0.99728 | -0.037052 | 0.99733 | -0.037536 | 11.2348
8 | -4.7301 | -2.0741 | 4.7333 | 2.0176 | 0.0031768 | -0.056443 | 0.14949 | 0.14881 | 0.14949 | 0.99738 | -0.037911 | 0.99816 | -0.022172 | 17.754
9 | 0.84222 | 0.40164 | -0.84218 | -0.40254 | 3.7471e-05 | -0.00090248 | 0.027007 | 0.027018 | 0.027018 | 0.99738 | -0.037911 | 0.99733 | -0.037536 | 12.2809
10 | 0.33714 | 0.1618 | -0.33708 | -0.16215 | 6.959e-05 | -0.00035022 | 0.010836 | 0.010841 | 0.010841 | 0.99621 | -0.060488 | 0.996 | -0.06189 | 5.1625
11 | 3.2856 | 1.491 | -3.2855 | -1.4909 | 0.00010793 | 8.5094e-05 | 0.10455 | 0.10455 | 0.10455 | 0.99621 | -0.060488 | 0.99617 | -0.06204 | 12.7505
12 | 0.65416 | 0.29646 | -0.65394 | -0.30558 | 0.0002238 | -0.0091254 | 0.020771 | 0.020882 | 0.020882 | 0.99816 | -0.022172 | 0.99784 | -0.019525 | 9.4918
13 | -5.3874 | -2.3141 | 5.3887 | 2.3156 | 0.0012798 | 0.0015307 | 0.16957 | 0.16957 | 0.16957 | 0.99816 | -0.022172 | 0.99849 | -0.010475 | 20.6796
14 | 0.33708 | 0.16215 | -0.33707 | -0.16325 | 7.2779e-06 | -0.001095 | 0.010841 | 0.010855 | 0.010855 | 0.996 | -0.06189 | 0.99598 | -0.061703 | 4.9341
15 | 3.2855 | 1.4909 | -3.2855 | -1.4915 | 1.5479e-05 | -0.0005724 | 0.10455 | 0.10456 | 0.10456 | 0.99617 | -0.06204 | 0.99616 | -0.062144 | 12.4182
16 | 0.39571 | 0.18069 | -0.39563 | -0.19001 | 8.3884e-05 | -0.0093203 | 0.012585 | 0.0127 | 0.0127 | 0.99784 | -0.019525 | 0.99765 | -0.017813 | 5.7726
17 | 0.25822 | 0.12489 | -0.2582 | -0.12505 | 1.8115e-05 | -0.0001641 | 0.0082982 | 0.0083004 | 0.0083004 | 0.99784 | -0.019525 | 0.99777 | -0.019989 | 3.9526
18 | -5.619 | -2.4272 | 5.6192 | 2.4223 | 0.00019066 | -0.0048315 | 0.17696 | 0.1769 | 0.17696 | 0.99849 | -0.010475 | 0.99852 | -0.010259 | 13.8683
19 | 0.39563 | 0.19001 | -0.39561 | -0.1916 | 1.4479e-05 | -0.0015912 | 0.0127 | 0.01272 | 0.01272 | 0.99765 | -0.017813 | 0.99761 | -0.017497 | 5.7817
20 | 3.1152 | 1.409 | -3.1151 | -1.4089 | 0.00010974 | 7.8312e-05 | 0.099078 | 0.099079 | 0.099079 | 0.99616 | -0.062144 | 0.99612 | -0.063812 | 12.0828
21 | -5.6192 | -2.4223 | 5.6252 | 2.2672 | 0.0060471 | -0.15507 | 0.1769 | 0.17514 | 0.1769 | 0.99852 | -0.010259 | 0.99965 | -0.0025932 | 13.8639
22 | -5.6985 | -2.3006 | 5.7002 | 2.2579 | 0.0016872 | -0.042725 | 0.17746 | 0.17699 | 0.17746 | 0.99965 | -0.0025932 | 0.99997 | -0.00020688 | 13.9077
23 | 0.073247 | 0.033378 | -0.073246 | -0.035475 | 6.4085e-07 | -0.0020966 | 0.0023244 | 0.0023502 | 0.0023502 | 0.99965 | -0.0025932 | 0.99965 | -0.002522 | 1.0683
24 | -20.458 | -8.7341 | 20.4587 | 8.7332 | 0.00064118 | -0.00090358 | 0.64216 | 0.64215 | 0.64216 | 0.99997 | -0.00020688 | 1 | 0 | 50.3263
25 | 14.7579 | 6.4762 | -14.7546 | -6.4868 | 0.0033054 | -0.010551 | 0.46525 | 0.4654 | 0.4654 | 0.99997 | -0.00020688 | 0.99973 | -0.0015395 | 36.4732
26 | 0.2987 | 0.14234 | -0.29869 | -0.14466 | 1.1917e-05 | -0.0023229 | 0.0095544 | 0.0095835 | 0.0095835 | 0.99973 | -0.0015395 | 0.9997 | -0.0011982 | 4.3561
27 | 14.4559 | 6.3444 | -14.452 | -6.3572 | 0.0038362 | -0.012837 | 0.45585 | 0.45602 | 0.45602 | 0.99973 | -0.0015395 | 0.99946 | -0.0031165 | 35.7384
28 | 0.54193 | 0.26109 | -0.5419 | -0.26246 | 2.3228e-05 | -0.0013632 | 0.017384 | 0.017402 | 0.017402 | 0.99889 | -0.023192 | 0.99885 | -0.02282 | 7.9098
29 | -0.54193 | -0.26109 | 0.54204 | 0.26091 | 0.00011748 | -0.00018641 | 0.017384 | 0.017381 | 0.017384 | 0.99889 | -0.023192 | 0.99912 | -0.021732 | 8.2782
30 | 13.6956 | 5.9886 | -13.6947 | -5.9919 | 0.00088906 | -0.0033687 | 0.43188 | 0.43193 | 0.43193 | 0.99912 | -0.021732 | 0.99905 | -0.022124 | 33.85
31 | -14.3149 | -6.2869 | 14.3174 | 6.2933 | 0.0024485 | 0.0063986 | 0.45173 | 0.45173 | 0.45173 | 0.99912 | -0.021732 | 0.99943 | -0.0032534 | 35.0179
32 | 14.452 | 6.3572 | -14.4517 | -6.3584 | 0.00033447 | -0.0011183 | 0.45602 | 0.45604 | 0.45604 | 0.99946 | -0.0031165 | 0.99943 | -0.0032534 | 35.7396
33 | 13.6222 | 5.9568 | -13.6196 | -5.9669 | 0.0026216 | -0.010049 | 0.4296 | 0.42974 | 0.42974 | 0.99905 | -0.022124 | 0.99885 | -0.023285 | 33.6784
34 | -2.5278 | -1.1329 | 2.5278 | 1.1271 | 9.1151e-05 | -0.0057799 | 0.080281 | 0.080211 | 0.080281 | 0.99605 | -0.065009 | 0.9961 | -0.064198 | 9.5345
35 | 2.1573 | 0.95351 | -2.1573 | -0.95351 | 3.7802e-05 | -3.5654e-06 | 0.068357 | 0.068358 | 0.068358 | 0.99605 | -0.065009 | 0.99603 | -0.065854 | 8.3363
36 | -2.963 | -1.3376 | 2.963 | 1.3368 | 1.7997e-05 | -0.00082348 | 0.094214 | 0.094204 | 0.094214 | 0.9961 | -0.064198 | 0.9961 | -0.064063 | 11.1893
37 | 0.43517 | 0.21042 | -0.4351 | -0.21062 | 7.2554e-05 | -0.00020025 | 0.014009 | 0.014012 | 0.014012 | 0.9961 | -0.064198 | 0.99592 | -0.065301 | 6.6722
38 | 2.1573 | 0.95351 | -2.1564 | -0.96566 | 0.00084885 | -0.01215 | 0.068358 | 0.068508 | 0.068508 | 0.99603 | -0.065854 | 0.9956 | -0.071158 | 18.925
39 | -3.115 | -1.4104 | 3.1151 | 1.4089 | 3.5335e-05 | -0.0014584 | 0.099097 | 0.099079 | 0.099097 | 0.9961 | -0.064063 | 0.99612 | -0.063812 | 11.7693
40 | 0.15175 | 0.073393 | -0.15175 | -0.073497 | 1.4011e-07 | -0.00010405 | 0.0048861 | 0.0048874 | 0.0048874 | 0.99592 | -0.065301 | 0.99592 | -0.065293 | 2.2216
41 | 2.1564 | 0.96566 | -2.1563 | -0.96717 | 0.00010564 | -0.0015074 | 0.068508 | 0.068527 | 0.068527 | 0.9956 | -0.071158 | 0.99554 | -0.071809 | 18.9302
42 | 1.8235 | 0.80597 | -1.8231 | -0.80574 | 0.00030815 | 0.00022739 | 0.057809 | 0.05781 | 0.05781 | 0.99554 | -0.071809 | 0.99533 | -0.077495 | 16.5173
43 | 1.8231 | 0.80574 | -1.8209 | -0.81678 | 0.0022155 | -0.011047 | 0.05781 | 0.057949 | 0.057949 | 0.99533 | -0.077495 | 0.99419 | -0.068853 | 26.3403
44 | 1.6942 | 0.76825 | -1.6941 | -0.76906 | 0.00014089 | -0.00081164 | 0.054015 | 0.054025 | 0.054025 | 0.99419 | -0.068853 | 0.99411 | -0.068233 | 24.5568
45 | 0.12674 | 0.048532 | -0.12673 | -0.058994 | 9.4603e-06 | -0.010462 | 0.0039405 | 0.0040591 | 0.0040591 | 0.99419 | -0.068853 | 0.99412 | -0.068391 | 1.8451
46 | 0.12673 | 0.058994 | -0.12672 | -0.061375 | 2.2366e-06 | -0.0023813 | 0.0040591 | 0.0040888 | 0.0040888 | 0.99412 | -0.068391 | 0.9941 | -0.068244 | 1.8585
47 | 1.2903 | 0.57353 | -1.2875 | -0.57286 | 0.0028571 | 0.00066738 | 0.041004 | 0.041017 | 0.041017 | 0.99411 | -0.068233 | 0.99176 | -0.087494 | 19.5319
48 | 1.0543 | 0.45995 | -1.0542 | -0.46282 | 0.00018623 | -0.0028635 | 0.033482 | 0.033516 | 0.033516 | 0.99176 | -0.087494 | 0.99159 | -0.086296 | 15.2347
49 | -0.37165 | -0.18 | 0.37166 | 0.1797 | 2.5203e-06 | -0.00030425 | 0.012039 | 0.012035 | 0.012039 | 0.99016 | -0.075023 | 0.99017 | -0.075082 | 5.4724
50 | 0.68089 | 0.30755 | -0.68044 | -0.32396 | 0.00045209 | -0.016411 | 0.021782 | 0.021985 | 0.021985 | 0.99017 | -0.075082 | 0.98955 | -0.069844 | 9.9931
51 | -1.0525 | -0.48725 | 1.0542 | 0.46282 | 0.0016073 | -0.024429 | 0.033815 | 0.033516 | 0.033815 | 0.99017 | -0.075082 | 0.99159 | -0.086296 | 15.3702
52 | 0.37933 | 0.18087 | -0.37932 | -0.18153 | 5.7382e-06 | -0.00066649 | 0.012259 | 0.012268 | 0.012268 | 0.98955 | -0.069844 | 0.98954 | -0.069716 | 5.5762
53 | 0.30111 | 0.14309 | -0.30095 | -0.14409 | 0.00015788 | -0.0009941 | 0.0097255 | 0.0097393 | 0.0097393 | 0.98955 | -0.069844 | 0.98901 | -0.0735 | 4.6377
54 | 0.10217 | 0.047303 | -0.10214 | -0.049467 | 3.6268e-05 | -0.0021639 | 0.0032846 | 0.0033119 | 0.0033119 | 0.98954 | -0.069716 | 0.98917 | -0.072253 | 1.5771
55 | 0.17396 | 0.082582 | -0.17388 | -0.084213 | 8.1402e-05 | -0.0016305 | 0.0056207 | 0.0056419 | 0.0056419 | 0.98901 | -0.0735 | 0.98852 | -0.076702 | 2.6866
56 | -11.6158 | -5.0915 | 11.6174 | 5.0954 | 0.0015269 | 0.0039313 | 0.36706 | 0.36706 | 0.36706 | 0.99743 | -0.044347 | 0.99767 | -0.03013 | 28.4543
57 | 10.6298 | 4.6222 | -10.6222 | -4.6028 | 0.0075961 | 0.019388 | 0.33547 | 0.33548 | 0.33548 | 0.99743 | -0.044347 | 0.99613 | -0.12206 | 26.0065
58 | 0.64149 | 0.30237 | -0.64122 | -0.30262 | 0.00027055 | -0.00025834 | 0.020525 | 0.02053 | 0.02053 | 0.99743 | -0.044347 | 0.99699 | -0.047406 | 9.7763
59 | 0.37012 | 0.17062 | -0.37007 | -0.17756 | 5.473e-05 | -0.0069385 | 0.011793 | 0.011878 | 0.011878 | 0.99767 | -0.03013 | 0.99753 | -0.028925 | 5.3992
60 | -11.9875 | -5.266 | 11.9952 | 5.2266 | 0.0077496 | -0.039437 | 0.37885 | 0.37834 | 0.37885 | 0.99767 | -0.03013 | 0.99835 | -0.026227 | 29.6904
61 | 10.301 | 4.4473 | -10.3001 | -4.4536 | 0.00088904 | -0.006284 | 0.32515 | 0.32523 | 0.32523 | 0.99613 | -0.12206 | 0.99604 | -0.12261 | 25.4881
62 | 0.34521 | 0.15926 | -0.3452 | -0.15997 | 4.8688e-06 | -0.00071227 | 0.011008 | 0.011017 | 0.011017 | 0.99699 | -0.047406 | 0.99697 | -0.047295 | 5.0075
63 | 0.37007 | 0.17756 | -0.37005 | -0.17922 | 1.3237e-05 | -0.0016627 | 0.011878 | 0.011899 | 0.011899 | 0.99753 | -0.028925 | 0.9975 | -0.028616 | 5.4087
64 | -12.123 | -5.2829 | 12.1233 | 5.2812 | 0.00032297 | -0.001609 | 0.38238 | 0.38236 | 0.38238 | 0.99835 | -0.026227 | 0.99837 | -0.026064 | 29.9669
65 | 0.12775 | 0.056247 | -0.12775 | -0.061483 | 4.8612e-06 | -0.0052365 | 0.0040362 | 0.0040996 | 0.0040996 | 0.99835 | -0.026227 | 0.99831 | -0.025932 | 1.8634
66 | -0.27648 | -0.13314 | 0.2765 | 0.12864 | 2.0002e-05 | -0.0044971 | 0.0088998 | 0.0088439 | 0.0088998 | 0.99534 | -0.11647 | 0.99541 | -0.11707 | 4.0454
67 | 0.27648 | 0.13314 | -0.27647 | -0.1339 | 3.4216e-06 | -0.00076355 | 0.0088998 | 0.0089095 | 0.0089095 | 0.99534 | -0.11647 | 0.99533 | -0.11636 | 4.0498
68 | -0.2765 | -0.12864 | 0.2765 | 0.12763 | 4.4541e-06 | -0.0010092 | 0.0088439 | 0.0088316 | 0.0088439 | 0.99541 | -0.11707 | 0.99542 | -0.11719 | 4.02
69 | 0.3452 | 0.15997 | -0.34515 | -0.16712 | 4.928e-05 | -0.0071454 | 0.011017 | 0.011105 | 0.011105 | 0.99697 | -0.047295 | 0.99684 | -0.046112 | 5.0479
70 | 0.34515 | 0.16712 | -0.34514 | -0.16716 | 9.0014e-06 | -4.2954e-05 | 0.011105 | 0.011106 | 0.011106 | 0.99684 | -0.046112 | 0.99681 | -0.046284 | 5.2885
71 | 3.566 | 1.6707 | -3.5636 | -1.6732 | 0.0023626 | -0.0025143 | 0.11413 | 0.11417 | 0.11417 | 0.99604 | -0.12261 | 0.99543 | -0.11724 | 51.8957
72 | 6.7341 | 2.7829 | -6.7324 | -2.8116 | 0.0016413 | -0.028721 | 0.21118 | 0.21151 | 0.21151 | 0.99604 | -0.12261 | 0.99579 | -0.12437 | 16.5757
73 | -12.4435 | -5.4363 | 12.4437 | 5.4354 | 0.00019159 | -0.00089969 | 0.39264 | 0.39263 | 0.39264 | 0.99837 | -0.026064 | 0.99839 | -0.02597 | 30.7709
74 | 0.12775 | 0.061483 | -0.12775 | -0.061871 | 3.667e-07 | -0.00038833 | 0.0040996 | 0.0041045 | 0.0041045 | 0.99831 | -0.025932 | 0.99831 | -0.025907 | 1.8657
75 | -12.4437 | -5.4354 | 12.445 | 5.4294 | 0.0012898 | -0.0060594 | 0.39263 | 0.39255 | 0.39263 | 0.99839 | -0.02597 | 0.9985 | -0.025339 | 30.77
76 | -3.7446 | -1.579 | 3.7447 | 1.5722 | 0.00011748 | -0.0067613 | 0.11783 | 0.11775 | 0.11783 | 0.99565 | -0.12527 | 0.99569 | -0.12505 | 9.2341
77 | 3.3683 | 1.3967 | -3.3682 | -1.3966 | 0.00010836 | 0.00014256 | 0.10572 | 0.10573 | 0.10573 | 0.99565 | -0.12527 | 0.9956 | -0.12885 | 8.1958
78 | -3.7447 | -1.5722 | 3.745 | 1.5559 | 0.00028313 | -0.016334 | 0.11775 | 0.11757 | 0.11775 | 0.99569 | -0.12505 | 0.99577 | -0.12452 | 9.2281
79 | 3.2679 | 1.348 | -3.2679 | -1.3507 | 3.5461e-05 | -0.0027004 | 0.1025 | 0.10253 | 0.10253 | 0.9956 | -0.12885 | 0.99558 | -0.12893 | 8.0351
80 | 2.8172 | 1.1864 | -2.817 | -1.2055 | 0.00018754 | -0.019107 | 0.088616 | 0.088834 | 0.088834 | 0.99577 | -0.12452 | 0.9957 | -0.12496 | 6.9619
81 | -6.6547 | -2.7765 | 6.6548 | 2.7758 | 3.9797e-05 | -0.00071212 | 0.20904 | 0.20903 | 0.20904 | 0.99577 | -0.12452 | 0.99577 | -0.12447 | 16.3825
82 | 0.092548 | 0.034228 | -0.092548 | -0.040231 | 6.225e-08 | -0.006003 | 0.0028606 | 0.0029255 | 0.0029255 | 0.99577 | -0.12452 | 0.99576 | -0.12452 | 0.22927
83 | 3.2679 | 1.3507 | -3.2678 | -1.3547 | 5.2691e-05 | -0.0040095 | 0.10253 | 0.10257 | 0.10257 | 0.99558 | -0.12893 | 0.99557 | -0.12904 | 8.0386
84 | -2.862 | -1.1663 | 2.862 | 1.1654 | 9.2176e-06 | -0.00092014 | 0.089616 | 0.089606 | 0.089616 | 0.99553 | -0.12928 | 0.99554 | -0.12925 | 7.0232
85 | 0.46594 | 0.20375 | -0.46592 | -0.22261 | 2.0673e-05 | -0.01886 | 0.014746 | 0.014974 | 0.014974 | 0.99553 | -0.12928 | 0.99549 | -0.1295 | 2.347
86 | 2.396 | 0.96258 | -2.3954 | -1.0493 | 0.00061356 | -0.086732 | 0.074875 | 0.075853 | 0.075853 | 0.99553 | -0.12928 | 0.99527 | -0.13106 | 5.9446
87 | -3.1823 | -1.3206 | 3.1824 | 1.3159 | 5.7852e-05 | -0.0046421 | 0.099908 | 0.099856 | 0.099908 | 0.99554 | -0.12925 | 0.99556 | -0.12912 | 7.8298
88 | 0.24189 | 0.1169 | -0.24189 | -0.11715 | 8.8008e-07 | -0.00025663 | 0.0077907 | 0.0077939 | 0.0077939 | 0.99549 | -0.1295 | 0.99548 | -0.12947 | 3.5427
89 | 0.22403 | 0.10572 | -0.22402 | -0.10686 | 3.3402e-06 | -0.001144 | 0.0071834 | 0.0071976 | 0.0071976 | 0.99549 | -0.1295 | 0.99547 | -0.12937 | 3.2716
90 | 1.6686 | 0.7069 | -1.6684 | -0.77739 | 0.00024599 | -0.070483 | 0.052562 | 0.053395 | 0.053395 | 0.99527 | -0.13106 | 0.99511 | -0.1319 | 4.1845
91 | 0.3378 | 0.15421 | -0.33774 | -0.16272 | 5.635e-05 | -0.0085053 | 0.01077 | 0.010875 | 0.010875 | 0.99527 | -0.13106 | 0.99511 | -0.12971 | 4.9434
92 | 0.38901 | 0.1882 | -0.389 | -0.1884 | 4.6182e-06 | -0.00020476 | 0.012534 | 0.012537 | 0.012537 | 0.99527 | -0.13106 | 0.99525 | -0.13159 | 1.5289
93 | -1.9558 | -0.83304 | 1.9559 | 0.81546 | 8.286e-05 | -0.017579 | 0.061652 | 0.061453 | 0.061652 | 0.99538 | -0.13828 | 0.99542 | -0.13798 | 4.8316
94 | 1.9558 | 0.83304 | -1.9558 | -0.83897 | 2.8052e-05 | -0.005925 | 0.061652 | 0.06172 | 0.06172 | 0.99538 | -0.13828 | 0.99536 | -0.13837 | 4.837
95 | -1.9559 | -0.81546 | 1.956 | 0.81525 | 0.00015642 | -0.00021518 | 0.061453 | 0.061446 | 0.061453 | 0.99542 | -0.13798 | 0.99557 | -0.12911 | 4.7638
96 | 1.593 | 0.66326 | -1.5929 | -0.66343 | 4.7186e-05 | -0.00016219 | 0.050044 | 0.050048 | 0.050048 | 0.99536 | -0.13837 | 0.99531 | -0.14166 | 3.8797
97 | -2.146 | -0.90723 | 2.146 | 0.90365 | 2.0342e-05 | -0.003584 | 0.067557 | 0.067516 | 0.067557 | 0.99557 | -0.12911 | 0.99558 | -0.12905 | 5.2944
98 | 0.092548 | 0.040231 | -0.092548 | -0.044823 | 4.964e-08 | -0.0045918 | 0.0029255 | 0.0029811 | 0.0029811 | 0.99576 | -0.12452 | 0.99576 | -0.12452 | 0.23363
99 | 2.817 | 1.2055 | -2.8169 | -1.2073 | 1.8078e-05 | -0.0018366 | 0.088834 | 0.088855 | 0.088855 | 0.9957 | -0.12496 | 0.99569 | -0.12501 | 6.9636
100 | -6.7323 | -2.8133 | 6.7324 | 2.8116 | 9.9014e-05 | -0.0017292 | 0.21153 | 0.21151 | 0.21153 | 0.99577 | -0.12447 | 0.99579 | -0.12437 | 16.5773
101 | 2.4134 | 1.0118 | -2.4133 | -1.0118 | 8.0753e-05 | 1.7675e-06 | 0.075871 | 0.075873 | 0.075873 | 0.99569 | -0.12501 | 0.99563 | -0.12871 | 5.8816
102 | -3.2678 | -1.3573 | 3.2678 | 1.3547 | 3.36e-05 | -0.0025549 | 0.1026 | 0.10257 | 0.1026 | 0.99556 | -0.12912 | 0.99557 | -0.12904 | 8.0409
103 | 0.22402 | 0.10686 | -0.22402 | -0.1085 | 4.8041e-06 | -0.0016374 | 0.0071976 | 0.0072182 | 0.0072182 | 0.99547 | -0.12937 | 0.99545 | -0.12919 | 3.281
104 | 0.26249 | 0.12688 | -0.26249 | -0.12713 | 2.5028e-06 | -0.00024795 | 0.0084576 | 0.0084608 | 0.0084608 | 0.99511 | -0.1319 | 0.9951 | -0.13232 | 1.0318
105 | 1.4059 | 0.65051 | -1.4051 | -0.65219 | 0.00079651 | -0.0016793 | 0.044938 | 0.044973 | 0.044973 | 0.99511 | -0.1319 | 0.99434 | -0.15821 | 5.4845
106 | 0.33774 | 0.16272 | -0.33773 | -0.16357 | 5.7359e-06 | -0.00085632 | 0.010875 | 0.010886 | 0.010886 | 0.99511 | -0.12971 | 0.9951 | -0.12956 | 4.9483
107 | 1.3365 | 0.53923 | -1.3365 | -0.54305 | 8.2882e-06 | -0.0038137 | 0.0418 | 0.041841 | 0.041841 | 0.99531 | -0.14166 | 0.9953 | -0.14171 | 3.2791
108 | 2.2675 | 0.95392 | -2.2675 | -0.95999 | 3.847e-05 | -0.0060685 | 0.071328 | 0.071396 | 0.071396 | 0.9956 | -0.12889 | 0.99558 | -0.129 | 5.5953
109 | -2.2675 | -0.95392 | 2.2676 | 0.94476 | 5.7929e-05 | -0.0091607 | 0.071328 | 0.071225 | 0.071328 | 0.9956 | -0.12889 | 0.99563 | -0.12871 | 5.59
110 | 2.146 | 0.90116 | -2.146 | -0.90162 | 2.6052e-06 | -0.00045962 | 0.067488 | 0.067493 | 0.067493 | 0.99558 | -0.129 | 0.99558 | -0.12901 | 5.2894
111 | 0.14572 | 0.067071 | -0.14572 | -0.070576 | 9.4948e-08 | -0.0035054 | 0.0046511 | 0.0046946 | 0.0046946 | 0.99563 | -0.12871 | 0.99563 | -0.12871 | 0.36791
112 | 2.146 | 0.90162 | -2.146 | -0.90365 | 1.1538e-05 | -0.0020347 | 0.067493 | 0.067516 | 0.067516 | 0.99558 | -0.12901 | 0.99558 | -0.12905 | 5.2912
113 | 1.2315 | 0.56812 | -1.2315 | -0.57326 | 1.9405e-05 | -0.0051407 | 0.039374 | 0.039437 | 0.039437 | 0.99434 | -0.15821 | 0.99432 | -0.15855 | 4.6838
114 | 1.3365 | 0.54305 | -1.3365 | -0.54716 | 8.9557e-06 | -0.0041123 | 0.041841 | 0.041886 | 0.041886 | 0.9953 | -0.14171 | 0.9953 | -0.14176 | 3.2826
115 | 1.3365 | 0.54716 | -1.3365 | -0.54729 | 2.2426e-05 | -0.0001358 | 0.041886 | 0.041888 | 0.041888 | 0.9953 | -0.14176 | 0.99527 | -0.14363 | 3.2472
116 | 0.49414 | 0.16476 | -0.49414 | -0.16854 | 1.0744e-06 | -0.003783 | 0.015108 | 0.015143 | 0.015143 | 0.99527 | -0.14363 | 0.99527 | -0.14366 | 1.1868
117 | 0.62053 | 0.27511 | -0.62051 | -0.27614 | 2.2671e-05 | -0.0010288 | 0.019688 | 0.0197 | 0.0197 | 0.99527 | -0.14363 | 0.99523 | -0.14338 | 8.9546
118 | 0.35794 | 0.15721 | -0.35782 | -0.17232 | 0.00011168 | -0.015106 | 0.01134 | 0.011523 | 0.011523 | 0.99523 | -0.14338 | 0.99494 | -0.14096 | 5.2378
119 | 0.26257 | 0.11893 | -0.26254 | -0.12585 | 2.7626e-05 | -0.0069222 | 0.0083609 | 0.0084458 | 0.0084458 | 0.99523 | -0.14338 | 0.99514 | -0.14254 | 3.839
120 | 0.35782 | 0.17232 | -0.35782 | -0.1733 | 7.362e-06 | -0.00097833 | 0.011523 | 0.011536 | 0.011536 | 0.99494 | -0.14096 | 0.99492 | -0.14078 | 5.2434
121 | 0.26254 | 0.12585 | -0.26254 | -0.12715 | 5.2622e-06 | -0.0013024 | 0.0084458 | 0.0084622 | 0.0084622 | 0.99514 | -0.14254 | 0.99512 | -0.14236 | 3.8465
122 | 0.49414 | 0.16854 | -0.49414 | -0.16924 | 1.9813e-07 | -0.00069509 | 0.015143 | 0.01515 | 0.01515 | 0.99527 | -0.14366 | 0.99526 | -0.14366 | 1.1873
123 | 0.50498 | 0.23808 | -0.50497 | -0.23829 | 3.0726e-06 | -0.00020678 | 0.01619 | 0.016193 | 0.016193 | 0.99543 | -0.11724 | 0.99542 | -0.11719 | 7.3604
124 | 3.0587 | 1.4351 | -3.0565 | -1.4384 | 0.0021202 | -0.0032805 | 0.09798 | 0.098028 | 0.098028 | 0.99543 | -0.11724 | 0.99478 | -0.11161 | 44.5584
125 | -0.34704 | -0.16808 | 0.34705 | 0.16747 | 4.3338e-06 | -0.00060529 | 0.011219 | 0.011212 | 0.011219 | 0.99216 | -0.11893 | 0.99217 | -0.11904 | 5.0997
126 | -0.34705 | -0.16747 | 0.34709 | 0.16125 | 4.4203e-05 | -0.0062222 | 0.011212 | 0.011134 | 0.011212 | 0.99217 | -0.11904 | 0.99229 | -0.12009 | 5.0962
127 | -0.34709 | -0.16125 | 0.3471 | 0.16119 | 1.3327e-05 | -6.2589e-05 | 0.011134 | 0.011133 | 0.011134 | 0.99229 | -0.12009 | 0.99233 | -0.1198 | 5.3019
128 | 0.66486 | 0.31475 | -0.6646 | -0.31496 | 0.00025704 | -0.00020974 | 0.02139 | 0.021395 | 0.021395 | 0.99274 | -0.11704 | 0.99233 | -0.1198 | 10.188
129 | -1.0154 | -0.48455 | 1.0156 | 0.48261 | 0.00011961 | -0.0019358 | 0.032717 | 0.032693 | 0.032717 | 0.99274 | -0.11704 | 0.99285 | -0.11802 | 14.8715
130 | -1.0156 | -0.48261 | 1.016 | 0.47605 | 0.00040391 | -0.006562 | 0.032693 | 0.03261 | 0.032693 | 0.99285 | -0.11802 | 0.99321 | -0.12129 | 14.8603
131 | -0.83209 | -0.39435 | 0.83214 | 0.39311 | 5.0044e-05 | -0.0012444 | 0.026625 | 0.02661 | 0.026625 | 0.99835 | -0.025687 | 0.99841 | -0.026184 | 12.1024
132 | 0.30092 | 0.1391 | -0.30089 | -0.145 | 3.068e-05 | -0.0058975 | 0.0095859 | 0.0096588 | 0.0096588 | 0.99835 | -0.025687 | 0.99826 | -0.024848 | 4.3904
133 | 0.53117 | 0.25525 | -0.53114 | -0.25709 | 3.0244e-05 | -0.0018451 | 0.01704 | 0.017063 | 0.017063 | 0.99835 | -0.025687 | 0.9983 | -0.025195 | 7.7561
134 | -0.96642 | -0.45814 | 0.96674 | 0.45811 | 0.00032863 | -2.3796e-05 | 0.030923 | 0.03092 | 0.030923 | 0.99841 | -0.026184 | 0.99877 | -0.023759 | 14.7254
135 | 0.30089 | 0.145 | -0.30089 | -0.14573 | 3.8071e-06 | -0.00072548 | 0.0096588 | 0.009668 | 0.009668 | 0.99826 | -0.024848 | 0.99825 | -0.024739 | 4.3945
136 | 0.53114 | 0.25709 | -0.53112 | -0.25713 | 2.3654e-05 | -3.9428e-05 | 0.017063 | 0.017064 | 0.017064 | 0.9983 | -0.025195 | 0.99825 | -0.025489 | 8.1258
137 | 0.23962 | 0.11596 | -0.23961 | -0.11605 | 8.9337e-06 | -9.5041e-05 | 0.0076981 | 0.0076994 | 0.0076994 | 0.99825 | -0.025489 | 0.99821 | -0.025736 | 3.6664
138 | -0.37699 | -0.18259 | 0.37704 | 0.1824 | 4.8923e-05 | -0.00018465 | 0.012216 | 0.012213 | 0.012216 | 0.98984 | -0.12053 | 0.98997 | -0.11967 | 5.8172
139 | 0.21335 | 0.10236 | -0.21328 | -0.1033 | 7.1289e-05 | -0.00093644 | 0.0069002 | 0.0069126 | 0.0069126 | 0.98997 | -0.11967 | 0.98962 | -0.12191 | 3.2917
140 | -0.8503 | -0.41064 | 0.8506 | 0.41057 | 0.00030562 | -7.3411e-05 | 0.027535 | 0.027531 | 0.027535 | 0.98997 | -0.11967 | 0.99035 | -0.11727 | 13.1117
141 | 0.088946 | 0.041942 | -0.088946 | -0.043078 | 5.243e-07 | -0.0011359 | 0.0028523 | 0.0028665 | 0.0028665 | 0.99526 | -0.14366 | 0.99526 | -0.14361 | 1.303
142 | 0.4052 | 0.12729 | -0.40518 | -0.19605 | 1.3667e-05 | -0.068759 | 0.012319 | 0.013056 | 0.013056 | 0.99526 | -0.14366 | 0.99523 | -0.14394 | 1.0232
143 | 0.40518 | 0.19605 | -0.40518 | -0.19624 | 4.4977e-06 | -0.00018327 | 0.013056 | 0.013059 | 0.013059 | 0.99523 | -0.14394 | 0.99521 | -0.14443 | 1.5925
144 | 1.084 | 0.50663 | -1.084 | -0.50724 | 4.2903e-05 | -0.00060821 | 0.034844 | 0.034852 | 0.034852 | 0.99134 | -0.12626 | 0.9913 | -0.12594 | 15.8417
145 | -1.1597 | -0.54327 | 1.1612 | 0.5435 | 0.0014896 | 0.00022658 | 0.037292 | 0.037283 | 0.037292 | 0.99134 | -0.12626 | 0.99269 | -0.11672 | 17.7579
146 | 1.084 | 0.50724 | -1.0829 | -0.52276 | 0.0011024 | -0.01552 | 0.034852 | 0.03505 | 0.03505 | 0.9913 | -0.12594 | 0.99037 | -0.11744 | 15.9318
147 | -1.4689 | -0.69254 | 1.4691 | 0.69082 | 0.0002251 | -0.0017132 | 0.047225 | 0.047203 | 0.047225 | 0.99269 | -0.11672 | 0.99283 | -0.11797 | 21.466
148 | 1.0829 | 0.52276 | -1.0829 | -0.52306 | 2.1298e-05 | -0.00029776 | 0.03505 | 0.035054 | 0.035054 | 0.99037 | -0.11744 | 0.99035 | -0.11727 | 15.9335
149 | -1.4691 | -0.69082 | 1.4697 | 0.68622 | 0.00060327 | -0.004602 | 0.047203 | 0.047144 | 0.047203 | 0.99283 | -0.11797 | 0.99321 | -0.12129 | 21.4559
150 | 0.35155 | 0.17021 | -0.35154 | -0.17026 | 1.0083e-05 | -4.5394e-05 | 0.011352 | 0.011353 | 0.011353 | 0.99321 | -0.12129 | 0.99318 | -0.12148 | 5.4062
151 | -2.8373 | -1.3325 | 2.8413 | 1.3347 | 0.0040086 | 0.0021912 | 0.091105 | 0.091101 | 0.091105 | 0.99321 | -0.12129 | 0.9947 | -0.11091 | 43.3835
152 | -3.0563 | -1.4388 | 3.0565 | 1.4384 | 0.00026165 | -0.00040421 | 0.098034 | 0.098028 | 0.098034 | 0.9947 | -0.11091 | 0.99478 | -0.11161 | 44.5611
153 | 1.2315 | 0.57326 | -1.2309 | -0.57509 | 0.00057737 | -0.001826 | 0.039437 | 0.03947 | 0.03947 | 0.99432 | -0.15855 | 0.99368 | -0.18021 | 4.8134
154 | 1.2309 | 0.57509 | -1.2309 | -0.57955 | 1.6935e-05 | -0.0044594 | 0.03947 | 0.039525 | 0.039525 | 0.99368 | -0.18021 | 0.99366 | -0.1805 | 4.6942
155 | 0.90459 | 0.4215 | -0.90454 | -0.42179 | 4.0836e-05 | -0.00028921 | 0.028993 | 0.028997 | 0.028997 | 0.99366 | -0.1805 | 0.9936 | -0.18258 | 3.5362
156 | 13.534 | 5.9254 | -13.5329 | -5.9296 | 0.0010677 | -0.0041501 | 0.42699 | 0.42704 | 0.42704 | 0.99885 | -0.023285 | 0.99877 | -0.023759 | 33.4673
157 | 12.4482 | 5.4143 | -12.445 | -5.4294 | 0.0032012 | -0.015057 | 0.39235 | 0.39255 | 0.39255 | 0.99877 | -0.023759 | 0.9985 | -0.025339 | 30.7639
158 | -0.90446 | -0.4265 | 0.90447 | 0.4223 | 8.613e-06 | -0.0042036 | 0.029056 | 0.029004 | 0.029056 | 0.99348 | -0.18643 | 0.99349 | -0.18623 | 3.4509
159 | 0.56485 | 0.26202 | -0.56482 | -0.26252 | 2.455e-05 | -0.00050189 | 0.018093 | 0.018099 | 0.018099 | 0.99348 | -0.18643 | 0.99342 | -0.18844 | 2.2072
160 | -0.90447 | -0.4223 | 0.90454 | 0.42179 | 7.1419e-05 | -0.00050546 | 0.029004 | 0.028997 | 0.029004 | 0.99349 | -0.18623 | 0.9936 | -0.18258 | 3.5371
161 | 0.27697 | 0.1231 | -0.27697 | -0.12317 | 3.8003e-06 | -6.1827e-05 | 0.0088076 | 0.0088084 | 0.0088084 | 0.99342 | -0.18844 | 0.9934 | -0.1889 | 2.5167
162 | 0.27697 | 0.12317 | -0.27695 | -0.12715 | 1.765e-05 | -0.0039881 | 0.0088084 | 0.0088562 | 0.0088562 | 0.9934 | -0.1889 | 0.99334 | -0.18843 | 4.0255
163 | 0.27695 | 0.12715 | -0.27692 | -0.13292 | 2.5852e-05 | -0.0057626 | 0.0088562 | 0.0089274 | 0.0089274 | 0.99334 | -0.18843 | 0.99326 | -0.18767 | 4.0579
164 | 0.27692 | 0.13292 | -0.27692 | -0.1334 | 2.1704e-06 | -0.00047952 | 0.0089274 | 0.0089335 | 0.0089335 | 0.99326 | -0.18767 | 0.99325 | -0.18761 | 4.0607
165 | 0.069959 | 0.033159 | -0.069959 | -0.033883 | 2.0853e-07 | -0.00072375 | 0.0022501 | 0.0022592 | 0.0022592 | 0.99325 | -0.18761 | 0.99325 | -0.18758 | 1.0269

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 20.6637 | 8.8362

## res_load
| p_mw | q_mvar
0 | 0.23646 | 0.11452
1 | 0.17055 | 0.082601
2 | 0.36214 | 0.17539
3 | 0.26142 | 0.12661
4 | 0.07206 | 0.0349
5 | 0.23027 | 0.11153
6 | 0.2582 | 0.12505
7 | 0.39561 | 0.1916
8 | 0.33707 | 0.16325
9 | 0.17033 | 0.082495
10 | 0.073246 | 0.035475
11 | 0.19099 | 0.092498
12 | 0.5419 | 0.26246
13 | 0.077294 | 0.037435
14 | 0.29869 | 0.14466
15 | 0.13434 | 0.065062
16 | 0.072449 | 0.035088
17 | 0.37046 | 0.17942
18 | 0.152 | 0.073619
19 | 0.28335 | 0.13723
20 | 0.33284 | 0.1612
21 | 0.15175 | 0.073497
22 | 0.12672 | 0.061375
23 | 0.40373 | 0.19554
24 | 0.23313 | 0.11291
25 | 0.37165 | 0.18
26 | 0.27715 | 0.13423
27 | 0.12699 | 0.061506
28 | 0.10214 | 0.049467
29 | 0.17388 | 0.084213
30 | 0.34459 | 0.16689
31 | 0.32121 | 0.15557
32 | 0.29601 | 0.14336
33 | 0.27647 | 0.1339
34 | 0.34514 | 0.16716
35 | 0.37005 | 0.17922
36 | 0.32024 | 0.1551
37 | 0.12775 | 0.061871
38 | 0.37628 | 0.18224
39 | 0.10035 | 0.048602
40 | 0.32035 | 0.15515
41 | 0.36278 | 0.1757
42 | 0.18993 | 0.091988
43 | 0.092548 | 0.044823
44 | 0.077552 | 0.03756
45 | 0.40357 | 0.19546
46 | 0.085368 | 0.041345
47 | 0.22402 | 0.1085
48 | 0.24189 | 0.11715
49 | 0.389 | 0.1884
50 | 0.33773 | 0.16357
51 | 0.25643 | 0.12419
52 | 0.12148 | 0.058836
53 | 0.26249 | 0.12713
54 | 0.17358 | 0.084067
55 | 0.2218 | 0.10742
56 | 0.34704 | 0.16808
57 | 0.35059 | 0.1698
58 | 0.31749 | 0.15377
59 | 0.13427 | 0.065031
60 | 0.30089 | 0.14573
61 | 0.22847 | 0.11065
62 | 0.29149 | 0.14118
63 | 0.26254 | 0.12715
64 | 0.35782 | 0.1733
65 | 0.37699 | 0.18259
66 | 0.25991 | 0.12588
67 | 0.088946 | 0.043078
68 | 0.40518 | 0.19624
69 | 0.075654 | 0.036641
70 | 0.30772 | 0.14904
71 | 0.23226 | 0.11249
72 | 0.21328 | 0.1033
73 | 0.35154 | 0.17026
74 | 0.21502 | 0.10414
75 | 0.32632 | 0.15805
76 | 0.085641 | 0.041478
77 | 0.11794 | 0.057121
78 | 0.23961 | 0.11605
79 | 0.33962 | 0.16448
80 | 0.28785 | 0.13941
81 | 0.20696 | 0.10024
82 | 0.069959 | 0.033883
83 | 0.14572 | 0.070576

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1