## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_99_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_99_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_99_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_99_0_node_31 | 20 | n |  | TRUE
4 | bus_MV_99_0_node_32 | 20 | n |  | TRUE
5 | bus_MV_99_0_node_30 | 20 | n |  | TRUE
6 | bus_MV_99_0_node_197 | 20 | n |  | TRUE
7 | bus_MV_99_0_node_28 | 20 | n |  | TRUE
8 | bus_MV_99_0_node_195 | 20 | n |  | TRUE
9 | bus_MV_99_0_node_159 | 20 | n |  | TRUE
10 | bus_MV_99_0_node_158 | 20 | n |  | TRUE
11 | bus_MV_99_0_node_160 | 20 | n |  | TRUE
12 | bus_MV_99_0_node_166 | 20 | n |  | TRUE
13 | bus_MV_99_0_node_173 | 20 | n |  | TRUE
14 | bus_MV_99_0_node_162 | 20 | n |  | TRUE
15 | bus_MV_99_0_node_4 | 20 | n |  | TRUE
16 | bus_MV_99_0_node_5 | 20 | n |  | TRUE
17 | bus_MV_99_0_node_6 | 20 | n |  | TRUE
18 | bus_MV_99_0_node_7 | 20 | n |  | TRUE
19 | bus_MV_99_0_node_36 | 20 | n |  | TRUE
20 | bus_MV_99_0_node_204 | 20 | n |  | TRUE
21 | bus_MV_99_0_node_37 | 20 | n |  | TRUE
22 | bus_MV_99_0_node_20 | 20 | n |  | TRUE
23 | bus_MV_99_0_node_8 | 20 | n |  | TRUE
24 | bus_MV_99_0_node_10 | 20 | n |  | TRUE
25 | bus_MV_99_0_node_11 | 20 | n |  | TRUE
26 | bus_MV_99_0_node_15 | 20 | n |  | TRUE
27 | bus_MV_99_0_node_16 | 20 | n |  | TRUE
28 | bus_MV_99_0_node_14 | 20 | n |  | TRUE
29 | bus_MV_99_0_node_188 | 20 | n |  | TRUE
30 | bus_MV_99_0_node_12 | 20 | n |  | TRUE
31 | bus_MV_99_0_node_29 | 20 | n |  | TRUE
32 | bus_MV_99_0_node_21 | 20 | n |  | TRUE
33 | bus_MV_99_0_node_25 | 20 | n |  | TRUE
34 | bus_MV_99_0_node_13 | 20 | n |  | TRUE
35 | bus_MV_99_0_node_26 | 20 | n |  | TRUE
36 | bus_MV_99_0_node_22 | 20 | n |  | TRUE
37 | bus_MV_99_0_node_187 | 20 | n |  | TRUE
38 | bus_MV_99_0_node_23 | 20 | n |  | TRUE
39 | bus_MV_99_0_node_51 | 20 | n |  | TRUE
40 | bus_MV_99_0_node_52 | 20 | n |  | TRUE
41 | bus_MV_99_0_node_45 | 20 | n |  | TRUE
42 | bus_MV_99_0_node_24 | 20 | n |  | TRUE
43 | bus_MV_99_0_node_17 | 20 | n |  | TRUE
44 | bus_MV_99_0_node_18 | 20 | n |  | TRUE
45 | bus_MV_99_0_node_19 | 20 | n |  | TRUE
46 | bus_MV_99_0_node_27 | 20 | n |  | TRUE
47 | bus_MV_99_0_node_33 | 20 | n |  | TRUE
48 | bus_MV_99_0_node_35 | 20 | n |  | TRUE
49 | bus_MV_99_0_node_34 | 20 | n |  | TRUE
50 | bus_MV_99_0_node_174 | 20 | n |  | TRUE
51 | bus_MV_99_0_node_38 | 20 | n |  | TRUE
52 | bus_MV_99_0_node_39 | 20 | n |  | TRUE
53 | bus_MV_99_0_node_40 | 20 | n |  | TRUE
54 | bus_MV_99_0_node_202 | 20 | n |  | TRUE
55 | bus_MV_99_0_node_201 | 20 | n |  | TRUE
56 | bus_MV_99_0_node_106 | 20 | n |  | TRUE
57 | bus_MV_99_0_node_107 | 20 | n |  | TRUE
58 | bus_MV_99_0_node_150 | 20 | n |  | TRUE
59 | bus_MV_99_0_node_105 | 20 | n |  | TRUE
60 | bus_MV_99_0_node_49 | 20 | n |  | TRUE
61 | bus_MV_99_0_node_44 | 20 | n |  | TRUE
62 | bus_MV_99_0_node_42 | 20 | n |  | TRUE
63 | bus_MV_99_0_node_43 | 20 | n |  | TRUE
64 | bus_MV_99_0_node_41 | 20 | n |  | TRUE
65 | bus_MV_99_0_node_47 | 20 | n |  | TRUE
66 | bus_MV_99_0_node_199 | 20 | n |  | TRUE
67 | bus_MV_99_0_node_182 | 20 | n |  | TRUE
68 | bus_MV_99_0_node_46 | 20 | n |  | TRUE
69 | bus_MV_99_0_node_48 | 20 | n |  | TRUE
70 | bus_MV_99_0_node_53 | 20 | n |  | TRUE
71 | bus_MV_99_0_node_198 | 20 | n |  | TRUE
72 | bus_MV_99_0_node_196 | 20 | n |  | TRUE
73 | bus_MV_99_0_node_50 | 20 | n |  | TRUE
74 | bus_MV_99_0_node_54 | 20 | n |  | TRUE
75 | bus_MV_99_0_node_56 | 20 | n |  | TRUE
76 | bus_MV_99_0_node_127 | 20 | n |  | TRUE
77 | bus_MV_99_0_node_126 | 20 | n |  | TRUE
78 | bus_MV_99_0_node_59 | 20 | n |  | TRUE
79 | bus_MV_99_0_node_62 | 20 | n |  | TRUE
80 | bus_MV_99_0_node_58 | 20 | n |  | TRUE
81 | bus_MV_99_0_node_55 | 20 | n |  | TRUE
82 | bus_MV_99_0_node_57 | 20 | n |  | TRUE
83 | bus_MV_99_0_node_115 | 20 | n |  | TRUE
84 | bus_MV_99_0_node_125 | 20 | n |  | TRUE
85 | bus_MV_99_0_node_61 | 20 | n |  | TRUE
86 | bus_MV_99_0_node_64 | 20 | n |  | TRUE
87 | bus_MV_99_0_node_65 | 20 | n |  | TRUE
88 | bus_MV_99_0_node_124 | 20 | n |  | TRUE
89 | bus_MV_99_0_node_113 | 20 | n |  | TRUE
90 | bus_MV_99_0_node_122 | 20 | n |  | TRUE
91 | bus_MV_99_0_node_60 | 20 | n |  | TRUE
92 | bus_MV_99_0_node_63 | 20 | n |  | TRUE
93 | bus_MV_99_0_node_76 | 20 | n |  | TRUE
94 | bus_MV_99_0_node_87 | 20 | n |  | TRUE
95 | bus_MV_99_0_node_112 | 20 | n |  | TRUE
96 | bus_MV_99_0_node_74 | 20 | n |  | TRUE
97 | bus_MV_99_0_node_75 | 20 | n |  | TRUE
98 | bus_MV_99_0_node_85 | 20 | n |  | TRUE
99 | bus_MV_99_0_node_69 | 20 | n |  | TRUE
100 | bus_MV_99_0_node_114 | 20 | n |  | TRUE
101 | bus_MV_99_0_node_67 | 20 | n |  | TRUE
102 | bus_MV_99_0_node_68 | 20 | n |  | TRUE
103 | bus_MV_99_0_node_88 | 20 | n |  | TRUE
104 | bus_MV_99_0_node_89 | 20 | n |  | TRUE
105 | bus_MV_99_0_node_70 | 20 | n |  | TRUE
106 | bus_MV_99_0_node_71 | 20 | n |  | TRUE
107 | bus_MV_99_0_node_72 | 20 | n |  | TRUE
108 | bus_MV_99_0_node_176 | 20 | n |  | TRUE
109 | bus_MV_99_0_node_73 | 20 | n |  | TRUE
110 | bus_MV_99_0_node_177 | 20 | n |  | TRUE
111 | bus_MV_99_0_node_194 | 20 | n |  | TRUE
112 | bus_MV_99_0_node_193 | 20 | n |  | TRUE
113 | bus_MV_99_0_node_77 | 20 | n |  | TRUE
114 | bus_MV_99_0_node_79 | 20 | n |  | TRUE
115 | bus_MV_99_0_node_82 | 20 | n |  | TRUE
116 | bus_MV_99_0_node_83 | 20 | n |  | TRUE
117 | bus_MV_99_0_node_131 | 20 | n |  | TRUE
118 | bus_MV_99_0_node_155 | 20 | n |  | TRUE
119 | bus_MV_99_0_node_153 | 20 | n |  | TRUE
120 | bus_MV_99_0_node_129 | 20 | n |  | TRUE
121 | bus_MV_99_0_node_78 | 20 | n |  | TRUE
122 | bus_MV_99_0_node_80 | 20 | n |  | TRUE
123 | bus_MV_99_0_node_81 | 20 | n |  | TRUE
124 | bus_MV_99_0_node_175 | 20 | n |  | TRUE
125 | bus_MV_99_0_node_144 | 20 | n |  | TRUE
126 | bus_MV_99_0_node_137 | 20 | n |  | TRUE
127 | bus_MV_99_0_node_128 | 20 | n |  | TRUE
128 | bus_MV_99_0_node_130 | 20 | n |  | TRUE
129 | bus_MV_99_0_node_183 | 20 | n |  | TRUE
130 | bus_MV_99_0_node_104 | 20 | n |  | TRUE
131 | bus_MV_99_0_node_84 | 20 | n |  | TRUE
132 | bus_MV_99_0_node_180 | 20 | n |  | TRUE
133 | bus_MV_99_0_node_186 | 20 | n |  | TRUE
134 | bus_MV_99_0_node_179 | 20 | n |  | TRUE
135 | bus_MV_99_0_node_185 | 20 | n |  | TRUE
136 | bus_MV_99_0_node_178 | 20 | n |  | TRUE
137 | bus_MV_99_0_node_90 | 20 | n |  | TRUE
138 | bus_MV_99_0_node_91 | 20 | n |  | TRUE
139 | bus_MV_99_0_node_93 | 20 | n |  | TRUE
140 | bus_MV_99_0_node_92 | 20 | n |  | TRUE
141 | bus_MV_99_0_node_94 | 20 | n |  | TRUE
142 | bus_MV_99_0_node_189 | 20 | n |  | TRUE
143 | bus_MV_99_0_node_192 | 20 | n |  | TRUE
144 | bus_MV_99_0_node_96 | 20 | n |  | TRUE
145 | bus_MV_99_0_node_190 | 20 | n |  | TRUE
146 | bus_MV_99_0_node_99 | 20 | n |  | TRUE
147 | bus_MV_99_0_node_95 | 20 | n |  | TRUE
148 | bus_MV_99_0_node_157 | 20 | n |  | TRUE
149 | bus_MV_99_0_node_110 | 20 | n |  | TRUE
150 | bus_MV_99_0_node_117 | 20 | n |  | TRUE
151 | bus_MV_99_0_node_116 | 20 | n |  | TRUE
152 | bus_MV_99_0_node_109 | 20 | n |  | TRUE
153 | bus_MV_99_0_node_119 | 20 | n |  | TRUE
154 | bus_MV_99_0_node_121 | 20 | n |  | TRUE
155 | bus_MV_99_0_node_97 | 20 | n |  | TRUE
156 | bus_MV_99_0_node_98 | 20 | n |  | TRUE
157 | bus_MV_99_0_node_156 | 20 | n |  | TRUE
158 | bus_MV_99_0_node_191 | 20 | n |  | TRUE
159 | bus_MV_99_0_node_100 | 20 | n |  | TRUE
160 | bus_MV_99_0_node_102 | 20 | n |  | TRUE
161 | bus_MV_99_0_node_103 | 20 | n |  | TRUE
162 | bus_MV_99_0_node_101 | 20 | n |  | TRUE
163 | bus_MV_99_0_node_141 | 20 | n |  | TRUE
164 | bus_MV_99_0_node_142 | 20 | n |  | TRUE
165 | bus_MV_99_0_node_139 | 20 | n |  | TRUE
166 | bus_MV_99_0_node_200 | 20 | n |  | TRUE
167 | bus_MV_99_0_node_152 | 20 | n |  | TRUE
168 | bus_MV_99_0_node_140 | 20 | n |  | TRUE
169 | bus_MV_99_0_node_143 | 20 | n |  | TRUE
170 | bus_MV_99_0_node_138 | 20 | n |  | TRUE
171 | bus_MV_99_0_node_151 | 20 | n |  | TRUE
172 | bus_MV_99_0_node_149 | 20 | n |  | TRUE
173 | bus_MV_99_0_node_206 | 20 | n |  | TRUE
174 | bus_MV_99_0_node_207 | 20 | n |  | TRUE
175 | bus_MV_99_0_node_108 | 20 | n |  | TRUE
176 | bus_MV_99_0_node_111 | 20 | n |  | TRUE
177 | bus_MV_99_0_node_123 | 20 | n |  | TRUE
178 | bus_MV_99_0_node_118 | 20 | n |  | TRUE
179 | bus_MV_99_0_node_120 | 20 | n |  | TRUE
180 | bus_MV_99_0_node_132 | 20 | n |  | TRUE
181 | bus_MV_99_0_node_133 | 20 | n |  | TRUE
182 | bus_MV_99_0_node_134 | 20 | n |  | TRUE
183 | bus_MV_99_0_node_146 | 20 | n |  | TRUE
184 | bus_MV_99_0_node_145 | 20 | n |  | TRUE
185 | bus_MV_99_0_node_136 | 20 | n |  | TRUE
186 | bus_MV_99_0_node_148 | 20 | n |  | TRUE
187 | bus_MV_99_0_node_147 | 20 | n |  | TRUE
188 | bus_MV_99_0_node_184 | 20 | n |  | TRUE
189 | bus_MV_99_0_node_181 | 20 | n |  | TRUE
190 | bus_MV_99_0_node_161 | 20 | n |  | TRUE
191 | bus_MV_99_0_node_163 | 20 | n |  | TRUE
192 | bus_MV_99_0_node_167 | 20 | n |  | TRUE
193 | bus_MV_99_0_node_164 | 20 | n |  | TRUE
194 | bus_MV_99_0_node_165 | 20 | n |  | TRUE
195 | bus_MV_99_0_node_171 | 20 | n |  | TRUE
196 | bus_MV_99_0_node_172 | 20 | n |  | TRUE
197 | bus_MV_99_0_node_169 | 20 | n |  | TRUE
198 | bus_MV_99_0_node_168 | 20 | n |  | TRUE
199 | bus_MV_99_0_node_170 | 20 | n |  | TRUE
200 | bus_MV_99_0_node_205 | 20 | n |  | TRUE
201 | bus_HV_99_0_node_195 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_99_0_load_0 | 0 | 0.24861 | 0.12041 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_99_0_load_30 | 5 | 0.14793 | 0.071645 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_99_0_load_197 | 6 | 0.11835 | 0.057319 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_99_0_load_28 | 7 | 0.27231 | 0.13189 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_99_0_load_159 | 9 | 0.10673 | 0.051694 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_99_0_load_158 | 10 | 0.051121 | 0.024759 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_99_0_load_160 | 11 | 0.085425 | 0.041373 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_99_0_load_173 | 13 | 0.33887 | 0.16412 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_99_0_load_4 | 15 | 0.3925 | 0.19009 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_99_0_load_36 | 19 | 0.25931 | 0.12559 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_99_0_load_204 | 20 | 0.37706 | 0.18262 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_99_0_load_8 | 23 | 0.18698 | 0.090561 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_99_0_load_10 | 24 | 0.17753 | 0.085984 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_99_0_load_188 | 29 | 0.21122 | 0.1023 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_99_0_load_29 | 31 | 0.22768 | 0.11027 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_99_0_load_25 | 33 | 0.25789 | 0.1249 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_99_0_load_13 | 34 | 0.071035 | 0.034404 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_99_0_load_26 | 35 | 0.06935 | 0.033588 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_99_0_load_22 | 36 | 0.31553 | 0.15282 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_99_0_load_187 | 37 | 0.06833 | 0.033094 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_99_0_load_51 | 39 | 0.10131 | 0.049068 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_99_0_load_45 | 41 | 0.11549 | 0.055936 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_99_0_load_17 | 43 | 0.39914 | 0.19331 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_99_0_load_18 | 44 | 0.068273 | 0.033066 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_99_0_load_33 | 47 | 0.31626 | 0.15317 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_99_0_load_35 | 48 | 0.15588 | 0.075494 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_99_0_load_34 | 49 | 0.13706 | 0.066383 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_99_0_load_174 | 50 | 0.071762 | 0.034756 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_99_0_load_38 | 51 | 0.14832 | 0.071835 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_99_0_load_201 | 55 | 0.13108 | 0.063487 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_99_0_load_150 | 58 | 0.14009 | 0.067849 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_99_0_load_105 | 59 | 0.11371 | 0.05507 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_99_0_load_49 | 60 | 0.11034 | 0.05344 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_99_0_load_43 | 63 | 0.10076 | 0.048801 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_99_0_load_41 | 64 | 0.10711 | 0.051875 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_99_0_load_199 | 66 | 0.056133 | 0.027187 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_99_0_load_198 | 71 | 0.11562 | 0.055996 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_99_0_load_50 | 73 | 0.15819 | 0.076614 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_99_0_load_54 | 74 | 0.12094 | 0.058574 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_99_0_load_56 | 75 | 0.11183 | 0.054163 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_99_0_load_127 | 76 | 0.11479 | 0.055593 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_99_0_load_126 | 77 | 0.087674 | 0.042462 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_99_0_load_62 | 79 | 0.10742 | 0.052025 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_99_0_load_58 | 80 | 0.1238 | 0.059957 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_99_0_load_55 | 81 | 0.15345 | 0.074318 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_99_0_load_115 | 83 | 0.11791 | 0.057107 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_99_0_load_65 | 87 | 0.11877 | 0.057521 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_99_0_load_124 | 88 | 0.12867 | 0.062319 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_99_0_load_63 | 92 | 0.098162 | 0.047542 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_99_0_load_87 | 94 | 0.1307 | 0.0633 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_99_0_load_74 | 96 | 0.13962 | 0.067621 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_99_0_load_85 | 98 | 0.078406 | 0.037974 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_99_0_load_114 | 100 | 0.10343 | 0.050093 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_99_0_load_67 | 101 | 0.12903 | 0.062494 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_99_0_load_89 | 104 | 0.094133 | 0.045591 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_99_0_load_70 | 105 | 0.12538 | 0.060725 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_99_0_load_71 | 106 | 0.14063 | 0.068111 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_99_0_load_176 | 108 | 0.076279 | 0.036944 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_99_0_load_194 | 111 | 0.10391 | 0.050324 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_99_0_load_193 | 112 | 0.12049 | 0.058354 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_99_0_load_77 | 113 | 0.12778 | 0.061888 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_99_0_load_82 | 115 | 0.10807 | 0.052341 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_99_0_load_153 | 119 | 0.080016 | 0.038754 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_99_0_load_175 | 124 | 0.099167 | 0.048029 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_99_0_load_144 | 125 | 0.11483 | 0.055616 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_99_0_load_137 | 126 | 0.15561 | 0.075367 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_99_0_load_128 | 127 | 0.14449 | 0.069979 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_99_0_load_183 | 129 | 0.10852 | 0.052558 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_99_0_load_84 | 131 | 0.095238 | 0.046126 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_99_0_load_180 | 132 | 0.081326 | 0.039388 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_99_0_load_186 | 133 | 0.093218 | 0.045148 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_99_0_load_178 | 136 | 0.13139 | 0.063633 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_99_0_load_90 | 137 | 0.12872 | 0.06234 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_99_0_load_93 | 139 | 0.11387 | 0.055148 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_99_0_load_94 | 141 | 0.084785 | 0.041063 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_99_0_load_189 | 142 | 0.13962 | 0.067619 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_99_0_load_192 | 143 | 0.10619 | 0.05143 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_99_0_load_96 | 144 | 0.1596 | 0.077299 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_99_0_load_157 | 148 | 0.067686 | 0.032782 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_99_0_load_116 | 151 | 0.061051 | 0.029569 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_99_0_load_109 | 152 | 0.11647 | 0.056407 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_99_0_load_121 | 154 | 0.15904 | 0.077027 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_99_0_load_97 | 155 | 0.083222 | 0.040306 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_99_0_load_191 | 158 | 0.075115 | 0.03638 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_99_0_load_100 | 159 | 0.064932 | 0.031448 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_99_0_load_102 | 160 | 0.075438 | 0.036536 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_99_0_load_101 | 162 | 0.11701 | 0.056669 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_99_0_load_141 | 163 | 0.091361 | 0.044248 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_99_0_load_139 | 165 | 0.12997 | 0.062948 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_99_0_load_200 | 166 | 0.14323 | 0.069369 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_99_0_load_140 | 168 | 0.070167 | 0.033983 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_99_0_load_143 | 169 | 0.085142 | 0.041236 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_99_0_load_138 | 170 | 0.15222 | 0.073722 | 0 | 0 |  | 1 | TRUE | wye
93 | MV_99_0_load_149 | 172 | 0.084996 | 0.041165 | 0 | 0 |  | 1 | TRUE | wye
94 | MV_99_0_load_206 | 173 | 0.15228 | 0.073753 | 0 | 0 |  | 1 | TRUE | wye
95 | MV_99_0_load_207 | 174 | 0.15311 | 0.074153 | 0 | 0 |  | 1 | TRUE | wye
96 | MV_99_0_load_108 | 175 | 0.11392 | 0.055174 | 0 | 0 |  | 1 | TRUE | wye
97 | MV_99_0_load_111 | 176 | 0.16104 | 0.077997 | 0 | 0 |  | 1 | TRUE | wye
98 | MV_99_0_load_123 | 177 | 0.097846 | 0.047389 | 0 | 0 |  | 1 | TRUE | wye
99 | MV_99_0_load_120 | 179 | 0.1135 | 0.054972 | 0 | 0 |  | 1 | TRUE | wye
100 | MV_99_0_load_132 | 180 | 0.1193 | 0.057779 | 0 | 0 |  | 1 | TRUE | wye
101 | MV_99_0_load_133 | 181 | 0.12588 | 0.060965 | 0 | 0 |  | 1 | TRUE | wye
102 | MV_99_0_load_148 | 186 | 0.12037 | 0.058299 | 0 | 0 |  | 1 | TRUE | wye
103 | MV_99_0_load_147 | 187 | 0.15254 | 0.07388 | 0 | 0 |  | 1 | TRUE | wye
104 | MV_99_0_load_184 | 188 | 0.068051 | 0.032958 | 0 | 0 |  | 1 | TRUE | wye
105 | MV_99_0_load_181 | 189 | 0.16293 | 0.07891 | 0 | 0 |  | 1 | TRUE | wye
106 | MV_99_0_load_161 | 190 | 0.38733 | 0.18759 | 0 | 0 |  | 1 | TRUE | wye
107 | MV_99_0_load_171 | 195 | 0.2162 | 0.10471 | 0 | 0 |  | 1 | TRUE | wye
108 | MV_99_0_load_172 | 196 | 0.41198 | 0.19953 | 0 | 0 |  | 1 | TRUE | wye
109 | MV_99_0_load_168 | 198 | 0.40998 | 0.19856 | 0 | 0 |  | 1 | TRUE | wye
110 | MV_99_0_load_170 | 199 | 0.39507 | 0.19134 | 0 | 0 |  | 1 | TRUE | wye
111 | MV_99_0_load_205 | 200 | 0.37094 | 0.17965 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_99_0_line_0 |  | 0 | 1 | 0.006093 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_99_0_line_1 |  | 1 | 2 | 1.1173 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
2 | MV_99_0_line_2 |  | 1 | 3 | 0.4294 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
3 | MV_99_0_line_3 |  | 2 | 9 | 0.031616 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
4 | MV_99_0_line_4 |  | 2 | 10 | 0.18392 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_99_0_line_5 |  | 3 | 4 | 0.036447 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
6 | MV_99_0_line_6 |  | 3 | 5 | 0.03228 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_99_0_line_7 |  | 4 | 47 | 0.022643 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
8 | MV_99_0_line_8 |  | 6 | 7 | 4.6487 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
9 | MV_99_0_line_9 |  | 6 | 8 | 0.11136 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
10 | MV_99_0_line_10 |  | 7 | 46 | 0.043155 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
11 | MV_99_0_line_11 |  | 8 | 72 | 0.18379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_99_0_line_12 |  | 8 | 54 | 2.7725 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
13 | MV_99_0_line_13 |  | 9 | 11 | 0.019128 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
14 | MV_99_0_line_14 |  | 11 | 12 | 1.0333 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
15 | MV_99_0_line_15 |  | 12 | 13 | 0.051731 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_99_0_line_16 |  | 12 | 14 | 0.68722 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
17 | MV_99_0_line_17 |  | 14 | 193 | 0.053386 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
18 | MV_99_0_line_18 |  | 14 | 194 | 0.29031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_99_0_line_19 |  | 15 | 16 | 0.040279 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_99_0_line_20 |  | 16 | 17 | 0.34713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_99_0_line_21 |  | 17 | 18 | 0.43216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_99_0_line_22 |  | 17 | 19 | 0.042163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_99_0_line_23 |  | 18 | 20 | 0.08665 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_99_0_line_24 |  | 19 | 21 | 0.035235 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
25 | MV_99_0_line_25 |  | 19 | 22 | 0.020079 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_99_0_line_26 |  | 21 | 49 | 0.025948 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
27 | MV_99_0_line_27 |  | 22 | 45 | 0.07009 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
28 | MV_99_0_line_28 |  | 23 | 24 | 0.022491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_99_0_line_29 |  | 23 | 25 | 0.12071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_99_0_line_30 |  | 24 | 26 | 0.04341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_99_0_line_31 |  | 25 | 27 | 0.01349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_99_0_line_32 |  | 26 | 35 | 0.059593 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_99_0_line_33 |  | 26 | 36 | 0.074617 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_99_0_line_34 |  | 27 | 37 | 0.026685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_99_0_line_35 |  | 28 | 29 | 0.028464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_99_0_line_36 |  | 28 | 30 | 0.26716 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_99_0_line_37 |  | 30 | 34 | 0.036739 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_99_0_line_38 |  | 31 | 32 | 0.041218 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
39 | MV_99_0_line_39 |  | 31 | 33 | 0.13661 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
40 | MV_99_0_line_40 |  | 32 | 45 | 0.14614 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
41 | MV_99_0_line_41 |  | 33 | 42 | 0.030953 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
42 | MV_99_0_line_42 |  | 34 | 38 | 0.02962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_99_0_line_43 |  | 35 | 42 | 0.066314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_99_0_line_44 |  | 36 | 38 | 0.06637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_99_0_line_45 |  | 39 | 40 | 0.038466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_99_0_line_46 |  | 39 | 41 | 1.0461 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_99_0_line_47 |  | 40 | 70 | 0.18712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_99_0_line_48 |  | 41 | 68 | 0.008542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_99_0_line_49 |  | 41 | 65 | 0.067562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_99_0_line_50 |  | 42 | 46 | 0.24165 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
51 | MV_99_0_line_51 |  | 43 | 44 | 0.018124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_99_0_line_52 |  | 43 | 45 | 0.021642 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_99_0_line_53 |  | 47 | 48 | 0.027471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_99_0_line_54 |  | 47 | 49 | 0.035746 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
55 | MV_99_0_line_55 |  | 47 | 50 | 0.027394 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_99_0_line_56 |  | 51 | 52 | 0.023974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_99_0_line_57 |  | 52 | 53 | 0.050495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_99_0_line_58 |  | 53 | 60 | 0.024249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_99_0_line_59 |  | 53 | 61 | 0.046289 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_99_0_line_60 |  | 54 | 55 | 0.076944 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_99_0_line_61 |  | 55 | 170 | 0.33032 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
62 | MV_99_0_line_62 |  | 56 | 57 | 0.13959 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_99_0_line_63 |  | 56 | 58 | 0.076595 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
64 | MV_99_0_line_64 |  | 56 | 59 | 0.048747 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_99_0_line_65 |  | 57 | 166 | 0.041612 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
66 | MV_99_0_line_66 |  | 58 | 170 | 0.12042 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
67 | MV_99_0_line_67 |  | 60 | 65 | 0.019191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_99_0_line_68 |  | 61 | 62 | 0.060932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_99_0_line_69 |  | 62 | 63 | 0.032679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_99_0_line_70 |  | 62 | 64 | 0.042819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_99_0_line_71 |  | 66 | 67 | 1.4571 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_99_0_line_72 |  | 67 | 144 | 0.32533 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_99_0_line_73 |  | 68 | 69 | 0.1403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_99_0_line_74 |  | 69 | 73 | 0.015411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_99_0_line_75 |  | 70 | 71 | 0.068684 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_99_0_line_76 |  | 71 | 72 | 0.02351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_99_0_line_77 |  | 74 | 75 | 0.054956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_99_0_line_78 |  | 74 | 76 | 0.077159 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_99_0_line_79 |  | 75 | 77 | 0.093148 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_99_0_line_80 |  | 77 | 88 | 0.078533 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_99_0_line_81 |  | 78 | 79 | 0.055251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_99_0_line_82 |  | 78 | 80 | 0.052211 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_99_0_line_83 |  | 80 | 91 | 0.046711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_99_0_line_84 |  | 80 | 85 | 0.080122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_99_0_line_85 |  | 81 | 82 | 0.007664 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_99_0_line_86 |  | 82 | 83 | 0.03547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_99_0_line_87 |  | 82 | 84 | 0.057702 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_99_0_line_88 |  | 83 | 89 | 0.04497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_99_0_line_89 |  | 84 | 90 | 0.063419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_99_0_line_90 |  | 85 | 86 | 0.065839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_99_0_line_91 |  | 85 | 87 | 0.039961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_99_0_line_92 |  | 86 | 94 | 0.020008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_99_0_line_93 |  | 87 | 95 | 0.042298 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_99_0_line_94 |  | 88 | 154 | 0.11253 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_99_0_line_95 |  | 88 | 90 | 0.06463 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_99_0_line_96 |  | 89 | 95 | 0.037754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_99_0_line_97 |  | 90 | 153 | 0.008661 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_99_0_line_98 |  | 91 | 92 | 0.023568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_99_0_line_99 |  | 92 | 93 | 0.036934 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_99_0_line_100 |  | 93 | 98 | 0.039449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_99_0_line_101 |  | 93 | 97 | 0.091732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_99_0_line_102 |  | 94 | 99 | 0.030092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_99_0_line_103 |  | 95 | 100 | 0.054575 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_99_0_line_104 |  | 96 | 97 | 0.027633 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_99_0_line_105 |  | 99 | 103 | 0.012452 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_99_0_line_106 |  | 99 | 102 | 0.045092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_99_0_line_107 |  | 101 | 102 | 0.034655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_99_0_line_108 |  | 103 | 104 | 0.069987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_99_0_line_109 |  | 104 | 127 | 0.046667 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_99_0_line_110 |  | 105 | 106 | 0.02479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_99_0_line_111 |  | 105 | 107 | 0.045928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_99_0_line_112 |  | 106 | 108 | 0.077089 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
113 | MV_99_0_line_113 |  | 107 | 109 | 0.14832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_99_0_line_114 |  | 108 | 110 | 0.035556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_99_0_line_115 |  | 109 | 111 | 0.067078 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_99_0_line_116 |  | 110 | 136 | 0.031568 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_99_0_line_117 |  | 111 | 112 | 0.004503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_99_0_line_118 |  | 113 | 114 | 0.006701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_99_0_line_119 |  | 114 | 115 | 0.020214 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
120 | MV_99_0_line_120 |  | 114 | 116 | 0.026399 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
121 | MV_99_0_line_121 |  | 115 | 120 | 0.020717 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
122 | MV_99_0_line_122 |  | 116 | 126 | 0.018013 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_99_0_line_123 |  | 116 | 127 | 0.055329 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
124 | MV_99_0_line_124 |  | 117 | 118 | 0.044471 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
125 | MV_99_0_line_125 |  | 117 | 119 | 0.019266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_99_0_line_126 |  | 117 | 120 | 0.025255 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
127 | MV_99_0_line_127 |  | 118 | 132 | 0.02729 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
128 | MV_99_0_line_128 |  | 118 | 131 | 0.025078 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
129 | MV_99_0_line_129 |  | 120 | 128 | 0.031744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_99_0_line_130 |  | 121 | 122 | 0.072374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_99_0_line_131 |  | 121 | 123 | 0.20186 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_99_0_line_132 |  | 122 | 124 | 0.014368 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_99_0_line_133 |  | 123 | 125 | 0.083407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_99_0_line_134 |  | 125 | 129 | 0.18323 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
135 | MV_99_0_line_135 |  | 125 | 130 | 0.11956 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
136 | MV_99_0_line_136 |  | 128 | 180 | 0.005967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_99_0_line_137 |  | 129 | 189 | 0.13729 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
138 | MV_99_0_line_138 |  | 130 | 168 | 0.04764 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
139 | MV_99_0_line_139 |  | 130 | 165 | 0.036268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_99_0_line_140 |  | 130 | 161 | 0.026638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_99_0_line_141 |  | 132 | 189 | 0.11047 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
142 | MV_99_0_line_142 |  | 133 | 134 | 0.081414 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
143 | MV_99_0_line_143 |  | 134 | 135 | 0.094249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_99_0_line_144 |  | 134 | 136 | 0.055463 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_99_0_line_145 |  | 135 | 188 | 0.041031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_99_0_line_146 |  | 137 | 138 | 0.065323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_99_0_line_147 |  | 137 | 139 | 0.15106 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
148 | MV_99_0_line_148 |  | 138 | 140 | 0.1132 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_99_0_line_149 |  | 139 | 141 | 0.037421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_99_0_line_150 |  | 140 | 142 | 0.012549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_99_0_line_151 |  | 141 | 147 | 0.084326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_99_0_line_152 |  | 141 | 148 | 0.077608 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
153 | MV_99_0_line_153 |  | 142 | 145 | 0.073188 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
154 | MV_99_0_line_154 |  | 143 | 144 | 0.057689 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
155 | MV_99_0_line_155 |  | 144 | 145 | 0.050862 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_99_0_line_156 |  | 145 | 146 | 0.05357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_99_0_line_157 |  | 146 | 157 | 0.018476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_99_0_line_158 |  | 146 | 156 | 0.078512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_99_0_line_159 |  | 147 | 149 | 0.045408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_99_0_line_160 |  | 148 | 150 | 0.040619 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
161 | MV_99_0_line_161 |  | 149 | 151 | 0.1162 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
162 | MV_99_0_line_162 |  | 149 | 152 | 0.056145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_99_0_line_163 |  | 150 | 153 | 0.003119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_99_0_line_164 |  | 151 | 178 | 0.077773 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_99_0_line_165 |  | 152 | 177 | 0.12271 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
166 | MV_99_0_line_166 |  | 152 | 175 | 0.088795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_99_0_line_167 |  | 155 | 156 | 0.037003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_99_0_line_168 |  | 157 | 158 | 0.021815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_99_0_line_169 |  | 159 | 160 | 0.018452 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_99_0_line_170 |  | 159 | 161 | 0.024374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_99_0_line_171 |  | 159 | 162 | 0.058255 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
172 | MV_99_0_line_172 |  | 163 | 164 | 0.008106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_99_0_line_173 |  | 163 | 165 | 0.096533 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
174 | MV_99_0_line_174 |  | 164 | 184 | 0.074751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_99_0_line_175 |  | 166 | 167 | 0.057543 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
176 | MV_99_0_line_176 |  | 167 | 171 | 0.098202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_99_0_line_177 |  | 167 | 185 | 0.011747 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
178 | MV_99_0_line_178 |  | 168 | 169 | 0.06142 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
179 | MV_99_0_line_179 |  | 169 | 185 | 0.082239 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
180 | MV_99_0_line_180 |  | 171 | 172 | 0.11643 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
181 | MV_99_0_line_181 |  | 172 | 174 | 0.11441 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
182 | MV_99_0_line_182 |  | 173 | 174 | 0.050553 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
183 | MV_99_0_line_183 |  | 175 | 176 | 0.046374 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
184 | MV_99_0_line_184 |  | 178 | 179 | 0.004605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
185 | MV_99_0_line_185 |  | 181 | 182 | 0.062653 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
186 | MV_99_0_line_186 |  | 182 | 183 | 0.11685 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
187 | MV_99_0_line_187 |  | 183 | 184 | 0.047143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
188 | MV_99_0_line_188 |  | 184 | 188 | 0.059381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
189 | MV_99_0_line_189 |  | 184 | 187 | 0.064602 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
190 | MV_99_0_line_190 |  | 185 | 186 | 0.067143 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
191 | MV_99_0_line_191 |  | 190 | 191 | 0.037487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
192 | MV_99_0_line_192 |  | 191 | 192 | 0.10815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
193 | MV_99_0_line_193 |  | 192 | 197 | 0.058252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
194 | MV_99_0_line_194 |  | 193 | 195 | 0.014155 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
195 | MV_99_0_line_195 |  | 194 | 196 | 0.053408 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
196 | MV_99_0_line_196 |  | 195 | 198 | 0.35487 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
197 | MV_99_0_line_197 |  | 197 | 199 | 0.010271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
198 | MV_99_0_line_198 |  | 198 | 200 | 2.2234 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
199 | MV_99_0_line_199 |  | 199 | 200 | 2.3438 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_99_0_trafo_195 | 25 MVA 110/20 kV | 201 | 8 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2609845.5431 | 1128385.5447
1 | 2609851.5348 | 1128386.7439
2 | 2609283.019 | 1127640.5197
3 | 2610047.4317 | 1128768.8505
4 | 2610052.6799 | 1128804.8657
5 | 2610043.7253 | 1128736.7843
6 | 2613658.2076 | 1132495.5903
7 | 2610500.3678 | 1129084.0692
8 | 2613615.5414 | 1132598.4558
9 | 2609266.8046 | 1127667.6607
10 | 2609125.4803 | 1127545.602
11 | 2609256.9944 | 1127684.0819
12 | 2608476.8834 | 1128361.6298
13 | 2608425.7565 | 1128352.8324
14 | 2608377.5703 | 1128967.3433
15 | 2610198.7768 | 1129217.4323
16 | 2610185.1599 | 1129179.5243
17 | 2610072.8671 | 1128941.8437
18 | 2609807.3066 | 1128869.2745
19 | 2610090.5249 | 1128903.5431
20 | 2609735.9599 | 1128820.1027
21 | 2610097.2688 | 1128868.9597
22 | 2610109.905 | 1128909.0002
23 | 2610513.3178 | 1128713.5996
24 | 2610515.4796 | 1128735.9867
25 | 2610393.4668 | 1128704.1224
26 | 2610516.1394 | 1128779.192
27 | 2610380.956 | 1128708.77
28 | 2610777.5193 | 1128626.3082
29 | 2610801.6894 | 1128611.1659
30 | 2610637.9102 | 1128733.9483
31 | 2610244.5593 | 1128890.3274
32 | 2610206.5777 | 1128906.5937
33 | 2610370.4273 | 1128837.24
34 | 2610645.996 | 1128769.7686
35 | 2610460.8225 | 1128801.3586
36 | 2610585.5693 | 1128806.5258
37 | 2610396.534 | 1128730.4627
38 | 2610651.6859 | 1128798.8375
39 | 2613918.8313 | 1132281.5666
40 | 2613904.7063 | 1132317.3517
41 | 2614964.8264 | 1132297.4746
42 | 2610399.2671 | 1128826.0251
43 | 2610114.6929 | 1128951.3266
44 | 2610113.6263 | 1128933.234
45 | 2610136.2974 | 1128950.053
46 | 2610508.329 | 1129041.6622
47 | 2610059.1534 | 1128826.5425
48 | 2610033.6656 | 1128836.7919
49 | 2610073.1295 | 1128859.4426
50 | 2610086.5462 | 1128826.8324
51 | 2614981.4994 | 1132127.2658
52 | 2614991.0089 | 1132148.6886
53 | 2614975.8301 | 1132190.7162
54 | 2614271.3505 | 1135292.2456
55 | 2614309.8306 | 1135358.9244
56 | 2614639.6568 | 1135706.5703
57 | 2614605.7439 | 1135841.788
58 | 2614565.1073 | 1135724.155
59 | 2614661.0342 | 1135750.3989
60 | 2614973.4539 | 1132214.5442
61 | 2615021.6864 | 1132184.4042
62 | 2615065.1296 | 1132170.1271
63 | 2615081.199 | 1132141.7643
64 | 2615050.9403 | 1132210.3672
65 | 2614970.0822 | 1132233.0227
66 | 2616300.5264 | 1135479.919
67 | 2615147.8431 | 1136371.1878
68 | 2614971.6835 | 1132292.3556
69 | 2615018.5714 | 1132357.2366
70 | 2613844.16 | 1132490.1311
71 | 2613787.6856 | 1132529.2216
72 | 2613770.2277 | 1132544.9453
73 | 2615031.8255 | 1132349.31
74 | 2614340.8329 | 1136871.8815
75 | 2614374.5781 | 1136828.4513
76 | 2614278.3017 | 1136826.6786
77 | 2614445.6044 | 1136888.7162
78 | 2614432.484 | 1136738.3559
79 | 2614390.3519 | 1136704.9544
80 | 2614458.3572 | 1136693.0065
81 | 2614525.6795 | 1136793.561
82 | 2614533.2907 | 1136792.4898
83 | 2614568.3514 | 1136797.8543
84 | 2614550.9767 | 1136847.3368
85 | 2614538.1693 | 1136686.2162
86 | 2614565.7679 | 1136630.7998
87 | 2614577.7678 | 1136692.3809
88 | 2614519.6807 | 1136914.7947
89 | 2614601.0588 | 1136767.7294
90 | 2614582.7368 | 1136900.6169
91 | 2614436.3477 | 1136663.3618
92 | 2614421.465 | 1136645.5065
93 | 2614391.9749 | 1136623.2701
94 | 2614584.2281 | 1136623.1096
95 | 2614583.7833 | 1136734.2492
96 | 2614335.3792 | 1136552.7682
97 | 2614344.0955 | 1136578.9905
98 | 2614358.1061 | 1136643.6553
99 | 2614612.8464 | 1136613.927
100 | 2614631.2846 | 1136707.7601
101 | 2614557.1598 | 1136579.165
102 | 2614591.6676 | 1136575.0237
103 | 2614625.3264 | 1136613.468
104 | 2614662.6168 | 1136565.7347
105 | 2614584.8383 | 1136378.9114
106 | 2614582.7434 | 1136354.2165
107 | 2614585.4822 | 1136424.6464
108 | 2614537.1084 | 1136292.0868
109 | 2614517.6034 | 1136490.8603
110 | 2614504.1525 | 1136305.3597
111 | 2614473.501 | 1136440.3191
112 | 2614472.0109 | 1136436.069
113 | 2614683.6082 | 1136462.7018
114 | 2614680.2167 | 1136468.4853
115 | 2614697.4478 | 1136479.1322
116 | 2614659.8185 | 1136485.3108
117 | 2614724.5596 | 1136463.5459
118 | 2614732.8625 | 1136431.3059
119 | 2614743.2045 | 1136468.6048
120 | 2614716.4851 | 1136487.3046
121 | 2614679.7951 | 1136413.8464
122 | 2614730.0096 | 1136383.2199
123 | 2614649.6973 | 1136292.7811
124 | 2614728.8071 | 1136368.9024
125 | 2614658.2605 | 1136213.3074
126 | 2614645.8358 | 1136473.9382
127 | 2614632.4976 | 1136533.4239
128 | 2614709.7164 | 1136518.3145
129 | 2614841.3417 | 1136220.799
130 | 2614673.1893 | 1136094.6855
131 | 2614711.6449 | 1136417.9367
132 | 2614750.4401 | 1136410.4301
133 | 2614348.7893 | 1136293.4511
134 | 2614425.1901 | 1136321.5793
135 | 2614413.3635 | 1136231.4627
136 | 2614474.1545 | 1136295.5277
137 | 2614884.6084 | 1136846.9352
138 | 2614906.561 | 1136789.0275
139 | 2614737.4242 | 1136880.9146
140 | 2614840.0439 | 1136698.3534
141 | 2614699.8958 | 1136881.4015
142 | 2614832.0511 | 1136688.6624
143 | 2614936.8948 | 1136658.2382
144 | 2614919.7432 | 1136603.1579
145 | 2614877.2373 | 1136631.0894
146 | 2614830.0544 | 1136605.4724
147 | 2614673.4154 | 1136961.0763
148 | 2614624.5732 | 1136900.0952
149 | 2614670.5131 | 1137006.3914
150 | 2614585.7404 | 1136912.0075
151 | 2614564.6884 | 1137054.3931
152 | 2614726.2157 | 1137004.6862
153 | 2614584.9399 | 1136908.993
154 | 2614451.2206 | 1137004.1086
155 | 2614842.3805 | 1136491.9137
156 | 2614845.599 | 1136528.5395
157 | 2614812.9459 | 1136598.3827
158 | 2614819.4363 | 1136577.555
159 | 2614688.5046 | 1136050.9462
160 | 2614670.1784 | 1136053.0993
161 | 2614691.3487 | 1136075.1533
162 | 2614681.707 | 1135993.0887
163 | 2614547.4758 | 1136135.8473
164 | 2614546.1179 | 1136143.8368
165 | 2614639.4847 | 1136106.6404
166 | 2614606.113 | 1135883.3981
167 | 2614570.8479 | 1135928.8688
168 | 2614645.8578 | 1136055.6654
169 | 2614610.6204 | 1136005.3584
170 | 2614473.7516 | 1135645.698
171 | 2614506.8532 | 1135858.4032
172 | 2614398.6747 | 1135901.4443
173 | 2614342.9634 | 1135756.7304
174 | 2614334.6892 | 1135806.6019
175 | 2614813.3319 | 1136998.1693
176 | 2614859.5722 | 1137001.694
177 | 2614747.9226 | 1137125.4597
178 | 2614511.7135 | 1137109.6042
179 | 2614508.1433 | 1137106.6831
180 | 2614708.9404 | 1136524.2266
181 | 2614360.7773 | 1136029.1613
182 | 2614359.5367 | 1136091.6556
183 | 2614447.6905 | 1136168.358
184 | 2614488.4879 | 1136166.8879
185 | 2614563.4393 | 1135938
186 | 2614515.4757 | 1135984.9857
187 | 2614481.7321 | 1136102.6404
188 | 2614448.0958 | 1136210.1994
189 | 2614847.6326 | 1136357.9277
190 | 2608421.9379 | 1128997.308
191 | 2608435.1695 | 1129032.3878
192 | 2608404.2076 | 1129107.1704
193 | 2608330.7772 | 1128964.4333
194 | 2608318.5957 | 1128723.8327
195 | 2608316.706 | 1128962.5576
196 | 2608267.9836 | 1128706.7778
197 | 2608449.3581 | 1129143.873
198 | 2607970.958 | 1129042.5125
199 | 2608452.4411 | 1129153.6709
200 | 2607174.0552 | 1131118.1675
201 | 2613615.5414 | 1132598.4558

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98704 | -0.75098 | 0.24861 | 0.12041
1 | 0.98704 | -0.751 | 0 | 0
2 | 0.98654 | -0.75446 | 0 | 0
3 | 0.98745 | -0.72496 | 0 | 0
4 | 0.98747 | -0.72482 | 0 | 0
5 | 0.98744 | -0.72502 | 0.14793 | 0.071645
6 | 0.99973 | -0.015689 | 0.11835 | 0.057319
7 | 0.9887 | -0.66739 | 0.27231 | 0.13189
8 | 1 | 0 | -16.5676 | -7.6703
9 | 0.98653 | -0.75454 | 0.10673 | 0.051694
10 | 0.98652 | -0.75458 | 0.051121 | 0.024759
11 | 0.98652 | -0.75459 | 0.085425 | 0.041373
12 | 0.98566 | -0.80621 | 0 | 0
13 | 0.98564 | -0.806 | 0.33887 | 0.16412
14 | 0.98541 | -0.80749 | 0 | 0
15 | 0.98735 | -0.71567 | 0.3925 | 0.19009
16 | 0.98738 | -0.71547 | 0 | 0
17 | 0.98755 | -0.71705 | 0 | 0
18 | 0.98734 | -0.7152 | 0 | 0
19 | 0.9876 | -0.7174 | 0.25931 | 0.12559
20 | 0.98728 | -0.7156 | 0.37706 | 0.18262
21 | 0.98755 | -0.7201 | 0 | 0
22 | 0.98761 | -0.7173 | 0 | 0
23 | 0.9879 | -0.69887 | 0.18698 | 0.090561
24 | 0.98791 | -0.69893 | 0.17753 | 0.085984
25 | 0.98789 | -0.69879 | 0 | 0
26 | 0.98793 | -0.69915 | 0 | 0
27 | 0.98789 | -0.69878 | 0 | 0
28 | 0.98773 | -0.69879 | 0 | 0
29 | 0.98772 | -0.69871 | 0.21122 | 0.1023
30 | 0.9878 | -0.69941 | 0 | 0
31 | 0.98783 | -0.7159 | 0.22768 | 0.11027
32 | 0.98779 | -0.71613 | 0 | 0
33 | 0.98808 | -0.70084 | 0.25789 | 0.1249
34 | 0.98781 | -0.69949 | 0.071035 | 0.034404
35 | 0.98801 | -0.69984 | 0.06935 | 0.033588
36 | 0.98785 | -0.69977 | 0.31553 | 0.15282
37 | 0.98789 | -0.69875 | 0.06833 | 0.033094
38 | 0.98782 | -0.69958 | 0 | 0
39 | 0.9994 | 0.0033528 | 0.10131 | 0.049068
40 | 0.99944 | 0.0029969 | 0 | 0
41 | 0.99791 | -0.0071225 | 0.11549 | 0.055936
42 | 0.9881 | -0.70066 | 0 | 0
43 | 0.98765 | -0.71682 | 0.39914 | 0.19331
44 | 0.98765 | -0.7168 | 0.068273 | 0.033066
45 | 0.98767 | -0.71694 | 0 | 0
46 | 0.98865 | -0.66767 | 0 | 0
47 | 0.98748 | -0.72473 | 0.31626 | 0.15317
48 | 0.98747 | -0.72468 | 0.15588 | 0.075494
49 | 0.98752 | -0.72209 | 0.13706 | 0.066383
50 | 0.98747 | -0.72476 | 0.071762 | 0.034756
51 | 0.99783 | -0.0064494 | 0.14832 | 0.071835
52 | 0.99784 | -0.0064917 | 0 | 0
53 | 0.99784 | -0.0065779 | 0 | 0
54 | 0.99231 | -0.43308 | 0 | 0
55 | 0.99221 | -0.43354 | 0.13108 | 0.063487
56 | 0.99079 | -0.51451 | 0 | 0
57 | 0.99061 | -0.51529 | 0 | 0
58 | 0.99099 | -0.50305 | 0.14009 | 0.067849
59 | 0.99078 | -0.51445 | 0.11371 | 0.05507
60 | 0.99786 | -0.0066733 | 0.11034 | 0.05344
61 | 0.99783 | -0.0067076 | 0 | 0
62 | 0.99781 | -0.0065652 | 0 | 0
63 | 0.99781 | -0.0065265 | 0.10076 | 0.048801
64 | 0.9978 | -0.0065115 | 0.10711 | 0.051875
65 | 0.99787 | -0.0067737 | 0 | 0
66 | 0.98546 | -0.5678 | 0.056133 | 0.027187
67 | 0.98562 | -0.56667 | 0 | 0
68 | 0.99791 | -0.0071084 | 0 | 0
69 | 0.99788 | -0.00686 | 0 | 0
70 | 0.99964 | 0.0012983 | 0 | 0
71 | 0.99975 | 0.0021045 | 0.11562 | 0.055996
72 | 0.99978 | 0.0018625 | 0 | 0
73 | 0.99787 | -0.0068309 | 0.15819 | 0.076614
74 | 0.98633 | -0.56473 | 0.12094 | 0.058574
75 | 0.98635 | -0.56489 | 0.11183 | 0.054163
76 | 0.98632 | -0.56484 | 0.11479 | 0.055593
77 | 0.98641 | -0.56447 | 0.087674 | 0.042462
78 | 0.98766 | -0.56979 | 0 | 0
79 | 0.98765 | -0.56972 | 0.10742 | 0.052025
80 | 0.98767 | -0.56971 | 0.1238 | 0.059957
81 | 0.98695 | -0.56681 | 0.15345 | 0.074318
82 | 0.98695 | -0.56683 | 0 | 0
83 | 0.98706 | -0.56788 | 0.11791 | 0.057107
84 | 0.98677 | -0.56522 | 0 | 0
85 | 0.98773 | -0.57021 | 0 | 0
86 | 0.98802 | -0.57282 | 0 | 0
87 | 0.98758 | -0.56887 | 0.11877 | 0.057521
88 | 0.98648 | -0.56404 | 0.12867 | 0.062319
89 | 0.98722 | -0.56928 | 0 | 0
90 | 0.98657 | -0.56345 | 0 | 0
91 | 0.98765 | -0.56954 | 0 | 0
92 | 0.98764 | -0.56946 | 0.098162 | 0.047542
93 | 0.98763 | -0.56957 | 0 | 0
94 | 0.98811 | -0.57361 | 0.1307 | 0.0633
95 | 0.98735 | -0.57044 | 0 | 0
96 | 0.9876 | -0.56946 | 0.13962 | 0.067621
97 | 0.98761 | -0.56942 | 0 | 0
98 | 0.98762 | -0.56953 | 0.078406 | 0.037974
99 | 0.98824 | -0.57485 | 0 | 0
100 | 0.98734 | -0.57038 | 0.10343 | 0.050093
101 | 0.98823 | -0.57473 | 0.12903 | 0.062494
102 | 0.98824 | -0.57478 | 0 | 0
103 | 0.9883 | -0.57538 | 0 | 0
104 | 0.98864 | -0.57835 | 0.094133 | 0.045591
105 | 0.98929 | -0.52981 | 0.12538 | 0.060725
106 | 0.9893 | -0.52991 | 0.14063 | 0.068111
107 | 0.98927 | -0.5297 | 0 | 0
108 | 0.98937 | -0.52941 | 0.076279 | 0.036944
109 | 0.98923 | -0.52931 | 0 | 0
110 | 0.9894 | -0.52964 | 0 | 0
111 | 0.9892 | -0.5295 | 0.10391 | 0.050324
112 | 0.9892 | -0.52949 | 0.12049 | 0.058354
113 | 0.98918 | -0.57314 | 0.12778 | 0.061888
114 | 0.98918 | -0.57315 | 0 | 0
115 | 0.98921 | -0.57303 | 0.10807 | 0.052341
116 | 0.98912 | -0.5738 | 0 | 0
117 | 0.98926 | -0.57122 | 0 | 0
118 | 0.98929 | -0.57108 | 0 | 0
119 | 0.98926 | -0.5712 | 0.080016 | 0.038754
120 | 0.98924 | -0.57129 | 0 | 0
121 | 0.98988 | -0.54254 | 0 | 0
122 | 0.98987 | -0.54245 | 0 | 0
123 | 0.9899 | -0.54272 | 0 | 0
124 | 0.98987 | -0.54244 | 0.099167 | 0.048029
125 | 0.98991 | -0.54278 | 0.11483 | 0.055616
126 | 0.98912 | -0.57376 | 0.15561 | 0.075367
127 | 0.98886 | -0.58038 | 0.14449 | 0.069979
128 | 0.98924 | -0.57125 | 0 | 0
129 | 0.9896 | -0.56045 | 0.10852 | 0.052558
130 | 0.99013 | -0.53076 | 0 | 0
131 | 0.98929 | -0.57111 | 0.095238 | 0.046126
132 | 0.98932 | -0.57099 | 0.081326 | 0.039388
133 | 0.98949 | -0.52899 | 0.093218 | 0.045148
134 | 0.98951 | -0.5289 | 0 | 0
135 | 0.9896 | -0.52976 | 0 | 0
136 | 0.98943 | -0.5294 | 0.13139 | 0.063633
137 | 0.98591 | -0.56704 | 0.12872 | 0.06234
138 | 0.98586 | -0.56658 | 0 | 0
139 | 0.98613 | -0.56548 | 0.11387 | 0.055148
140 | 0.98577 | -0.56578 | 0 | 0
141 | 0.98617 | -0.56584 | 0.084785 | 0.041063
142 | 0.98576 | -0.56569 | 0.13962 | 0.067619
143 | 0.98564 | -0.56647 | 0.10619 | 0.05143
144 | 0.98566 | -0.56639 | 0.1596 | 0.077299
145 | 0.98569 | -0.56618 | 0 | 0
146 | 0.98568 | -0.56609 | 0 | 0
147 | 0.9861 | -0.5652 | 0 | 0
148 | 0.98641 | -0.56414 | 0.067686 | 0.032782
149 | 0.98606 | -0.56484 | 0 | 0
150 | 0.98655 | -0.56322 | 0 | 0
151 | 0.98602 | -0.56512 | 0.061051 | 0.029569
152 | 0.98602 | -0.56452 | 0.11647 | 0.056407
153 | 0.98655 | -0.56328 | 0 | 0
154 | 0.98645 | -0.56426 | 0.15904 | 0.077027
155 | 0.98566 | -0.56598 | 0.083222 | 0.040306
156 | 0.98567 | -0.56602 | 0 | 0
157 | 0.98567 | -0.56607 | 0 | 0
158 | 0.98567 | -0.56605 | 0.075115 | 0.03638
159 | 0.99011 | -0.5306 | 0.064932 | 0.031448
160 | 0.99011 | -0.53058 | 0.075438 | 0.036536
161 | 0.99012 | -0.53068 | 0 | 0
162 | 0.9901 | -0.53069 | 0.11701 | 0.056669
163 | 0.98983 | -0.53179 | 0.091361 | 0.044248
164 | 0.98982 | -0.53169 | 0 | 0
165 | 0.99006 | -0.53019 | 0.12997 | 0.062948
166 | 0.9905 | -0.52142 | 0.14323 | 0.069369
167 | 0.99036 | -0.52975 | 0 | 0
168 | 0.99018 | -0.53053 | 0.070167 | 0.033983
169 | 0.99025 | -0.53022 | 0.085142 | 0.041236
170 | 0.99131 | -0.48472 | 0.15222 | 0.073722
171 | 0.99031 | -0.52929 | 0 | 0
172 | 0.99022 | -0.52985 | 0.084996 | 0.041165
173 | 0.99014 | -0.53038 | 0.15228 | 0.073753
174 | 0.99015 | -0.53028 | 0.15311 | 0.074153
175 | 0.98599 | -0.56422 | 0.11392 | 0.055174
176 | 0.98598 | -0.56432 | 0.16104 | 0.077997
177 | 0.986 | -0.56467 | 0.097846 | 0.047389
178 | 0.98601 | -0.56501 | 0 | 0
179 | 0.98601 | -0.56501 | 0.1135 | 0.054972
180 | 0.98924 | -0.57124 | 0.1193 | 0.057779
181 | 0.98966 | -0.53076 | 0.12588 | 0.060965
182 | 0.98967 | -0.53085 | 0 | 0
183 | 0.9897 | -0.53065 | 0 | 0
184 | 0.98971 | -0.53072 | 0 | 0
185 | 0.99034 | -0.52981 | 0 | 0
186 | 0.99033 | -0.52991 | 0.12037 | 0.058299
187 | 0.98969 | -0.53084 | 0.15254 | 0.07388
188 | 0.98965 | -0.53013 | 0.068051 | 0.032958
189 | 0.98949 | -0.56092 | 0.16293 | 0.07891
190 | 0.98328 | -0.89874 | 0.38733 | 0.18759
191 | 0.9833 | -0.89892 | 0 | 0
192 | 0.98335 | -0.89942 | 0 | 0
193 | 0.9854 | -0.80756 | 0 | 0
194 | 0.98526 | -0.80608 | 0 | 0
195 | 0.98539 | -0.80757 | 0.2162 | 0.10471
196 | 0.98522 | -0.80636 | 0.41198 | 0.19953
197 | 0.98338 | -0.89968 | 0 | 0
198 | 0.9852 | -0.81837 | 0.40998 | 0.19856
199 | 0.98339 | -0.89973 | 0.39507 | 0.19134
200 | 0.98432 | -0.86834 | 0.37094 | 0.17965
201 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.24861 | -0.12041 | 0.24861 | 0.12027 | 5.3079e-07 | -0.00014157 | 0.0080789 | 0.0080771 | 0.0080789 | 0.98704 | -0.75098 | 0.98704 | -0.751 | 3.6722
1 | 2.7782 | 1.0867 | -2.7769 | -1.2227 | 0.0013367 | -0.13597 | 0.087248 | 0.088783 | 0.088783 | 0.98704 | -0.751 | 0.98654 | -0.75446 | 6.9579
2 | -3.0268 | -1.207 | 3.0275 | 1.2077 | 0.00069606 | 0.00071474 | 0.095302 | 0.09529 | 0.095302 | 0.98704 | -0.751 | 0.98745 | -0.72496 | 7.3878
3 | 2.7258 | 1.1981 | -2.7257 | -1.202 | 3.7097e-05 | -0.0038458 | 0.087124 | 0.08717 | 0.08717 | 0.98654 | -0.75446 | 0.98653 | -0.75454 | 6.8315
4 | 0.051122 | 0.024546 | -0.051121 | -0.024759 | 9.0383e-07 | -0.00021313 | 0.0016594 | 0.0016621 | 0.0016621 | 0.98654 | -0.75446 | 0.98652 | -0.75458 | 0.79149
5 | -3.1755 | -1.2793 | 3.1755 | 1.2749 | 5.6377e-05 | -0.0044341 | 0.10008 | 0.10003 | 0.10008 | 0.98745 | -0.72496 | 0.98747 | -0.72482 | 7.8435
6 | 0.14793 | 0.071609 | -0.14793 | -0.071645 | 1.3278e-06 | -3.6742e-05 | 0.0048047 | 0.0048052 | 0.0048052 | 0.98745 | -0.72496 | 0.98744 | -0.72502 | 2.2882
7 | -3.1755 | -1.2749 | 3.1755 | 1.2721 | 3.4997e-05 | -0.0027549 | 0.10003 | 0.1 | 0.10003 | 0.98747 | -0.72482 | 0.98748 | -0.72473 | 7.8397
8 | 7.2598 | 3.2575 | -7.216 | -3.1524 | 0.043836 | 0.10517 | 0.22977 | 0.22991 | 0.22991 | 0.99973 | -0.015689 | 0.9887 | -0.66739 | 17.8229
9 | -7.3782 | -3.3149 | 7.3792 | 3.3175 | 0.0010844 | 0.0026081 | 0.23356 | 0.23356 | 0.23356 | 0.99973 | -0.015689 | 1 | 0 | 18.1055
10 | 6.9437 | 3.0205 | -6.9433 | -3.0256 | 0.00032599 | -0.0051173 | 0.22109 | 0.22115 | 0.22115 | 0.9887 | -0.66739 | 0.98865 | -0.66767 | 17.3315
11 | 0.95879 | 0.44116 | -0.95856 | -0.44548 | 0.00022816 | -0.0043196 | 0.030467 | 0.03052 | 0.03052 | 1 | 0 | 0.99978 | 0.0018625 | 13.8729
12 | 8.2156 | 3.9012 | -8.1815 | -3.817 | 0.034125 | 0.084157 | 0.26254 | 0.26264 | 0.26264 | 1 | 0 | 0.99231 | -0.43308 | 20.3595
13 | 2.619 | 1.1503 | -2.619 | -1.1526 | 2.0712e-05 | -0.0023277 | 0.083702 | 0.083729 | 0.083729 | 0.98653 | -0.75454 | 0.98652 | -0.75459 | 6.5619
14 | 2.5335 | 1.1112 | -2.5323 | -1.1108 | 0.0012092 | 0.000474 | 0.080954 | 0.080986 | 0.080986 | 0.98652 | -0.75459 | 0.98566 | -0.80621 | 6.278
15 | 0.33888 | 0.16293 | -0.33887 | -0.16412 | 8.3869e-06 | -0.0011974 | 0.011012 | 0.011028 | 0.011028 | 0.98566 | -0.80621 | 0.98564 | -0.806 | 5.0126
16 | 2.1934 | 0.94782 | -2.1929 | -1.0314 | 0.00052739 | -0.083581 | 0.069982 | 0.070992 | 0.070992 | 0.98566 | -0.80621 | 0.98541 | -0.80749 | 5.5636
17 | 1.7809 | 0.83863 | -1.7808 | -0.84513 | 2.7466e-05 | -0.0064988 | 0.057665 | 0.057747 | 0.057747 | 0.98541 | -0.80749 | 0.9854 | -0.80756 | 4.5256
18 | 0.41207 | 0.19277 | -0.412 | -0.19948 | 6.9271e-05 | -0.006709 | 0.013327 | 0.013412 | 0.013412 | 0.98541 | -0.80749 | 0.98526 | -0.80608 | 6.0963
19 | -0.3925 | -0.19009 | 0.39251 | 0.19005 | 1.1667e-05 | -3.957e-05 | 0.012751 | 0.01275 | 0.012751 | 0.98735 | -0.71567 | 0.98738 | -0.71547 | 6.0717
20 | -0.39251 | -0.19005 | 0.39258 | 0.182 | 7.4733e-05 | -0.0080595 | 0.01275 | 0.012649 | 0.01275 | 0.98738 | -0.71547 | 0.98755 | -0.71705 | 5.7955
21 | 0.37717 | 0.1725 | -0.37709 | -0.18253 | 8.5667e-05 | -0.010036 | 0.012124 | 0.012249 | 0.012249 | 0.98755 | -0.71705 | 0.98734 | -0.7152 | 5.5676
22 | -0.76975 | -0.35449 | 0.76979 | 0.35352 | 3.4525e-05 | -0.00097159 | 0.024772 | 0.02476 | 0.024772 | 0.98755 | -0.71705 | 0.9876 | -0.7174 | 11.2602
23 | 0.37709 | 0.18253 | -0.37706 | -0.18262 | 2.3165e-05 | -8.6325e-05 | 0.012249 | 0.01225 | 0.01225 | 0.98734 | -0.7152 | 0.98728 | -0.7156 | 5.8334
24 | 3.8568 | 1.6016 | -3.8567 | -1.6015 | 9.3717e-05 | 0.00015701 | 0.12207 | 0.12207 | 0.12207 | 0.9876 | -0.7174 | 0.98755 | -0.7201 | 9.4627
25 | -4.8859 | -2.0808 | 4.8859 | 2.0783 | 7.4734e-05 | -0.0024189 | 0.15523 | 0.1552 | 0.15523 | 0.9876 | -0.7174 | 0.98761 | -0.7173 | 12.165
26 | 3.8567 | 1.6015 | -3.8566 | -1.6014 | 6.9016e-05 | 0.00011563 | 0.12207 | 0.12207 | 0.12207 | 0.98755 | -0.7201 | 0.98752 | -0.72209 | 9.4628
27 | -4.8859 | -2.0783 | 4.8862 | 2.0699 | 0.00026066 | -0.0084446 | 0.1552 | 0.1551 | 0.1552 | 0.98761 | -0.7173 | 0.98767 | -0.71694 | 12.1628
28 | -0.25532 | -0.11991 | 0.25532 | 0.11938 | 2.0383e-06 | -0.00052349 | 0.0082424 | 0.0082359 | 0.0082424 | 0.9879 | -0.69887 | 0.98791 | -0.69893 | 3.7465
29 | 0.068331 | 0.029345 | -0.06833 | -0.032158 | 7.7258e-07 | -0.0028125 | 0.002173 | 0.0022068 | 0.0022068 | 0.9879 | -0.69887 | 0.98789 | -0.69879 | 1.0031
30 | -0.43285 | -0.20537 | 0.43286 | 0.20436 | 1.1348e-05 | -0.0010082 | 0.014 | 0.013987 | 0.014 | 0.98791 | -0.69893 | 0.98793 | -0.69915 | 6.3635
31 | 0.06833 | 0.032158 | -0.06833 | -0.032472 | 8.7861e-08 | -0.00031431 | 0.0022068 | 0.0022107 | 0.0022107 | 0.98789 | -0.69879 | 0.98789 | -0.69878 | 1.0049
32 | -1.0307 | -0.48385 | 1.0308 | 0.48249 | 8.8022e-05 | -0.0013627 | 0.033271 | 0.033254 | 0.033271 | 0.98793 | -0.69915 | 0.98801 | -0.69984 | 15.1234
33 | 0.59787 | 0.2795 | -0.59782 | -0.27955 | 4.9443e-05 | -5.5963e-05 | 0.019284 | 0.019286 | 0.019286 | 0.98793 | -0.69915 | 0.98785 | -0.69977 | 9.1836
34 | 0.06833 | 0.032472 | -0.06833 | -0.033094 | 1.7472e-07 | -0.00062174 | 0.0022107 | 0.0022186 | 0.0022186 | 0.98789 | -0.69878 | 0.98789 | -0.69875 | 1.0084
35 | 0.21122 | 0.10164 | -0.21122 | -0.1023 | 1.7856e-06 | -0.0006625 | 0.0068507 | 0.0068591 | 0.0068591 | 0.98773 | -0.69879 | 0.98772 | -0.69871 | 3.1178
36 | -0.21122 | -0.10164 | 0.21124 | 0.095418 | 1.6549e-05 | -0.0062188 | 0.0068507 | 0.0067738 | 0.0068507 | 0.98773 | -0.69879 | 0.9878 | -0.69941 | 3.114
37 | -0.21124 | -0.095418 | 0.21124 | 0.094562 | 2.247e-06 | -0.00085525 | 0.0067738 | 0.0067636 | 0.0067738 | 0.9878 | -0.69941 | 0.98781 | -0.69949 | 3.079
38 | 5.3545 | 2.2729 | -5.3543 | -2.2778 | 0.00018408 | -0.0049505 | 0.16999 | 0.17005 | 0.17005 | 0.98783 | -0.7159 | 0.98779 | -0.71613 | 13.3264
39 | -5.5821 | -2.3831 | 5.5829 | 2.3848 | 0.00076712 | 0.0016942 | 0.17737 | 0.17737 | 0.17737 | 0.98783 | -0.7159 | 0.98808 | -0.70084 | 13.7497
40 | 5.3543 | 2.2778 | -5.3536 | -2.2954 | 0.00065365 | -0.017548 | 0.17005 | 0.17025 | 0.17025 | 0.98779 | -0.71613 | 0.98767 | -0.71694 | 13.3426
41 | -5.8408 | -2.5097 | 5.841 | 2.506 | 0.00016493 | -0.0037047 | 0.18573 | 0.18569 | 0.18573 | 0.98808 | -0.70084 | 0.9881 | -0.70066 | 14.5556
42 | -0.28228 | -0.12897 | 0.28228 | 0.12828 | 3.2496e-06 | -0.00068913 | 0.0090694 | 0.009061 | 0.0090694 | 0.98781 | -0.69949 | 0.98782 | -0.69958 | 4.1224
43 | -1.1002 | -0.51608 | 1.1003 | 0.51457 | 0.00011154 | -0.0015126 | 0.035505 | 0.035486 | 0.035505 | 0.98801 | -0.69984 | 0.9881 | -0.70066 | 16.1388
44 | 0.28229 | 0.12673 | -0.28228 | -0.12828 | 7.2596e-06 | -0.0015442 | 0.0090424 | 0.009061 | 0.009061 | 0.98785 | -0.69977 | 0.98782 | -0.69958 | 4.1186
45 | -0.84261 | -0.39538 | 0.84265 | 0.39447 | 3.7102e-05 | -0.00090634 | 0.026885 | 0.026874 | 0.026885 | 0.9994 | 0.0033528 | 0.99944 | 0.0029969 | 12.2204
46 | 0.7413 | 0.34631 | -0.74026 | -0.3469 | 0.0010417 | -0.00059299 | 0.023634 | 0.023649 | 0.023649 | 0.9994 | 0.0033528 | 0.99791 | -0.0071225 | 11.2614
47 | -0.84265 | -0.39447 | 0.84283 | 0.39006 | 0.00018004 | -0.0044101 | 0.026874 | 0.026819 | 0.026874 | 0.99944 | 0.0029969 | 0.99964 | 0.0012983 | 12.2153
48 | 0.15819 | 0.072711 | -0.15819 | -0.072914 | 2.894e-07 | -0.00020301 | 0.0050365 | 0.005039 | 0.005039 | 0.99791 | -0.0071225 | 0.99791 | -0.0071084 | 2.2904
49 | 0.46657 | 0.21826 | -0.46655 | -0.21986 | 2.0053e-05 | -0.0016004 | 0.014901 | 0.01492 | 0.01492 | 0.99791 | -0.0071225 | 0.99787 | -0.0067737 | 6.782
50 | -6.9412 | -3.0206 | 6.9433 | 3.0256 | 0.0021096 | 0.0050204 | 0.22116 | 0.22115 | 0.22116 | 0.9881 | -0.70066 | 0.98865 | -0.66767 | 17.144
51 | 0.068273 | 0.032644 | -0.068273 | -0.033066 | 1.1866e-07 | -0.00042208 | 0.0022119 | 0.0022172 | 0.0022172 | 0.98765 | -0.71682 | 0.98765 | -0.7168 | 1.0078
52 | -0.46741 | -0.22596 | 0.46742 | 0.22545 | 6.6498e-06 | -0.00050208 | 0.015174 | 0.015168 | 0.015174 | 0.98765 | -0.71682 | 0.98767 | -0.71694 | 6.8974
53 | 0.15588 | 0.074855 | -0.15588 | -0.075494 | 9.3865e-07 | -0.00063931 | 0.005055 | 0.0050631 | 0.0050631 | 0.98748 | -0.72473 | 0.98747 | -0.72468 | 2.3014
54 | -3.7194 | -1.5349 | 3.7195 | 1.535 | 8.8281e-05 | 0.00014103 | 0.11763 | 0.11763 | 0.11763 | 0.98748 | -0.72473 | 0.98752 | -0.72209 | 9.1183
55 | 0.071762 | 0.034724 | -0.071762 | -0.034756 | 2.6515e-07 | -3.1723e-05 | 0.0023306 | 0.002331 | 0.002331 | 0.98748 | -0.72473 | 0.98747 | -0.72476 | 1.11
56 | -0.14832 | -0.071835 | 0.14832 | 0.071265 | 7.2642e-07 | -0.00056971 | 0.0047677 | 0.0047605 | 0.0047677 | 0.99783 | -0.0064494 | 0.99784 | -0.0064917 | 2.1671
57 | -0.14832 | -0.071265 | 0.14832 | 0.070065 | 1.5229e-06 | -0.0012 | 0.0047605 | 0.0047456 | 0.0047605 | 0.99784 | -0.0064917 | 0.99784 | -0.0065779 | 2.1639
58 | -0.3562 | -0.16745 | 0.3562 | 0.16687 | 4.1946e-06 | -0.00057524 | 0.011387 | 0.01138 | 0.011387 | 0.99784 | -0.0065779 | 0.99786 | -0.0066733 | 5.1757
59 | 0.20788 | 0.097381 | -0.20787 | -0.097434 | 3.6377e-06 | -5.2742e-05 | 0.006641 | 0.0066417 | 0.0066417 | 0.99784 | -0.0065779 | 0.99783 | -0.0067076 | 3.1627
60 | 8.1815 | 3.817 | -8.1807 | -3.8261 | 0.00082037 | -0.009058 | 0.26264 | 0.26276 | 0.26276 | 0.99231 | -0.43308 | 0.99221 | -0.43354 | 20.5921
61 | 8.0496 | 3.7626 | -8.0456 | -3.7529 | 0.0039407 | 0.0096985 | 0.25852 | 0.25853 | 0.25853 | 0.99221 | -0.43354 | 0.99131 | -0.48472 | 20.041
62 | 7.6374 | 3.5519 | -7.6361 | -3.5684 | 0.0013 | -0.016485 | 0.24541 | 0.24562 | 0.24562 | 0.99079 | -0.51451 | 0.99061 | -0.51529 | 19.2494
63 | -7.7511 | -3.6059 | 7.7519 | 3.6079 | 0.00084821 | 0.002073 | 0.24908 | 0.24907 | 0.24908 | 0.99079 | -0.51451 | 0.99099 | -0.50305 | 19.3083
64 | 0.11371 | 0.053928 | -0.11371 | -0.05507 | 8.7836e-07 | -0.0011423 | 0.0036667 | 0.0036811 | 0.0036811 | 0.99079 | -0.51451 | 0.99078 | -0.51445 | 1.6732
65 | 7.6361 | 3.5684 | -7.6356 | -3.5673 | 0.00044812 | 0.0010921 | 0.24562 | 0.24562 | 0.24562 | 0.99061 | -0.51529 | 0.9905 | -0.52142 | 19.0406
66 | -7.892 | -3.6758 | 7.8934 | 3.6792 | 0.0013825 | 0.0033906 | 0.25361 | 0.2536 | 0.25361 | 0.99099 | -0.50305 | 0.99131 | -0.48472 | 19.6596
67 | -0.46654 | -0.22031 | 0.46655 | 0.21986 | 5.7056e-06 | -0.00045456 | 0.014926 | 0.01492 | 0.014926 | 0.99786 | -0.0066733 | 0.99787 | -0.0067737 | 6.7846
68 | 0.20787 | 0.097434 | -0.20787 | -0.098881 | 3.5979e-06 | -0.0014474 | 0.0066417 | 0.0066596 | 0.0066596 | 0.99783 | -0.0067076 | 0.99781 | -0.0065652 | 3.0271
69 | 0.10076 | 0.048024 | -0.10076 | -0.048801 | 4.5631e-07 | -0.00077669 | 0.0032293 | 0.003239 | 0.003239 | 0.99781 | -0.0065652 | 0.99781 | -0.0065265 | 1.4723
70 | 0.10711 | 0.050857 | -0.10711 | -0.051875 | 6.7514e-07 | -0.0010177 | 0.0034303 | 0.0034431 | 0.0034431 | 0.99781 | -0.0065652 | 0.9978 | -0.0065115 | 1.565
71 | -0.056133 | -0.027187 | 0.056142 | 0.025502 | 8.5651e-06 | -0.0016841 | 0.001827 | 0.001806 | 0.001827 | 0.98546 | -0.5678 | 0.98562 | -0.56667 | 0.87002
72 | -0.056142 | -0.025502 | 0.056144 | 0.025126 | 1.8858e-06 | -0.00037612 | 0.001806 | 0.0018015 | 0.001806 | 0.98562 | -0.56667 | 0.98566 | -0.56639 | 0.86001
73 | 0.15819 | 0.072914 | -0.15819 | -0.076248 | 4.7944e-06 | -0.0033343 | 0.005039 | 0.0050801 | 0.0050801 | 0.99791 | -0.0071084 | 0.99788 | -0.00686 | 2.3091
74 | 0.15819 | 0.076248 | -0.15819 | -0.076614 | 5.3144e-07 | -0.00036624 | 0.0050801 | 0.0050847 | 0.0050847 | 0.99788 | -0.00686 | 0.99787 | -0.0068309 | 2.3112
75 | -0.84283 | -0.39006 | 0.84292 | 0.39003 | 8.8017e-05 | -2.6813e-05 | 0.026819 | 0.026818 | 0.026819 | 0.99964 | 0.0012983 | 0.99975 | 0.0021045 | 12.7711
76 | -0.95853 | -0.44603 | 0.95856 | 0.44548 | 2.9242e-05 | -0.00055239 | 0.030527 | 0.03052 | 0.030527 | 0.99975 | 0.0021045 | 0.99978 | 0.0018625 | 13.876
77 | -0.23573 | -0.11408 | 0.23573 | 0.1128 | 4.3008e-06 | -0.0012753 | 0.0076646 | 0.0076484 | 0.0076646 | 0.98633 | -0.56473 | 0.98635 | -0.56489 | 3.4839
78 | 0.11479 | 0.055505 | -0.11479 | -0.055593 | 1.915e-06 | -8.8411e-05 | 0.0037317 | 0.0037328 | 0.0037328 | 0.98633 | -0.56473 | 0.98632 | -0.56484 | 1.7775
79 | -0.34756 | -0.16697 | 0.34758 | 0.16687 | 2.1133e-05 | -9.4956e-05 | 0.011285 | 0.011284 | 0.011285 | 0.98635 | -0.56489 | 0.98641 | -0.56447 | 5.3738
80 | -0.43526 | -0.20933 | 0.43529 | 0.20926 | 2.7952e-05 | -7.3721e-05 | 0.014135 | 0.014133 | 0.014135 | 0.98641 | -0.56447 | 0.98648 | -0.56404 | 6.7307
81 | 0.10742 | 0.050739 | -0.10742 | -0.052025 | 8.9345e-07 | -0.0012865 | 0.0034723 | 0.0034885 | 0.0034885 | 0.98766 | -0.56979 | 0.98765 | -0.56972 | 1.5857
82 | -0.10742 | -0.050739 | 0.10742 | 0.050679 | 1.1213e-06 | -6.0099e-05 | 0.0034723 | 0.0034715 | 0.0034723 | 0.98766 | -0.56979 | 0.98767 | -0.56971 | 1.6535
83 | 0.31621 | 0.14838 | -0.3162 | -0.14946 | 6.5079e-06 | -0.001086 | 0.010209 | 0.010223 | 0.010223 | 0.98767 | -0.56971 | 0.98765 | -0.56954 | 4.6466
84 | -0.54742 | -0.25901 | 0.54746 | 0.25716 | 3.3469e-05 | -0.0018563 | 0.017701 | 0.017677 | 0.017701 | 0.98767 | -0.56971 | 0.98773 | -0.57021 | 8.0457
85 | -0.15345 | -0.074318 | 0.15345 | 0.07414 | 2.5434e-07 | -0.00017816 | 0.0049869 | 0.0049847 | 0.0049869 | 0.98695 | -0.56681 | 0.98695 | -0.56683 | 2.2668
86 | -2.5574 | -1.2121 | 2.5577 | 1.2113 | 0.00032442 | -0.00072879 | 0.082777 | 0.082767 | 0.082777 | 0.98695 | -0.56683 | 0.98706 | -0.56788 | 37.626
87 | 2.4039 | 1.1379 | -2.4035 | -1.1391 | 0.00046628 | -0.0012034 | 0.077793 | 0.07781 | 0.07781 | 0.98695 | -0.56683 | 0.98677 | -0.56522 | 35.368
88 | -2.6756 | -1.2684 | 2.6761 | 1.2675 | 0.00045015 | -0.00091274 | 0.086598 | 0.086585 | 0.086598 | 0.98706 | -0.56788 | 0.98722 | -0.56928 | 39.3629
89 | 2.4035 | 1.1391 | -2.4029 | -1.1405 | 0.00051271 | -0.001322 | 0.07781 | 0.077828 | 0.077828 | 0.98677 | -0.56522 | 0.98657 | -0.56345 | 35.3764
90 | -3.4472 | -1.6298 | 3.4483 | 1.6286 | 0.0010914 | -0.0012103 | 0.11144 | 0.11142 | 0.11144 | 0.98773 | -0.57021 | 0.98802 | -0.57282 | 50.6548
91 | 2.8997 | 1.3727 | -2.8992 | -1.3734 | 0.00046907 | -0.00079156 | 0.093763 | 0.093775 | 0.093775 | 0.98773 | -0.57021 | 0.98758 | -0.56887 | 42.625
92 | -3.4483 | -1.6286 | 3.4486 | 1.6282 | 0.00033159 | -0.00036802 | 0.11142 | 0.11142 | 0.11142 | 0.98802 | -0.57282 | 0.98811 | -0.57361 | 50.6461
93 | 2.7805 | 1.3159 | -2.7799 | -1.3156 | 0.00060933 | 0.00033243 | 0.089918 | 0.089918 | 0.089918 | 0.98758 | -0.56887 | 0.98735 | -0.57044 | 42.8183
94 | 0.15905 | 0.076899 | -0.15904 | -0.077027 | 5.3601e-06 | -0.00012737 | 0.0051696 | 0.0051713 | 0.0051713 | 0.98648 | -0.56404 | 0.98645 | -0.56426 | 2.4625
95 | -0.72301 | -0.34848 | 0.72307 | 0.34844 | 6.3518e-05 | -3.5305e-05 | 0.023487 | 0.023486 | 0.023487 | 0.98648 | -0.56404 | 0.98657 | -0.56345 | 11.1841
96 | -2.6761 | -1.2675 | 2.6764 | 1.2668 | 0.00037781 | -0.00076657 | 0.086585 | 0.086574 | 0.086585 | 0.98722 | -0.56928 | 0.98735 | -0.57044 | 39.357
97 | 1.6799 | 0.79201 | -1.6798 | -0.7922 | 3.4147e-05 | -0.00019114 | 0.054343 | 0.054345 | 0.054345 | 0.98657 | -0.56345 | 0.98655 | -0.56328 | 24.7025
98 | 0.3162 | 0.14946 | -0.3162 | -0.15001 | 3.2901e-06 | -0.00054792 | 0.010223 | 0.010229 | 0.010229 | 0.98765 | -0.56954 | 0.98764 | -0.56946 | 4.6497
99 | 0.21803 | 0.10247 | -0.21803 | -0.10251 | 3.2631e-06 | -4.0964e-05 | 0.0070416 | 0.0070421 | 0.0070421 | 0.98764 | -0.56946 | 0.98763 | -0.56957 | 3.3534
100 | 0.078407 | 0.037055 | -0.078406 | -0.037974 | 3.3993e-07 | -0.00091862 | 0.0025348 | 0.0025464 | 0.0025464 | 0.98763 | -0.56957 | 0.98762 | -0.56953 | 1.1575
101 | 0.13962 | 0.065454 | -0.13962 | -0.06759 | 2.5026e-06 | -0.0021355 | 0.0045073 | 0.0045342 | 0.0045342 | 0.98763 | -0.56957 | 0.98761 | -0.56942 | 2.061
102 | -3.5793 | -1.6915 | 3.5798 | 1.691 | 0.00053734 | -0.0005422 | 0.11566 | 0.11565 | 0.11566 | 0.98811 | -0.57361 | 0.98824 | -0.57485 | 52.5718
103 | 0.10343 | 0.048823 | -0.10343 | -0.050093 | 8.1861e-07 | -0.00127 | 0.003344 | 0.00336 | 0.00336 | 0.98735 | -0.57044 | 0.98734 | -0.57038 | 1.5273
104 | -0.13962 | -0.067621 | 0.13962 | 0.06759 | 1.0123e-06 | -3.1542e-05 | 0.0045346 | 0.0045342 | 0.0045346 | 0.9876 | -0.56946 | 0.98761 | -0.56942 | 2.1593
105 | -3.7089 | -1.7516 | 3.7091 | 1.7514 | 0.00023863 | -0.00021959 | 0.11981 | 0.11981 | 0.11981 | 0.98824 | -0.57485 | 0.9883 | -0.57538 | 54.4609
106 | 0.12904 | 0.060635 | -0.12904 | -0.061686 | 1.0474e-06 | -0.0010511 | 0.0041647 | 0.0041778 | 0.0041778 | 0.98824 | -0.57485 | 0.98824 | -0.57478 | 1.899
107 | -0.12903 | -0.062494 | 0.12904 | 0.061686 | 8.0949e-07 | -0.00080783 | 0.0041881 | 0.0041778 | 0.0041881 | 0.98823 | -0.57473 | 0.98824 | -0.57478 | 1.9037
108 | -3.7091 | -1.7514 | 3.7104 | 1.7502 | 0.001341 | -0.0012349 | 0.11981 | 0.11979 | 0.11981 | 0.9883 | -0.57538 | 0.98864 | -0.57835 | 54.4592
109 | -3.8046 | -1.7958 | 3.8055 | 1.795 | 0.00094005 | -0.00081045 | 0.12284 | 0.12283 | 0.12284 | 0.98864 | -0.57835 | 0.98886 | -0.58038 | 55.8381
110 | -0.34979 | -0.16469 | 0.3498 | 0.16411 | 4.2095e-06 | -0.00057803 | 0.011282 | 0.011275 | 0.011282 | 0.98929 | -0.52981 | 0.9893 | -0.52991 | 5.1281
111 | 0.22441 | 0.10396 | -0.22441 | -0.10504 | 3.1993e-06 | -0.0010722 | 0.0072169 | 0.0072302 | 0.0072302 | 0.98929 | -0.52981 | 0.98927 | -0.5297 | 3.2864
112 | -0.49043 | -0.23222 | 0.49046 | 0.23215 | 3.4432e-05 | -6.8509e-05 | 0.015834 | 0.015833 | 0.015834 | 0.9893 | -0.52991 | 0.98937 | -0.52941 | 7.5399
113 | 0.22441 | 0.10504 | -0.2244 | -0.1085 | 1.0413e-05 | -0.0034625 | 0.0072302 | 0.0072736 | 0.0072736 | 0.98927 | -0.5297 | 0.98923 | -0.52931 | 3.3062
114 | -0.56674 | -0.2691 | 0.56676 | 0.26827 | 1.5897e-05 | -0.0008263 | 0.018306 | 0.018295 | 0.018306 | 0.98937 | -0.52941 | 0.9894 | -0.52964 | 8.3207
115 | 0.2244 | 0.1085 | -0.22439 | -0.10857 | 6.3237e-06 | -7.4399e-05 | 0.0072736 | 0.0072746 | 0.0072746 | 0.98923 | -0.52931 | 0.9892 | -0.5295 | 3.4641
116 | -0.56676 | -0.26827 | 0.56678 | 0.26825 | 1.8826e-05 | -2.5101e-05 | 0.018295 | 0.018295 | 0.018295 | 0.9894 | -0.52964 | 0.98943 | -0.5294 | 8.712
117 | 0.12049 | 0.058249 | -0.12049 | -0.058354 | 9.1714e-08 | -0.00010518 | 0.0039054 | 0.0039068 | 0.0039068 | 0.9892 | -0.5295 | 0.9892 | -0.52949 | 1.7758
118 | -0.12778 | -0.061888 | 0.12778 | 0.061732 | 1.535e-07 | -0.00015651 | 0.0041435 | 0.0041415 | 0.0041435 | 0.98918 | -0.57314 | 0.98918 | -0.57315 | 1.8834
119 | -4.2344 | -2.0018 | 4.2346 | 2.0006 | 0.00011668 | -0.0011771 | 0.13669 | 0.13667 | 0.13669 | 0.98918 | -0.57315 | 0.98921 | -0.57303 | 21.4243
120 | 4.1067 | 1.94 | -4.1064 | -1.9408 | 0.00022403 | -0.00072331 | 0.13255 | 0.13256 | 0.13256 | 0.98918 | -0.57315 | 0.98912 | -0.5738 | 36.6178
121 | -4.3426 | -2.0529 | 4.3427 | 2.0531 | 7.2663e-05 | 0.00013935 | 0.14018 | 0.14017 | 0.14018 | 0.98921 | -0.57303 | 0.98924 | -0.57129 | 10.8663
122 | 0.15561 | 0.074946 | -0.15561 | -0.075367 | 6.1169e-07 | -0.00042059 | 0.0050408 | 0.0050462 | 0.0050462 | 0.98912 | -0.5738 | 0.98912 | -0.57376 | 2.2937
123 | 3.9508 | 1.8658 | -3.95 | -1.8649 | 0.0008259 | 0.00087665 | 0.12752 | 0.12752 | 0.12752 | 0.98912 | -0.5738 | 0.98886 | -0.58038 | 36.4333
124 | -4.5421 | -2.1452 | 4.5422 | 2.1398 | 0.00014756 | -0.0053861 | 0.14658 | 0.14651 | 0.14658 | 0.98926 | -0.57122 | 0.98929 | -0.57108 | 11.4876
125 | 0.080016 | 0.038304 | -0.080016 | -0.038754 | 1.7273e-07 | -0.00045012 | 0.0025887 | 0.0025944 | 0.0025944 | 0.98926 | -0.57122 | 0.98926 | -0.5712 | 1.1793
126 | 4.4621 | 2.1069 | -4.462 | -2.11 | 8.0922e-05 | -0.0030602 | 0.14399 | 0.14403 | 0.14403 | 0.98926 | -0.57122 | 0.98924 | -0.57129 | 11.2877
127 | -4.6375 | -2.1859 | 4.6376 | 2.1826 | 9.4338e-05 | -0.0033033 | 0.1496 | 0.14956 | 0.1496 | 0.98929 | -0.57108 | 0.98932 | -0.57099 | 11.7242
128 | 0.095239 | 0.046097 | -0.095238 | -0.046126 | 4.2598e-07 | -2.9034e-05 | 0.0030875 | 0.0030878 | 0.0030878 | 0.98929 | -0.57108 | 0.98929 | -0.57111 | 1.4704
129 | 0.1193 | 0.056898 | -0.1193 | -0.057639 | 6.3196e-07 | -0.00074151 | 0.003857 | 0.0038664 | 0.0038664 | 0.98924 | -0.57129 | 0.98924 | -0.57125 | 1.7574
130 | 0.099168 | 0.046 | -0.099167 | -0.047693 | 9.8844e-07 | -0.0016929 | 0.003188 | 0.0032091 | 0.0032091 | 0.98988 | -0.54254 | 0.98987 | -0.54245 | 1.4587
131 | -0.099168 | -0.046 | 0.099171 | 0.041278 | 2.6904e-06 | -0.0047219 | 0.003188 | 0.0031325 | 0.003188 | 0.98988 | -0.54254 | 0.9899 | -0.54272 | 1.4491
132 | 0.099167 | 0.047693 | -0.099167 | -0.048029 | 1.9779e-07 | -0.00033607 | 0.0032091 | 0.0032134 | 0.0032134 | 0.98987 | -0.54245 | 0.98987 | -0.54244 | 1.4606
133 | -0.099171 | -0.041278 | 0.099172 | 0.039327 | 1.0851e-06 | -0.0019511 | 0.0031325 | 0.0031111 | 0.0031325 | 0.9899 | -0.54272 | 0.98991 | -0.54278 | 1.4239
134 | 4.9922 | 2.3396 | -4.9913 | -2.3378 | 0.00084546 | 0.0017773 | 0.16077 | 0.16078 | 0.16078 | 0.98991 | -0.54278 | 0.9896 | -0.56045 | 12.4636
135 | -5.2062 | -2.4345 | 5.2068 | 2.4358 | 0.00059945 | 0.001288 | 0.1676 | 0.1676 | 0.1676 | 0.98991 | -0.54278 | 0.99013 | -0.53076 | 12.9923
136 | 0.1193 | 0.057639 | -0.1193 | -0.057779 | 1.1912e-07 | -0.00013938 | 0.0038664 | 0.0038681 | 0.0038681 | 0.98924 | -0.57125 | 0.98924 | -0.57124 | 1.7582
137 | 4.8828 | 2.2852 | -4.8823 | -2.3018 | 0.00052528 | -0.016597 | 0.15726 | 0.15747 | 0.15747 | 0.9896 | -0.56045 | 0.98949 | -0.56092 | 12.3411
138 | -6.8241 | -3.2007 | 6.8245 | 3.1951 | 0.00035534 | -0.0056692 | 0.21976 | 0.21968 | 0.21976 | 0.99013 | -0.53076 | 0.99018 | -0.53053 | 17.2224
139 | 1.3599 | 0.64197 | -1.3598 | -0.64279 | 9.3101e-05 | -0.00082125 | 0.043845 | 0.043856 | 0.043856 | 0.99013 | -0.53076 | 0.99006 | -0.53019 | 19.9344
140 | 0.25738 | 0.12296 | -0.25738 | -0.12358 | 2.4619e-06 | -0.00062278 | 0.0083165 | 0.0083243 | 0.0083243 | 0.99013 | -0.53076 | 0.99012 | -0.53068 | 3.7838
141 | -4.7189 | -2.222 | 4.7194 | 2.2229 | 0.00045673 | 0.00092923 | 0.1522 | 0.15219 | 0.1522 | 0.98932 | -0.57099 | 0.98949 | -0.56092 | 11.7981
142 | -0.093218 | -0.045148 | 0.09322 | 0.045053 | 1.3239e-06 | -9.4333e-05 | 0.0030217 | 0.0030205 | 0.0030217 | 0.98949 | -0.52899 | 0.98951 | -0.5289 | 1.4389
143 | -0.79143 | -0.3769 | 0.79152 | 0.37472 | 8.2199e-05 | -0.0021792 | 0.025573 | 0.025546 | 0.025573 | 0.98951 | -0.5289 | 0.9896 | -0.52976 | 11.6243
144 | 0.69821 | 0.33185 | -0.69816 | -0.33188 | 5.0265e-05 | -3.3341e-05 | 0.022553 | 0.022554 | 0.022554 | 0.98951 | -0.5289 | 0.98943 | -0.5294 | 10.7399
145 | -0.79152 | -0.37472 | 0.79155 | 0.37377 | 3.573e-05 | -0.00094885 | 0.025546 | 0.025534 | 0.025546 | 0.9896 | -0.52976 | 0.98965 | -0.53013 | 11.6118
146 | 0.62004 | 0.28872 | -0.62 | -0.29022 | 3.5008e-05 | -0.0015055 | 0.020026 | 0.020045 | 0.020045 | 0.98591 | -0.56704 | 0.98586 | -0.56658 | 9.1115
147 | -0.74875 | -0.35106 | 0.74891 | 0.35098 | 0.00015778 | -7.6495e-05 | 0.024214 | 0.024211 | 0.024214 | 0.98591 | -0.56704 | 0.98613 | -0.56548 | 11.5303
148 | 0.62 | 0.29022 | -0.61994 | -0.29283 | 6.0822e-05 | -0.0026086 | 0.020045 | 0.020078 | 0.020078 | 0.98586 | -0.56658 | 0.98577 | -0.56578 | 9.1264
149 | -0.86278 | -0.40613 | 0.86281 | 0.40527 | 3.8913e-05 | -0.00085735 | 0.027915 | 0.027904 | 0.027915 | 0.98613 | -0.56548 | 0.98617 | -0.56584 | 12.6886
150 | 0.61994 | 0.29283 | -0.61993 | -0.29312 | 6.7548e-06 | -0.00028915 | 0.020078 | 0.020082 | 0.020082 | 0.98577 | -0.56578 | 0.98576 | -0.56569 | 9.128
151 | 0.66395 | 0.31293 | -0.6639 | -0.31487 | 5.2028e-05 | -0.0019425 | 0.021486 | 0.02151 | 0.02151 | 0.98617 | -0.56584 | 0.9861 | -0.5652 | 9.7774
152 | -1.6115 | -0.75926 | 1.6119 | 0.75941 | 0.000376 | 0.00014539 | 0.052147 | 0.052146 | 0.052147 | 0.98617 | -0.56584 | 0.98641 | -0.56414 | 24.832
153 | 0.48032 | 0.2255 | -0.48029 | -0.22557 | 3.1488e-05 | -6.5172e-05 | 0.015539 | 0.01554 | 0.01554 | 0.98576 | -0.56569 | 0.98569 | -0.56618 | 7.4
154 | -0.10619 | -0.05143 | 0.10619 | 0.051364 | 1.2271e-06 | -6.6138e-05 | 0.0034556 | 0.0034548 | 0.0034556 | 0.98564 | -0.56647 | 0.98566 | -0.56639 | 1.6455
155 | -0.32194 | -0.15379 | 0.32195 | 0.15374 | 9.894e-06 | -5.2794e-05 | 0.010449 | 0.010449 | 0.010449 | 0.98566 | -0.56639 | 0.98569 | -0.56618 | 4.9759
156 | 0.15834 | 0.07183 | -0.15834 | -0.073072 | 1.8599e-06 | -0.0012421 | 0.0050921 | 0.0051072 | 0.0051072 | 0.98569 | -0.56618 | 0.98568 | -0.56609 | 2.3215
157 | 0.075115 | 0.035445 | -0.075115 | -0.035874 | 1.4627e-07 | -0.00042854 | 0.0024325 | 0.0024379 | 0.0024379 | 0.98568 | -0.56609 | 0.98567 | -0.56607 | 1.1081
158 | 0.083223 | 0.037627 | -0.083222 | -0.039448 | 7.5617e-07 | -0.001821 | 0.0026749 | 0.0026973 | 0.0026973 | 0.98568 | -0.56609 | 0.98567 | -0.56602 | 1.226
159 | 0.6639 | 0.31487 | -0.66387 | -0.31591 | 2.8065e-05 | -0.0010459 | 0.02151 | 0.021524 | 0.021524 | 0.9861 | -0.5652 | 0.98606 | -0.56484 | 9.7834
160 | -1.6796 | -0.79219 | 1.6798 | 0.79227 | 0.00021375 | 8.6698e-05 | 0.054347 | 0.054346 | 0.054347 | 0.98641 | -0.56414 | 0.98655 | -0.56322 | 25.8795
161 | 0.17456 | 0.082498 | -0.17456 | -0.082628 | 6.6167e-06 | -0.00013073 | 0.0056524 | 0.0056541 | 0.0056541 | 0.98606 | -0.56484 | 0.98602 | -0.56512 | 2.6924
162 | 0.48931 | 0.23342 | -0.48929 | -0.23471 | 1.89e-05 | -0.0012977 | 0.015871 | 0.015888 | 0.015888 | 0.98606 | -0.56484 | 0.98602 | -0.56452 | 7.2217
163 | -1.6798 | -0.79227 | 1.6798 | 0.7922 | 1.2298e-05 | -6.8832e-05 | 0.054346 | 0.054345 | 0.054346 | 0.98655 | -0.56322 | 0.98655 | -0.56328 | 24.7029
164 | 0.1135 | 0.05306 | -0.1135 | -0.054865 | 1.4057e-06 | -0.0018049 | 0.0036682 | 0.0036909 | 0.0036909 | 0.98602 | -0.56512 | 0.98601 | -0.56501 | 1.6777
165 | 0.097848 | 0.047248 | -0.097846 | -0.047389 | 2.2137e-06 | -0.00014103 | 0.0031811 | 0.003183 | 0.003183 | 0.98602 | -0.56452 | 0.986 | -0.56467 | 1.5157
166 | 0.27497 | 0.13106 | -0.27496 | -0.13312 | 9.4552e-06 | -0.0020584 | 0.008918 | 0.0089441 | 0.0089441 | 0.98602 | -0.56452 | 0.98599 | -0.56422 | 4.0655
167 | -0.083222 | -0.040306 | 0.083222 | 0.039448 | 3.6084e-07 | -0.00085823 | 0.0027082 | 0.0026973 | 0.0027082 | 0.98566 | -0.56598 | 0.98567 | -0.56602 | 1.231
168 | 0.075115 | 0.035874 | -0.075115 | -0.03638 | 1.7354e-07 | -0.00050599 | 0.0024379 | 0.0024443 | 0.0024443 | 0.98567 | -0.56607 | 0.98567 | -0.56605 | 1.1111
169 | 0.075439 | 0.036105 | -0.075438 | -0.036536 | 1.468e-07 | -0.00043185 | 0.0024384 | 0.0024439 | 0.0024439 | 0.99011 | -0.5306 | 0.99011 | -0.53058 | 1.1108
170 | -0.25738 | -0.12415 | 0.25738 | 0.12358 | 2.2567e-06 | -0.00056983 | 0.0083315 | 0.0083243 | 0.0083315 | 0.99011 | -0.5306 | 0.99012 | -0.53068 | 3.7871
171 | 0.11701 | 0.056601 | -0.11701 | -0.056669 | 1.491e-06 | -6.7242e-05 | 0.0037897 | 0.0037905 | 0.0037905 | 0.99011 | -0.5306 | 0.9901 | -0.53069 | 1.805
172 | 1.1382 | 0.53553 | -1.1382 | -0.53572 | 1.4565e-05 | -0.0001853 | 0.036686 | 0.036689 | 0.036689 | 0.98983 | -0.53179 | 0.98982 | -0.53169 | 16.6767
173 | -1.2296 | -0.57978 | 1.2299 | 0.57984 | 0.00027034 | 5.6396e-05 | 0.039647 | 0.039645 | 0.039647 | 0.98983 | -0.53179 | 0.99006 | -0.53019 | 18.8794
174 | 1.1382 | 0.53572 | -1.1381 | -0.53743 | 0.00013441 | -0.0017085 | 0.036689 | 0.03671 | 0.03671 | 0.98982 | -0.53169 | 0.98971 | -0.53072 | 16.6866
175 | 7.4924 | 3.498 | -7.4918 | -3.4965 | 0.00059651 | 0.001448 | 0.24099 | 0.24099 | 0.24099 | 0.9905 | -0.52142 | 0.99036 | -0.52975 | 18.6813
176 | 0.39046 | 0.18648 | -0.39044 | -0.18878 | 2.0904e-05 | -0.0022934 | 0.012613 | 0.012642 | 0.012642 | 0.99036 | -0.52975 | 0.99031 | -0.52929 | 5.7463
177 | 7.1013 | 3.31 | -7.1013 | -3.3114 | 9.4665e-05 | -0.0013945 | 0.22838 | 0.22839 | 0.22839 | 0.99036 | -0.52975 | 0.99034 | -0.52981 | 17.8992
178 | -6.8946 | -3.2291 | 6.8951 | 3.2217 | 0.0004673 | -0.0073048 | 0.22196 | 0.22186 | 0.22196 | 0.99018 | -0.53053 | 0.99025 | -0.53022 | 17.3948
179 | -6.9802 | -3.263 | 6.9809 | 3.2532 | 0.00064072 | -0.009774 | 0.22462 | 0.2245 | 0.22462 | 0.99025 | -0.53022 | 0.99034 | -0.52981 | 17.6036
180 | 0.39044 | 0.18878 | -0.39041 | -0.18889 | 3.3156e-05 | -0.00011553 | 0.012642 | 0.012644 | 0.012644 | 0.99031 | -0.52929 | 0.99022 | -0.52985 | 6.0207
181 | 0.30541 | 0.14773 | -0.30539 | -0.14785 | 1.9943e-05 | -0.00012142 | 0.0098904 | 0.0098921 | 0.0098921 | 0.99022 | -0.52985 | 0.99015 | -0.53028 | 4.7105
182 | -0.15228 | -0.073753 | 0.15228 | 0.073695 | 2.1916e-06 | -5.7794e-05 | 0.0049331 | 0.0049323 | 0.0049331 | 0.99014 | -0.53038 | 0.99015 | -0.53028 | 2.3491
183 | 0.16105 | 0.077944 | -0.16104 | -0.077997 | 2.2675e-06 | -5.2401e-05 | 0.0052382 | 0.0052389 | 0.0052389 | 0.98599 | -0.56422 | 0.98598 | -0.56432 | 2.4947
184 | 0.1135 | 0.054865 | -0.1135 | -0.054972 | 8.3795e-08 | -0.00010687 | 0.0036909 | 0.0036923 | 0.0036923 | 0.98601 | -0.56501 | 0.98601 | -0.56501 | 1.6783
185 | -0.12588 | -0.060965 | 0.12588 | 0.059501 | 1.3858e-06 | -0.0014648 | 0.0040797 | 0.0040613 | 0.0040797 | 0.98966 | -0.53076 | 0.98967 | -0.53085 | 1.8544
186 | -0.12588 | -0.059501 | 0.12588 | 0.059366 | 3.4325e-06 | -0.00013449 | 0.0040613 | 0.0040595 | 0.0040613 | 0.98967 | -0.53085 | 0.9897 | -0.53065 | 1.9339
187 | -0.12588 | -0.059366 | 0.12588 | 0.058264 | 1.0337e-06 | -0.0011022 | 0.0040595 | 0.0040459 | 0.0040595 | 0.9897 | -0.53065 | 0.98971 | -0.53072 | 1.8452
188 | 0.85966 | 0.40536 | -0.8596 | -0.40673 | 6.096e-05 | -0.0013706 | 0.027722 | 0.027739 | 0.027739 | 0.98971 | -0.53072 | 0.98965 | -0.53013 | 12.6088
189 | 0.15254 | 0.073806 | -0.15254 | -0.07388 | 2.8126e-06 | -7.378e-05 | 0.0049428 | 0.0049438 | 0.0049438 | 0.98971 | -0.53072 | 0.98969 | -0.53084 | 2.3542
190 | 0.12037 | 0.058222 | -0.12037 | -0.058299 | 1.8179e-06 | -7.7475e-05 | 0.0038977 | 0.0038987 | 0.0038987 | 0.99034 | -0.52981 | 0.99033 | -0.52991 | 1.8565
191 | -0.38733 | -0.18759 | 0.38734 | 0.18673 | 7.9823e-06 | -0.00086301 | 0.012635 | 0.012624 | 0.012635 | 0.98328 | -0.89874 | 0.9833 | -0.89892 | 5.7432
192 | -0.38734 | -0.18673 | 0.38736 | 0.18424 | 2.2951e-05 | -0.00249 | 0.012624 | 0.012592 | 0.012624 | 0.9833 | -0.89892 | 0.98335 | -0.89942 | 5.7381
193 | -0.38736 | -0.18424 | 0.38738 | 0.1829 | 1.2314e-05 | -0.0013413 | 0.012592 | 0.012575 | 0.012592 | 0.98335 | -0.89942 | 0.98338 | -0.89968 | 5.7238
194 | 1.7808 | 0.84513 | -1.7808 | -0.84686 | 7.2955e-06 | -0.0017231 | 0.057747 | 0.057768 | 0.057768 | 0.9854 | -0.80756 | 0.98539 | -0.80757 | 4.5273
195 | 0.412 | 0.19948 | -0.41198 | -0.19953 | 1.7118e-05 | -5.1169e-05 | 0.013412 | 0.013413 | 0.013413 | 0.98526 | -0.80608 | 0.98522 | -0.80636 | 6.387
196 | 1.5646 | 0.74214 | -1.5645 | -0.74266 | 0.00016306 | -0.00051395 | 0.050731 | 0.050743 | 0.050743 | 0.98539 | -0.80757 | 0.9852 | -0.81837 | 3.9336
197 | -0.38738 | -0.1829 | 0.38738 | 0.18266 | 2.1679e-06 | -0.00023651 | 0.012575 | 0.012572 | 0.012575 | 0.98338 | -0.89968 | 0.98339 | -0.89973 | 5.7161
198 | 1.1545 | 0.5441 | -1.1539 | -0.54856 | 0.00055612 | -0.0044654 | 0.037396 | 0.037471 | 0.037471 | 0.9852 | -0.81837 | 0.98432 | -0.86834 | 2.9047
199 | -0.78244 | -0.374 | 0.78298 | 0.36891 | 0.00053981 | -0.0050915 | 0.025458 | 0.025384 | 0.025458 | 0.98339 | -0.89973 | 0.98432 | -0.86834 | 3.1046

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.5676 | 7.6703

## res_load
| p_mw | q_mvar
0 | 0.24861 | 0.12041
1 | 0.14793 | 0.071645
2 | 0.11835 | 0.057319
3 | 0.27231 | 0.13189
4 | 0.10673 | 0.051694
5 | 0.051121 | 0.024759
6 | 0.085425 | 0.041373
7 | 0.33887 | 0.16412
8 | 0.3925 | 0.19009
9 | 0.25931 | 0.12559
10 | 0.37706 | 0.18262
11 | 0.18698 | 0.090561
12 | 0.17753 | 0.085984
13 | 0.21122 | 0.1023
14 | 0.22768 | 0.11027
15 | 0.25789 | 0.1249
16 | 0.071035 | 0.034404
17 | 0.06935 | 0.033588
18 | 0.31553 | 0.15282
19 | 0.06833 | 0.033094
20 | 0.10131 | 0.049068
21 | 0.11549 | 0.055936
22 | 0.39914 | 0.19331
23 | 0.068273 | 0.033066
24 | 0.31626 | 0.15317
25 | 0.15588 | 0.075494
26 | 0.13706 | 0.066383
27 | 0.071762 | 0.034756
28 | 0.14832 | 0.071835
29 | 0.13108 | 0.063487
30 | 0.14009 | 0.067849
31 | 0.11371 | 0.05507
32 | 0.11034 | 0.05344
33 | 0.10076 | 0.048801
34 | 0.10711 | 0.051875
35 | 0.056133 | 0.027187
36 | 0.11562 | 0.055996
37 | 0.15819 | 0.076614
38 | 0.12094 | 0.058574
39 | 0.11183 | 0.054163
40 | 0.11479 | 0.055593
41 | 0.087674 | 0.042462
42 | 0.10742 | 0.052025
43 | 0.1238 | 0.059957
44 | 0.15345 | 0.074318
45 | 0.11791 | 0.057107
46 | 0.11877 | 0.057521
47 | 0.12867 | 0.062319
48 | 0.098162 | 0.047542
49 | 0.1307 | 0.0633
50 | 0.13962 | 0.067621
51 | 0.078406 | 0.037974
52 | 0.10343 | 0.050093
53 | 0.12903 | 0.062494
54 | 0.094133 | 0.045591
55 | 0.12538 | 0.060725
56 | 0.14063 | 0.068111
57 | 0.076279 | 0.036944
58 | 0.10391 | 0.050324
59 | 0.12049 | 0.058354
60 | 0.12778 | 0.061888
61 | 0.10807 | 0.052341
62 | 0.080016 | 0.038754
63 | 0.099167 | 0.048029
64 | 0.11483 | 0.055616
65 | 0.15561 | 0.075367
66 | 0.14449 | 0.069979
67 | 0.10852 | 0.052558
68 | 0.095238 | 0.046126
69 | 0.081326 | 0.039388
70 | 0.093218 | 0.045148
71 | 0.13139 | 0.063633
72 | 0.12872 | 0.06234
73 | 0.11387 | 0.055148
74 | 0.084785 | 0.041063
75 | 0.13962 | 0.067619
76 | 0.10619 | 0.05143
77 | 0.1596 | 0.077299
78 | 0.067686 | 0.032782
79 | 0.061051 | 0.029569
80 | 0.11647 | 0.056407
81 | 0.15904 | 0.077027
82 | 0.083222 | 0.040306
83 | 0.075115 | 0.03638
84 | 0.064932 | 0.031448
85 | 0.075438 | 0.036536
86 | 0.11701 | 0.056669
87 | 0.091361 | 0.044248
88 | 0.12997 | 0.062948
89 | 0.14323 | 0.069369
90 | 0.070167 | 0.033983
91 | 0.085142 | 0.041236
92 | 0.15222 | 0.073722
93 | 0.084996 | 0.041165
94 | 0.15228 | 0.073753
95 | 0.15311 | 0.074153
96 | 0.11392 | 0.055174
97 | 0.16104 | 0.077997
98 | 0.097846 | 0.047389
99 | 0.1135 | 0.054972
100 | 0.1193 | 0.057779
101 | 0.12588 | 0.060965
102 | 0.12037 | 0.058299
103 | 0.15254 | 0.07388
104 | 0.068051 | 0.032958
105 | 0.16293 | 0.07891
106 | 0.38733 | 0.18759
107 | 0.2162 | 0.10471
108 | 0.41198 | 0.19953
109 | 0.40998 | 0.19856
110 | 0.39507 | 0.19134
111 | 0.37094 | 0.17965

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1