## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_9_2_node_19 | 20 | n |  | TRUE
1 | bus_MV_9_2_node_20 | 20 | n |  | TRUE
2 | bus_MV_9_2_node_21 | 20 | n |  | TRUE
3 | bus_MV_9_2_node_40 | 20 | n |  | TRUE
4 | bus_MV_9_2_node_44 | 20 | n |  | TRUE
5 | bus_MV_9_2_node_136 | 20 | n |  | TRUE
6 | bus_MV_9_2_node_42 | 20 | n |  | TRUE
7 | bus_MV_9_2_node_105 | 20 | n |  | TRUE
8 | bus_MV_9_2_node_117 | 20 | n |  | TRUE
9 | bus_MV_9_2_node_39 | 20 | n |  | TRUE
10 | bus_MV_9_2_node_46 | 20 | n |  | TRUE
11 | bus_MV_9_2_node_36 | 20 | n |  | TRUE
12 | bus_MV_9_2_node_22 | 20 | n |  | TRUE
13 | bus_MV_9_2_node_24 | 20 | n |  | TRUE
14 | bus_MV_9_2_node_23 | 20 | n |  | TRUE
15 | bus_MV_9_2_node_26 | 20 | n |  | TRUE
16 | bus_MV_9_2_node_25 | 20 | n |  | TRUE
17 | bus_MV_9_2_node_31 | 20 | n |  | TRUE
18 | bus_MV_9_2_node_29 | 20 | n |  | TRUE
19 | bus_MV_9_2_node_30 | 20 | n |  | TRUE
20 | bus_MV_9_2_node_37 | 20 | n |  | TRUE
21 | bus_MV_9_2_node_32 | 20 | n |  | TRUE
22 | bus_MV_9_2_node_33 | 20 | n |  | TRUE
23 | bus_MV_9_2_node_129 | 20 | n |  | TRUE
24 | bus_MV_9_2_node_35 | 20 | n |  | TRUE
25 | bus_MV_9_2_node_130 | 20 | n |  | TRUE
26 | bus_MV_9_2_node_64 | 20 | n |  | TRUE
27 | bus_MV_9_2_node_38 | 20 | n |  | TRUE
28 | bus_MV_9_2_node_47 | 20 | n |  | TRUE
29 | bus_MV_9_2_node_132 | 20 | n |  | TRUE
30 | bus_MV_9_2_node_140 | 20 | n |  | TRUE
31 | bus_MV_9_2_node_133 | 20 | n |  | TRUE
32 | bus_MV_9_2_node_131 | 20 | n |  | TRUE
33 | bus_MV_9_2_node_155 | 20 | n |  | TRUE
34 | bus_MV_9_2_node_104 | 20 | n |  | TRUE
35 | bus_MV_9_2_node_116 | 20 | n |  | TRUE
36 | bus_MV_9_2_node_115 | 20 | n |  | TRUE
37 | bus_MV_9_2_node_103 | 20 | n |  | TRUE
38 | bus_MV_9_2_node_77 | 20 | n |  | TRUE
39 | bus_MV_9_2_node_48 | 20 | n |  | TRUE
40 | bus_MV_9_2_node_49 | 20 | n |  | TRUE
41 | bus_MV_9_2_node_51 | 20 | n |  | TRUE
42 | bus_MV_9_2_node_54 | 20 | n |  | TRUE
43 | bus_MV_9_2_node_137 | 20 | n |  | TRUE
44 | bus_MV_9_2_node_52 | 20 | n |  | TRUE
45 | bus_MV_9_2_node_156 | 20 | n |  | TRUE
46 | bus_MV_9_2_node_53 | 20 | n |  | TRUE
47 | bus_MV_9_2_node_63 | 20 | n |  | TRUE
48 | bus_MV_9_2_node_142 | 20 | n |  | TRUE
49 | bus_MV_9_2_node_87 | 20 | n |  | TRUE
50 | bus_MV_9_2_node_62 | 20 | n |  | TRUE
51 | bus_MV_9_2_node_141 | 20 | n |  | TRUE
52 | bus_MV_9_2_node_61 | 20 | n |  | TRUE
53 | bus_MV_9_2_node_56 | 20 | n |  | TRUE
54 | bus_MV_9_2_node_59 | 20 | n |  | TRUE
55 | bus_MV_9_2_node_60 | 20 | n |  | TRUE
56 | bus_MV_9_2_node_71 | 20 | n |  | TRUE
57 | bus_MV_9_2_node_85 | 20 | n |  | TRUE
58 | bus_MV_9_2_node_135 | 20 | n |  | TRUE
59 | bus_MV_9_2_node_76 | 20 | n |  | TRUE
60 | bus_MV_9_2_node_148 | 20 | n |  | TRUE
61 | bus_MV_9_2_node_58 | 20 | n |  | TRUE
62 | bus_MV_9_2_node_55 | 20 | n |  | TRUE
63 | bus_MV_9_2_node_107 | 20 | n |  | TRUE
64 | bus_MV_9_2_node_72 | 20 | n |  | TRUE
65 | bus_MV_9_2_node_73 | 20 | n |  | TRUE
66 | bus_MV_9_2_node_138 | 20 | n |  | TRUE
67 | bus_MV_9_2_node_86 | 20 | n |  | TRUE
68 | bus_MV_9_2_node_108 | 20 | n |  | TRUE
69 | bus_MV_9_2_node_152 | 20 | n |  | TRUE
70 | bus_MV_9_2_node_70 | 20 | n |  | TRUE
71 | bus_MV_9_2_node_84 | 20 | n |  | TRUE
72 | bus_MV_9_2_node_66 | 20 | n |  | TRUE
73 | bus_MV_9_2_node_67 | 20 | n |  | TRUE
74 | bus_MV_9_2_node_153 | 20 | n |  | TRUE
75 | bus_MV_9_2_node_74 | 20 | n |  | TRUE
76 | bus_MV_9_2_node_139 | 20 | n |  | TRUE
77 | bus_MV_9_2_node_128 | 20 | n |  | TRUE
78 | bus_MV_9_2_node_78 | 20 | n |  | TRUE
79 | bus_MV_9_2_node_79 | 20 | n |  | TRUE
80 | bus_MV_9_2_node_81 | 20 | n |  | TRUE
81 | bus_MV_9_2_node_149 | 20 | n |  | TRUE
82 | bus_MV_9_2_node_150 | 20 | n |  | TRUE
83 | bus_MV_9_2_node_144 | 20 | n |  | TRUE
84 | bus_MV_9_2_node_83 | 20 | n |  | TRUE
85 | bus_MV_9_2_node_143 | 20 | n |  | TRUE
86 | bus_MV_9_2_node_151 | 20 | n |  | TRUE
87 | bus_MV_9_2_node_145 | 20 | n |  | TRUE
88 | bus_MV_9_2_node_109 | 20 | n |  | TRUE
89 | bus_MV_9_2_node_110 | 20 | n |  | TRUE
90 | bus_MV_9_2_node_113 | 20 | n |  | TRUE
91 | bus_MV_9_2_node_114 | 20 | n |  | TRUE
92 | bus_MV_9_2_node_111 | 20 | n |  | TRUE
93 | bus_MV_9_2_node_112 | 20 | n |  | TRUE
94 | bus_MV_9_2_node_118 | 20 | n |  | TRUE
95 | bus_MV_9_2_node_119 | 20 | n |  | TRUE
96 | bus_MV_9_2_node_120 | 20 | n |  | TRUE
97 | bus_MV_9_2_node_121 | 20 | n |  | TRUE
98 | bus_MV_9_2_node_122 | 20 | n |  | TRUE
99 | bus_MV_9_2_node_123 | 20 | n |  | TRUE
100 | bus_MV_9_2_node_125 | 20 | n |  | TRUE
101 | bus_MV_9_2_node_126 | 20 | n |  | TRUE
102 | bus_MV_9_2_node_124 | 20 | n |  | TRUE
103 | bus_MV_9_2_node_127 | 20 | n |  | TRUE
104 | bus_MV_9_2_node_134 | 20 | n |  | TRUE
105 | bus_MV_9_2_node_154 | 20 | n |  | TRUE
106 | bus_MV_9_2_node_146 | 20 | n |  | TRUE
107 | bus_MV_9_2_node_147 | 20 | n |  | TRUE
108 | bus_HV_9_2_node_72 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_9_2_load_19 | 0 | 0.24078 | 0.11662 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_9_2_load_44 | 4 | 0.29645 | 0.14358 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_9_2_load_136 | 5 | 0.37208 | 0.18021 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_9_2_load_117 | 8 | 0.096368 | 0.046673 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_9_2_load_39 | 9 | 0.29217 | 0.14151 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_9_2_load_22 | 12 | 0.29722 | 0.14395 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_9_2_load_24 | 13 | 0.16172 | 0.078322 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_9_2_load_30 | 19 | 0.15806 | 0.076551 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_9_2_load_37 | 20 | 0.18949 | 0.091774 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_9_2_load_32 | 21 | 0.22029 | 0.10669 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_9_2_load_129 | 23 | 0.075148 | 0.036396 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_9_2_load_130 | 25 | 0.12626 | 0.061149 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_9_2_load_64 | 26 | 0.24773 | 0.11998 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_9_2_load_38 | 27 | 0.24556 | 0.11893 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_9_2_load_47 | 28 | 0.3258 | 0.15779 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_9_2_load_140 | 30 | 0.071983 | 0.034863 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_9_2_load_133 | 31 | 0.7113 | 0.3445 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_9_2_load_155 | 33 | 0.1063 | 0.051483 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_9_2_load_116 | 35 | 0.1347 | 0.065236 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_9_2_load_115 | 36 | 0.12339 | 0.05976 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_9_2_load_103 | 37 | 0.38288 | 0.18544 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_9_2_load_77 | 38 | 0.41139 | 0.19924 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_9_2_load_48 | 39 | 0.33829 | 0.16384 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_9_2_load_137 | 43 | 0.18349 | 0.088869 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_9_2_load_156 | 45 | 0.33345 | 0.1615 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_9_2_load_142 | 48 | 0.38238 | 0.1852 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_9_2_load_87 | 49 | 0.24693 | 0.11959 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_9_2_load_141 | 51 | 0.31778 | 0.15391 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_9_2_load_135 | 58 | 0.10925 | 0.052911 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_9_2_load_76 | 59 | 0.25627 | 0.12412 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_9_2_load_55 | 62 | 0.41204 | 0.19956 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_9_2_load_107 | 63 | 0.077899 | 0.037728 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_9_2_load_138 | 66 | 0.20567 | 0.099611 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_9_2_load_86 | 67 | 0.25721 | 0.12457 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_9_2_load_152 | 69 | 0.33978 | 0.16456 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_9_2_load_70 | 70 | 0.41457 | 0.20079 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_9_2_load_84 | 71 | 0.27004 | 0.13079 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_9_2_load_153 | 74 | 0.3538 | 0.17135 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_9_2_load_74 | 75 | 0.34585 | 0.1675 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_9_2_load_139 | 76 | 0.36323 | 0.17592 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_9_2_load_78 | 78 | 0.17469 | 0.084606 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_9_2_load_150 | 82 | 0.21855 | 0.10585 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_9_2_load_83 | 84 | 0.20573 | 0.099641 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_9_2_load_143 | 85 | 0.23598 | 0.11429 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_9_2_load_109 | 88 | 0.084048 | 0.040706 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_9_2_load_113 | 90 | 0.21235 | 0.10285 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_9_2_load_114 | 91 | 0.3189 | 0.15445 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_9_2_load_111 | 92 | 0.081965 | 0.039698 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_9_2_load_112 | 93 | 0.09261 | 0.044853 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_9_2_load_118 | 94 | 0.13752 | 0.066604 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_9_2_load_121 | 97 | 0.11137 | 0.053941 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_9_2_load_124 | 102 | 0.090075 | 0.043625 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_9_2_load_127 | 103 | 0.090305 | 0.043736 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_9_2_load_134 | 104 | 0.37864 | 0.18338 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_9_2_load_154 | 105 | 0.22088 | 0.10697 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_9_2_load_146 | 106 | 0.21874 | 0.10594 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 64 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_9_2_line_0 |  | 0 | 1 | 0.077624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_9_2_line_1 |  | 1 | 2 | 0.46577 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_9_2_line_2 |  | 2 | 3 | 0.58707 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
3 | MV_9_2_line_3 |  | 2 | 4 | 0.053976 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_9_2_line_4 |  | 2 | 5 | 0.5271 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
5 | MV_9_2_line_5 |  | 3 | 9 | 0.051134 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_9_2_line_6 |  | 3 | 6 | 0.27445 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
7 | MV_9_2_line_7 |  | 5 | 10 | 0.024021 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
8 | MV_9_2_line_8 |  | 6 | 7 | 0.098339 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
9 | MV_9_2_line_9 |  | 6 | 8 | 0.090754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_9_2_line_10 |  | 7 | 33 | 0.036308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_9_2_line_11 |  | 7 | 34 | 0.097742 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
12 | MV_9_2_line_12 |  | 8 | 35 | 0.030098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_9_2_line_13 |  | 9 | 16 | 0.044927 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_9_2_line_14 |  | 10 | 11 | 1.1183 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_9_2_line_15 |  | 11 | 28 | 0.1421 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_9_2_line_16 |  | 11 | 29 | 1.2337 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
17 | MV_9_2_line_17 |  | 12 | 13 | 0.022566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_9_2_line_18 |  | 12 | 14 | 0.062834 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_9_2_line_19 |  | 13 | 15 | 0.023184 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_9_2_line_20 |  | 14 | 16 | 0.22792 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_9_2_line_21 |  | 15 | 17 | 0.26386 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_9_2_line_22 |  | 17 | 20 | 0.005286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_9_2_line_23 |  | 17 | 18 | 0.51103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_9_2_line_24 |  | 18 | 19 | 0.0734 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_9_2_line_25 |  | 21 | 22 | 0.079981 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_9_2_line_26 |  | 21 | 23 | 0.79597 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_9_2_line_27 |  | 22 | 24 | 0.53417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_9_2_line_28 |  | 23 | 25 | 0.13026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_9_2_line_29 |  | 23 | 26 | 0.17853 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_9_2_line_30 |  | 24 | 27 | 0.079153 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_9_2_line_31 |  | 25 | 32 | 0.12252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_9_2_line_32 |  | 27 | 30 | 1.4759 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_9_2_line_33 |  | 29 | 31 | 0.030596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_9_2_line_34 |  | 29 | 32 | 0.22144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_9_2_line_35 |  | 31 | 100 | 0.052475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_9_2_line_36 |  | 34 | 37 | 0.020221 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
37 | MV_9_2_line_37 |  | 34 | 66 | 0.11374 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
38 | MV_9_2_line_38 |  | 36 | 37 | 0.039163 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
39 | MV_9_2_line_39 |  | 36 | 38 | 0.16076 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
40 | MV_9_2_line_40 |  | 38 | 55 | 0.007106 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
41 | MV_9_2_line_41 |  | 39 | 40 | 0.039398 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_9_2_line_42 |  | 40 | 41 | 0.45887 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
43 | MV_9_2_line_43 |  | 40 | 42 | 0.29095 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
44 | MV_9_2_line_44 |  | 41 | 43 | 0.01328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_9_2_line_45 |  | 41 | 44 | 1.0607 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
46 | MV_9_2_line_46 |  | 42 | 49 | 0.029492 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
47 | MV_9_2_line_47 |  | 44 | 45 | 0.025605 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
48 | MV_9_2_line_48 |  | 44 | 46 | 0.17322 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_9_2_line_49 |  | 44 | 47 | 0.57702 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
50 | MV_9_2_line_50 |  | 45 | 60 | 0.014428 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
51 | MV_9_2_line_51 |  | 46 | 48 | 0.045032 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_9_2_line_52 |  | 47 | 59 | 0.046572 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
53 | MV_9_2_line_53 |  | 47 | 52 | 0.22974 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_9_2_line_54 |  | 47 | 55 | 0.31409 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
55 | MV_9_2_line_55 |  | 50 | 51 | 0.047447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_9_2_line_56 |  | 50 | 52 | 0.18328 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
57 | MV_9_2_line_57 |  | 50 | 53 | 0.67983 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
58 | MV_9_2_line_58 |  | 50 | 54 | 0.6388 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
59 | MV_9_2_line_59 |  | 52 | 57 | 0.054561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_9_2_line_60 |  | 52 | 58 | 0.027913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_9_2_line_61 |  | 53 | 61 | 1.0302 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
62 | MV_9_2_line_62 |  | 53 | 62 | 0.086795 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_9_2_line_63 |  | 54 | 63 | 0.0022913 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
64 | MV_9_2_line_64 |  | 55 | 56 | 0.71946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_9_2_line_65 |  | 56 | 70 | 0.004589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_9_2_line_66 |  | 57 | 71 | 0.006476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_9_2_line_67 |  | 60 | 107 | 0.59358 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
68 | MV_9_2_line_68 |  | 61 | 67 | 0.055139 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
69 | MV_9_2_line_69 |  | 63 | 68 | 0.01477 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
70 | MV_9_2_line_70 |  | 64 | 65 | 0.3456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_9_2_line_71 |  | 64 | 66 | 0.012965 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
72 | MV_9_2_line_72 |  | 65 | 69 | 0.03984 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_9_2_line_73 |  | 68 | 88 | 0.010357 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
74 | MV_9_2_line_74 |  | 68 | 89 | 0.062687 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_9_2_line_75 |  | 72 | 73 | 1.0867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_9_2_line_76 |  | 72 | 74 | 0.007398 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_9_2_line_77 |  | 72 | 75 | 0.69762 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
78 | MV_9_2_line_78 |  | 73 | 76 | 0.012452 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_9_2_line_79 |  | 76 | 77 | 0.017216 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_9_2_line_80 |  | 77 | 99 | 0.068926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_9_2_line_81 |  | 78 | 79 | 0.043875 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
82 | MV_9_2_line_82 |  | 79 | 80 | 0.27651 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
83 | MV_9_2_line_83 |  | 80 | 84 | 0.003542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_9_2_line_84 |  | 80 | 85 | 0.17891 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
85 | MV_9_2_line_85 |  | 81 | 82 | 0.012261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_9_2_line_86 |  | 81 | 83 | 0.1501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_9_2_line_87 |  | 83 | 86 | 0.55485 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
88 | MV_9_2_line_88 |  | 83 | 87 | 0.42303 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
89 | MV_9_2_line_89 |  | 83 | 85 | 0.059363 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
90 | MV_9_2_line_90 |  | 86 | 105 | 0.040264 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
91 | MV_9_2_line_91 |  | 87 | 106 | 0.023441 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
92 | MV_9_2_line_92 |  | 88 | 90 | 0.01309 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
93 | MV_9_2_line_93 |  | 89 | 91 | 0.013535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_9_2_line_94 |  | 90 | 93 | 0.0098211 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_9_2_line_95 |  | 92 | 93 | 0.023722 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_9_2_line_96 |  | 94 | 95 | 0.05952 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_9_2_line_97 |  | 94 | 96 | 0.084706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_9_2_line_98 |  | 95 | 97 | 0.088068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_9_2_line_99 |  | 95 | 98 | 0.046792 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_9_2_line_100 |  | 96 | 99 | 0.028622 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_9_2_line_101 |  | 98 | 100 | 0.018994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_9_2_line_102 |  | 98 | 101 | 0.014135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_9_2_line_103 |  | 98 | 102 | 0.05938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_9_2_line_104 |  | 99 | 103 | 0.056347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_9_2_line_105 |  | 101 | 104 | 0.03671 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_9_2_line_106 |  | 106 | 107 | 0.011834 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_9_2_trafo_72 | 25 MVA 110/20 kV | 108 | 64 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2706768.5028 | 1236046.6436
1 | 2706845.1498 | 1236033.0444
2 | 2707039.7396 | 1236134.4473
3 | 2706927.0002 | 1235671.2943
4 | 2707042.0294 | 1236188.3745
5 | 2707073.0004 | 1236660.4965
6 | 2707056.3423 | 1235659.9035
7 | 2707071.0834 | 1235566.1303
8 | 2707118.682 | 1235723.4426
9 | 2706876.4484 | 1235678.9906
10 | 2707091.1132 | 1236676.3353
11 | 2707689.9604 | 1237369.2973
12 | 2706729.5725 | 1235748.6929
13 | 2706712.3269 | 1235763.2464
14 | 2706779.7271 | 1235710.8428
15 | 2706694.6088 | 1235778.1987
16 | 2706894.9608 | 1235719.9218
17 | 2706629.1032 | 1235944.2392
18 | 2706435.3225 | 1236147.4095
19 | 2706368.1052 | 1236177.2731
20 | 2706634.3474 | 1235943.4661
21 | 2708851.8057 | 1236926.5973
22 | 2708780.6404 | 1236963.0998
23 | 2708457.5825 | 1236235.1092
24 | 2708558.8745 | 1237223.8344
25 | 2708336.1802 | 1236187.9297
26 | 2708529.8365 | 1236071.8545
27 | 2708593.4577 | 1237295.033
28 | 2707667.9654 | 1237509.6852
29 | 2708066.125 | 1236194.3743
30 | 2709318.8787 | 1238580.3772
31 | 2708049.8618 | 1236168.4585
32 | 2708224.467 | 1236138.3466
33 | 2707106.4357 | 1235574.8409
34 | 2707081.7991 | 1235476.4767
35 | 2707130.0032 | 1235751.322
36 | 2707024.4316 | 1235475.2205
37 | 2707063.1676 | 1235469.4553
38 | 2707064.9379 | 1235319.6524
39 | 2706464.7251 | 1234580.491
40 | 2706465.5633 | 1234619.8806
41 | 2706637.5036 | 1234743.0911
42 | 2706249.3706 | 1234425.1737
43 | 2706643.598 | 1234754.8984
44 | 2707123.1273 | 1234859.4145
45 | 2707131.1142 | 1234835.0843
46 | 2707149.9407 | 1234986.2064
47 | 2706909.8435 | 1235188.904
48 | 2707158.9566 | 1235028.6015
49 | 2706238.4739 | 1234397.7691
50 | 2706800.8242 | 1235260.9432
51 | 2706815.5313 | 1235306.0533
52 | 2706818.9405 | 1235132.9596
53 | 2706489.5231 | 1235255.7188
54 | 2706584.3822 | 1234987.1582
55 | 2707063.2912 | 1235312.7397
56 | 2707419.383 | 1235122.9094
57 | 2706768.6989 | 1235132.0003
58 | 2706815.4943 | 1235160.6591
59 | 2706932.1023 | 1235147.9953
60 | 2707138.177 | 1234826.3049
61 | 2706206.0178 | 1234934.4212
62 | 2706403.0397 | 1235263.064
63 | 2706583.3319 | 1234985.1218
64 | 2707199.7707 | 1235470.4104
65 | 2707452.5748 | 1235395.8527
66 | 2707194.1454 | 1235458.7222
67 | 2706188.0161 | 1234882.3041
68 | 2706576.5616 | 1234971.9952
69 | 2707439.75 | 1235433.5721
70 | 2707420.9674 | 1235118.6014
71 | 2706767.8794 | 1235138.4239
72 | 2707998.0373 | 1235298.7559
73 | 2708119.5755 | 1235917.2436
74 | 2708000.9262 | 1235305.5692
75 | 2708282.1195 | 1234661.598
76 | 2708109.5443 | 1235909.8665
77 | 2708095.4887 | 1235919.8073
78 | 2707529.4919 | 1234221.1529
79 | 2707571.2386 | 1234234.6521
80 | 2707477.5713 | 1234416.697
81 | 2707219.4213 | 1234317.0687
82 | 2707213.0386 | 1234306.5899
83 | 2707240.9878 | 1234444.7445
84 | 2707480.1699 | 1234419.1125
85 | 2707300.1091 | 1234439.3965
86 | 2706852.7877 | 1234420.2332
87 | 2707427.548 | 1234671.5881
88 | 2706572.0011 | 1234962.6962
89 | 2706523.1246 | 1234978.5977
90 | 2706569.8136 | 1234949.7905
91 | 2706514.2857 | 1234968.347
92 | 2706551.9616 | 1234922.0012
93 | 2706562.472 | 1234943.2672
94 | 2708004.688 | 1236035.6846
95 | 2708006.6505 | 1236087.3323
96 | 2708033.3664 | 1235959.7972
97 | 2707946.7779 | 1236033.2801
98 | 2708045.106 | 1236113.6963
99 | 2708027.6367 | 1235931.9159
100 | 2708043.0845 | 1236128.2819
101 | 2708057.2983 | 1236120.8458
102 | 2708066.5766 | 1236059.7041
103 | 2707971.7756 | 1235935.7872
104 | 2708078.4237 | 1236091.3192
105 | 2706814.1955 | 1234431.7149
106 | 2707422.7975 | 1234694.3864
107 | 2707419.4803 | 1234705.7462
108 | 2707199.7707 | 1235470.4104

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99787 | -0.048031 | 0.24078 | 0.11662
1 | 0.99789 | -0.048251 | 0 | 0
2 | 0.99803 | -0.049378 | 0 | 0
3 | 0.99865 | -0.037916 | 0 | 0
4 | 0.998 | -0.049572 | 0.29645 | 0.14358
5 | 0.99691 | -0.087555 | 0.37208 | 0.18021
6 | 0.999 | -0.03127 | 0 | 0
7 | 0.99913 | -0.028789 | 0 | 0
8 | 0.99897 | -0.031029 | 0.096368 | 0.046673
9 | 0.99854 | -0.038719 | 0.29217 | 0.14151
10 | 0.99686 | -0.088138 | 0 | 0
11 | 0.99449 | -0.11487 | 0 | 0
12 | 0.99816 | -0.037238 | 0.29722 | 0.14395
13 | 0.99815 | -0.037131 | 0.16172 | 0.078322
14 | 0.99826 | -0.036509 | 0 | 0
15 | 0.99814 | -0.037065 | 0 | 0
16 | 0.99849 | -0.038363 | 0 | 0
17 | 0.99802 | -0.036253 | 0 | 0
18 | 0.99792 | -0.035538 | 0 | 0
19 | 0.99791 | -0.035403 | 0.15806 | 0.076551
20 | 0.99802 | -0.036241 | 0.18949 | 0.091774
21 | 0.98786 | -0.2496 | 0.22029 | 0.10669
22 | 0.98781 | -0.25002 | 0 | 0
23 | 0.98869 | -0.24328 | 0.075148 | 0.036396
24 | 0.98759 | -0.24822 | 0 | 0
25 | 0.98883 | -0.24451 | 0.12626 | 0.061149
26 | 0.9886 | -0.24383 | 0.24773 | 0.11998
27 | 0.98754 | -0.24854 | 0.24556 | 0.11893
28 | 0.9944 | -0.11544 | 0.3258 | 0.15779
29 | 0.98926 | -0.24816 | 0 | 0
30 | 0.98734 | -0.24997 | 0.071983 | 0.034863
31 | 0.98916 | -0.24727 | 0.7113 | 0.3445
32 | 0.98898 | -0.24583 | 0 | 0
33 | 0.99913 | -0.028744 | 0.1063 | 0.051483
34 | 0.99926 | -0.026277 | 0 | 0
35 | 0.99897 | -0.030981 | 0.1347 | 0.065236
36 | 0.99912 | -0.031258 | 0.12339 | 0.05976
37 | 0.99924 | -0.026885 | 0.38288 | 0.18544
38 | 0.99867 | -0.048895 | 0.41139 | 0.19924
39 | 0.99774 | -0.069478 | 0.33829 | 0.16384
40 | 0.99776 | -0.069316 | 0 | 0
41 | 0.99782 | -0.06822 | 0 | 0
42 | 0.99773 | -0.070502 | 0 | 0
43 | 0.99782 | -0.068191 | 0.18349 | 0.088869
44 | 0.99799 | -0.064406 | 0 | 0
45 | 0.99798 | -0.064596 | 0.33345 | 0.1615
46 | 0.99791 | -0.063645 | 0 | 0
47 | 0.99832 | -0.056857 | 0 | 0
48 | 0.99789 | -0.063439 | 0.38238 | 0.1852
49 | 0.99772 | -0.070622 | 0.24693 | 0.11959
50 | 0.99814 | -0.060832 | 0 | 0
51 | 0.99812 | -0.060653 | 0.31778 | 0.15391
52 | 0.99821 | -0.059231 | 0 | 0
53 | 0.99805 | -0.063186 | 0 | 0
54 | 0.99802 | -0.063102 | 0 | 0
55 | 0.99866 | -0.049083 | 0 | 0
56 | 0.99828 | -0.045903 | 0 | 0
57 | 0.99819 | -0.059057 | 0 | 0
58 | 0.99821 | -0.059195 | 0.10925 | 0.052911
59 | 0.99831 | -0.057054 | 0.25627 | 0.12412
60 | 0.99798 | -0.064685 | 0 | 0
61 | 0.998 | -0.06455 | 0 | 0
62 | 0.99798 | -0.06362 | 0.41204 | 0.19956
63 | 0.99802 | -0.06311 | 0.077899 | 0.037728
64 | 1 | 0 | -13.4314 | -5.7128
65 | 0.99985 | 0.0013132 | 0 | 0
66 | 0.99996 | -0.00073173 | 0.20567 | 0.099611
67 | 0.99799 | -0.064783 | 0.25721 | 0.12457
68 | 0.99802 | -0.063155 | 0 | 0
69 | 0.99982 | 0.0011495 | 0.33978 | 0.16456
70 | 0.99828 | -0.04588 | 0.41457 | 0.20079
71 | 0.99819 | -0.059036 | 0.27004 | 0.13079
72 | 0.98752 | -0.23422 | 0 | 0
73 | 0.9885 | -0.24257 | 0 | 0
74 | 0.98752 | -0.23418 | 0.3538 | 0.17135
75 | 0.98705 | -0.23723 | 0.34585 | 0.1675
76 | 0.98851 | -0.24243 | 0.36323 | 0.17592
77 | 0.98855 | -0.24217 | 0 | 0
78 | 0.99766 | -0.07256 | 0.17469 | 0.084606
79 | 0.99766 | -0.072434 | 0 | 0
80 | 0.99767 | -0.072224 | 0 | 0
81 | 0.99768 | -0.070039 | 0 | 0
82 | 0.99768 | -0.070006 | 0.21855 | 0.10585
83 | 0.99772 | -0.070413 | 0 | 0
84 | 0.99767 | -0.072216 | 0.20573 | 0.099641
85 | 0.9977 | -0.071038 | 0.23598 | 0.11429
86 | 0.9977 | -0.070983 | 0 | 0
87 | 0.99781 | -0.0684 | 0 | 0
88 | 0.99802 | -0.063173 | 0.084048 | 0.040706
89 | 0.99799 | -0.062919 | 0 | 0
90 | 0.99802 | -0.063257 | 0.21235 | 0.10285
91 | 0.99799 | -0.062867 | 0.3189 | 0.15445
92 | 0.99801 | -0.063255 | 0.081965 | 0.039698
93 | 0.99801 | -0.063278 | 0.09261 | 0.044853
94 | 0.98881 | -0.24432 | 0.13752 | 0.066604
95 | 0.98891 | -0.24513 | 0 | 0
96 | 0.98868 | -0.24329 | 0 | 0
97 | 0.9889 | -0.24502 | 0.11137 | 0.053941
98 | 0.98899 | -0.24582 | 0 | 0
99 | 0.98864 | -0.24294 | 0 | 0
100 | 0.98904 | -0.24621 | 0 | 0
101 | 0.98898 | -0.24576 | 0 | 0
102 | 0.98898 | -0.24576 | 0.090075 | 0.043625
103 | 0.98864 | -0.24288 | 0.090305 | 0.043736
104 | 0.98897 | -0.24559 | 0.37864 | 0.18338
105 | 0.99769 | -0.071129 | 0.22088 | 0.10697
106 | 0.99782 | -0.068285 | 0.21874 | 0.10594
107 | 0.99782 | -0.068217 | 0 | 0
108 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.24078 | -0.11662 | 0.24079 | 0.11477 | 6.189e-06 | -0.0018437 | 0.0077397 | 0.0077166 | 0.0077397 | 0.99787 | -0.048031 | 0.99789 | -0.048251 | 3.518
1 | -0.24079 | -0.11477 | 0.24083 | 0.10371 | 3.638e-05 | -0.011065 | 0.0077166 | 0.0075842 | 0.0077166 | 0.99789 | -0.048251 | 0.99803 | -0.049378 | 3.5075
2 | -4.8347 | -2.2337 | 4.8373 | 2.1913 | 0.0025404 | -0.042373 | 0.15404 | 0.15351 | 0.15404 | 0.99803 | -0.049378 | 0.99865 | -0.037916 | 18.2951
3 | 0.29646 | 0.14352 | -0.29645 | -0.14358 | 8.7293e-06 | -5.8713e-05 | 0.0095269 | 0.0095278 | 0.0095278 | 0.99803 | -0.049378 | 0.998 | -0.049572 | 4.537
4 | 4.2974 | 1.9864 | -4.2939 | -1.9827 | 0.0035231 | 0.0037432 | 0.13694 | 0.13695 | 0.13695 | 0.99803 | -0.049378 | 0.99691 | -0.087555 | 16.7017
5 | 1.0992 | 0.50429 | -1.099 | -0.50429 | 0.00011133 | 8.8636e-06 | 0.034957 | 0.034958 | 0.034958 | 0.99865 | -0.037916 | 0.99854 | -0.038719 | 16.6467
6 | -5.9364 | -2.6956 | 5.9382 | 2.6763 | 0.0017816 | -0.019284 | 0.18846 | 0.18821 | 0.18846 | 0.99865 | -0.037916 | 0.999 | -0.03127 | 22.3829
7 | 3.9218 | 1.8025 | -3.9216 | -1.8032 | 0.00018125 | -0.00068722 | 0.12498 | 0.12499 | 0.12499 | 0.99691 | -0.087555 | 0.99686 | -0.088138 | 34.529
8 | -6.1693 | -2.7853 | 6.1699 | 2.7785 | 0.00068818 | -0.0068677 | 0.1956 | 0.19551 | 0.1956 | 0.999 | -0.03127 | 0.99913 | -0.028789 | 23.23
9 | 0.23107 | 0.10903 | -0.23106 | -0.11119 | 6.6283e-06 | -0.0021605 | 0.0073831 | 0.00741 | 0.00741 | 0.999 | -0.03127 | 0.99897 | -0.031029 | 3.3682
10 | 0.1063 | 0.050618 | -0.1063 | -0.051483 | 5.6268e-07 | -0.00086522 | 0.0034017 | 0.0034126 | 0.0034126 | 0.99913 | -0.028789 | 0.99913 | -0.028744 | 1.5512
11 | -6.2762 | -2.8291 | 6.277 | 2.8223 | 0.00070737 | -0.0068064 | 0.19891 | 0.19882 | 0.19891 | 0.99913 | -0.028789 | 0.99926 | -0.026277 | 23.6233
12 | 0.1347 | 0.064519 | -0.1347 | -0.065236 | 7.4998e-07 | -0.00071692 | 0.0043158 | 0.0043248 | 0.0043248 | 0.99897 | -0.031029 | 0.99897 | -0.030981 | 1.9658
13 | 0.80687 | 0.36278 | -0.80683 | -0.36384 | 3.9251e-05 | -0.0010579 | 0.025576 | 0.025588 | 0.025588 | 0.99854 | -0.038719 | 0.99849 | -0.038363 | 11.631
14 | 3.9216 | 1.8032 | -3.9132 | -1.8351 | 0.00847 | -0.031877 | 0.12499 | 0.12546 | 0.12546 | 0.99686 | -0.088138 | 0.99449 | -0.11487 | 34.6573
15 | 0.32582 | 0.15764 | -0.3258 | -0.15779 | 2.7954e-05 | -0.00015025 | 0.010507 | 0.010509 | 0.010509 | 0.99449 | -0.11487 | 0.9944 | -0.11544 | 5.0042
16 | 3.5873 | 1.6774 | -3.5724 | -1.6618 | 0.014968 | 0.015595 | 0.11495 | 0.11497 | 0.11497 | 0.99449 | -0.11487 | 0.98926 | -0.24816 | 32.8492
17 | 0.50934 | 0.22528 | -0.50933 | -0.22582 | 7.8185e-06 | -0.00053448 | 0.016107 | 0.016113 | 0.016113 | 0.99816 | -0.037238 | 0.99815 | -0.037131 | 7.3241
18 | -0.80655 | -0.36923 | 0.80663 | 0.3692 | 7.3676e-05 | -2.8595e-05 | 0.025654 | 0.025653 | 0.025654 | 0.99816 | -0.037238 | 0.99826 | -0.036509 | 12.2162
19 | 0.34761 | 0.14749 | -0.34761 | -0.14804 | 3.6934e-06 | -0.0005504 | 0.010921 | 0.010927 | 0.010927 | 0.99815 | -0.037131 | 0.99814 | -0.037065 | 4.9669
20 | -0.80663 | -0.3692 | 0.80683 | 0.36384 | 0.00019973 | -0.0053649 | 0.025653 | 0.025588 | 0.025653 | 0.99826 | -0.036509 | 0.99849 | -0.038363 | 11.6605
21 | 0.34761 | 0.14804 | -0.34757 | -0.15431 | 4.2335e-05 | -0.0062632 | 0.010927 | 0.010999 | 0.010999 | 0.99814 | -0.037065 | 0.99802 | -0.036253 | 4.9998
22 | 0.18949 | 0.091648 | -0.18949 | -0.091774 | 2.6162e-07 | -0.00012563 | 0.0060883 | 0.0060899 | 0.0060899 | 0.99802 | -0.036253 | 0.99802 | -0.036241 | 2.7681
23 | 0.15808 | 0.062659 | -0.15806 | -0.074806 | 1.6959e-05 | -0.012147 | 0.0049184 | 0.0050585 | 0.0050585 | 0.99802 | -0.036253 | 0.99792 | -0.035538 | 2.2993
24 | 0.15806 | 0.074806 | -0.15806 | -0.076551 | 2.5182e-06 | -0.0017445 | 0.0050585 | 0.0050803 | 0.0050803 | 0.99792 | -0.035538 | 0.99791 | -0.035403 | 2.3092
25 | 0.31766 | 0.1395 | -0.31764 | -0.13958 | 1.4649e-05 | -8.3997e-05 | 0.010138 | 0.010139 | 0.010139 | 0.98786 | -0.2496 | 0.98781 | -0.25002 | 4.8283
26 | -0.53794 | -0.24619 | 0.53837 | 0.24552 | 0.00042358 | -0.00066276 | 0.017288 | 0.017277 | 0.017288 | 0.98786 | -0.2496 | 0.98869 | -0.24328 | 8.2323
27 | 0.31764 | 0.13958 | -0.31757 | -0.152 | 7.4394e-05 | -0.01242 | 0.010139 | 0.010291 | 0.010291 | 0.98781 | -0.25002 | 0.98759 | -0.24822 | 4.6778
28 | -0.86126 | -0.4017 | 0.8614 | 0.3987 | 0.00013371 | -0.0030008 | 0.027748 | 0.02771 | 0.027748 | 0.98869 | -0.24328 | 0.98883 | -0.24451 | 12.6126
29 | 0.24775 | 0.11978 | -0.24773 | -0.11998 | 2.0542e-05 | -0.00019545 | 0.0080348 | 0.0080375 | 0.0080375 | 0.98869 | -0.24328 | 0.9886 | -0.24383 | 3.8274
30 | 0.31757 | 0.152 | -0.31755 | -0.15208 | 1.4937e-05 | -8.2802e-05 | 0.010291 | 0.010292 | 0.010292 | 0.98759 | -0.24822 | 0.98754 | -0.24854 | 4.9011
31 | -0.98765 | -0.45985 | 0.98782 | 0.45704 | 0.00016528 | -0.0028118 | 0.031805 | 0.03177 | 0.031805 | 0.98883 | -0.24451 | 0.98898 | -0.24583 | 14.4569
32 | 0.071998 | 0.033154 | -0.071983 | -0.034863 | 1.4247e-05 | -0.0017091 | 0.002317 | 0.0023385 | 0.0023385 | 0.98754 | -0.24854 | 0.98734 | -0.24997 | 1.1136
33 | 2.5843 | 1.2099 | -2.584 | -1.2105 | 0.00028322 | -0.00063083 | 0.083266 | 0.083275 | 0.083275 | 0.98926 | -0.24816 | 0.98916 | -0.24727 | 37.8522
34 | 0.98812 | 0.45195 | -0.98782 | -0.45704 | 0.00029779 | -0.0050844 | 0.031707 | 0.03177 | 0.03177 | 0.98926 | -0.24816 | 0.98898 | -0.24583 | 14.441
35 | 1.8727 | 0.866 | -1.8724 | -0.86715 | 0.00025405 | -0.0011504 | 0.060213 | 0.060228 | 0.060228 | 0.98916 | -0.24727 | 0.98904 | -0.24621 | 27.3762
36 | 6.5879 | 2.6155 | -6.5878 | -2.6169 | 0.00015517 | -0.0014002 | 0.20477 | 0.20479 | 0.20479 | 0.99926 | -0.026277 | 0.99924 | -0.026885 | 24.3213
37 | -12.8649 | -5.4378 | 12.8715 | 5.4471 | 0.0065995 | 0.0092606 | 0.40349 | 0.40349 | 0.40349 | 0.99926 | -0.026277 | 0.99996 | -0.00073173 | 49.2059
38 | -6.2044 | -2.4308 | 6.2049 | 2.4315 | 0.00051738 | 0.00064785 | 0.19253 | 0.19253 | 0.19253 | 0.99912 | -0.031258 | 0.99924 | -0.026885 | 23.4793
39 | 6.081 | 2.3711 | -6.079 | -2.3686 | 0.0020376 | 0.0025348 | 0.18858 | 0.18859 | 0.18859 | 0.99912 | -0.031258 | 0.99867 | -0.048895 | 22.9983
40 | 5.6676 | 2.1693 | -5.6675 | -2.1698 | 4.0016e-05 | -0.00050474 | 0.17542 | 0.17542 | 0.17542 | 0.99867 | -0.048895 | 0.99866 | -0.049083 | 20.8342
41 | -0.33829 | -0.16384 | 0.3383 | 0.1638 | 8.3019e-06 | -4.1623e-05 | 0.010875 | 0.010875 | 0.010875 | 0.99774 | -0.069478 | 0.99776 | -0.069316 | 5.1787
42 | -0.58524 | -0.28258 | 0.58527 | 0.2477 | 2.9016e-05 | -0.034878 | 0.018803 | 0.018386 | 0.018803 | 0.99776 | -0.069316 | 0.99782 | -0.06822 | 2.2331
43 | 0.24694 | 0.11878 | -0.24693 | -0.11952 | 6.5251e-06 | -0.00074033 | 0.007928 | 0.0079374 | 0.0079374 | 0.99776 | -0.069316 | 0.99773 | -0.070502 | 0.96797
44 | 0.18349 | 0.088554 | -0.18349 | -0.088869 | 6.1638e-07 | -0.00031551 | 0.0058944 | 0.0058984 | 0.0058984 | 0.99782 | -0.06822 | 0.99782 | -0.068191 | 2.6811
45 | -0.76876 | -0.33626 | 0.76887 | 0.25565 | 0.00011024 | -0.080603 | 0.024275 | 0.023437 | 0.024275 | 0.99782 | -0.06822 | 0.99799 | -0.064406 | 2.883
46 | 0.24693 | 0.11952 | -0.24693 | -0.11959 | 6.6228e-07 | -7.5038e-05 | 0.0079374 | 0.0079383 | 0.0079383 | 0.99773 | -0.070502 | 0.99772 | -0.070622 | 0.96809
47 | 1.6083 | 0.62802 | -1.6083 | -0.62996 | 1.1692e-05 | -0.0019377 | 0.049943 | 0.049963 | 0.049963 | 0.99799 | -0.064406 | 0.99798 | -0.064596 | 5.9339
48 | 0.38243 | 0.18002 | -0.38239 | -0.18413 | 3.4712e-05 | -0.0041086 | 0.012226 | 0.012277 | 0.012277 | 0.99799 | -0.064406 | 0.99791 | -0.063645 | 5.5807
49 | -2.7596 | -1.0637 | 2.7604 | 1.0205 | 0.00076872 | -0.043218 | 0.085548 | 0.0851 | 0.085548 | 0.99799 | -0.064406 | 0.99832 | -0.056857 | 10.1601
50 | 1.2749 | 0.46846 | -1.2749 | -0.46956 | 4.0765e-06 | -0.0010942 | 0.039288 | 0.039299 | 0.039299 | 0.99798 | -0.064596 | 0.99798 | -0.064685 | 4.6673
51 | 0.38239 | 0.18413 | -0.38238 | -0.1852 | 9.0718e-06 | -0.001068 | 0.012277 | 0.012291 | 0.012291 | 0.99791 | -0.063645 | 0.99789 | -0.063439 | 5.5868
52 | 0.25627 | 0.124 | -0.25627 | -0.12412 | 1.1251e-06 | -0.00011853 | 0.0082323 | 0.0082338 | 0.0082338 | 0.99832 | -0.056857 | 0.99831 | -0.057054 | 1.0041
53 | 2.2346 | 0.86427 | -2.2344 | -0.88158 | 0.00020233 | -0.017306 | 0.069281 | 0.069465 | 0.069465 | 0.99832 | -0.056857 | 0.99821 | -0.059231 | 8.25
54 | -5.2513 | -2.0087 | 5.2528 | 1.9862 | 0.0015169 | -0.022532 | 0.16258 | 0.16233 | 0.16258 | 0.99832 | -0.056857 | 0.99866 | -0.049083 | 19.3085
55 | 0.31779 | 0.15278 | -0.31778 | -0.15391 | 6.5965e-06 | -0.0011267 | 0.010198 | 0.010212 | 0.010212 | 0.99814 | -0.060832 | 0.99812 | -0.060653 | 4.6418
56 | -1.855 | -0.71385 | 1.8551 | 0.7 | 0.00011056 | -0.013851 | 0.057485 | 0.057341 | 0.057485 | 0.99814 | -0.060832 | 0.99821 | -0.059231 | 6.8272
57 | 0.66935 | 0.19382 | -0.6693 | -0.24552 | 5.1644e-05 | -0.051697 | 0.020154 | 0.02062 | 0.02062 | 0.99814 | -0.060832 | 0.99805 | -0.063186 | 2.4489
58 | 0.86788 | 0.36724 | -0.86779 | -0.41578 | 8.8641e-05 | -0.048538 | 0.027255 | 0.027833 | 0.027833 | 0.99814 | -0.060832 | 0.99802 | -0.063102 | 3.3056
59 | 0.27004 | 0.12933 | -0.27004 | -0.13063 | 5.4715e-06 | -0.0012964 | 0.0086589 | 0.0086752 | 0.0086752 | 0.99821 | -0.059231 | 0.99819 | -0.059057 | 3.9433
60 | 0.10925 | 0.052247 | -0.10925 | -0.052911 | 4.581e-07 | -0.00066394 | 0.0035021 | 0.0035104 | 0.0035104 | 0.99821 | -0.059231 | 0.99821 | -0.059195 | 1.5956
61 | 0.25723 | 0.046045 | -0.25721 | -0.12443 | 1.1582e-05 | -0.078389 | 0.0075582 | 0.0082649 | 0.0082649 | 0.99805 | -0.063186 | 0.998 | -0.06455 | 0.98158
62 | 0.41207 | 0.19947 | -0.41204 | -0.19956 | 2.7118e-05 | -8.622e-05 | 0.013242 | 0.013243 | 0.013243 | 0.99805 | -0.063186 | 0.99798 | -0.06362 | 6.3062
63 | 0.86779 | 0.41578 | -0.86779 | -0.41596 | 3.2474e-07 | -0.00017408 | 0.027833 | 0.027835 | 0.027835 | 0.99802 | -0.063102 | 0.99802 | -0.06311 | 3.3058
64 | 0.41474 | 0.1836 | -0.41457 | -0.20068 | 0.00016768 | -0.017076 | 0.013111 | 0.013319 | 0.013319 | 0.99866 | -0.049083 | 0.99828 | -0.045903 | 6.0541
65 | 0.41457 | 0.20068 | -0.41457 | -0.20079 | 1.0869e-06 | -0.00010887 | 0.013319 | 0.01332 | 0.01332 | 0.99828 | -0.045903 | 0.99828 | -0.04588 | 6.0547
66 | 0.27004 | 0.13063 | -0.27004 | -0.13079 | 6.5081e-07 | -0.00015387 | 0.0086752 | 0.0086772 | 0.0086772 | 0.99819 | -0.059057 | 0.99819 | -0.059036 | 3.9442
67 | 1.2749 | 0.46956 | -1.2747 | -0.51456 | 0.00016973 | -0.045006 | 0.039299 | 0.039769 | 0.039769 | 0.99798 | -0.064685 | 0.99782 | -0.068217 | 4.7232
68 | 0.25721 | 0.12443 | -0.25721 | -0.12457 | 1.3427e-06 | -0.00014022 | 0.0082649 | 0.0082667 | 0.0082667 | 0.998 | -0.06455 | 0.99799 | -0.064783 | 1.0081
69 | 0.78989 | 0.37823 | -0.78989 | -0.37935 | 1.7353e-06 | -0.0011224 | 0.025332 | 0.025346 | 0.025346 | 0.99802 | -0.06311 | 0.99802 | -0.063155 | 3.0102
70 | 0.33984 | 0.15628 | -0.33978 | -0.16452 | 5.4297e-05 | -0.0082343 | 0.010798 | 0.0109 | 0.0109 | 1 | 0 | 0.99985 | 0.0013132 | 4.9544
71 | 13.0776 | 5.5461 | -13.0772 | -5.5467 | 0.00039897 | -0.00062427 | 0.41006 | 0.41007 | 0.41007 | 1 | 0 | 0.99996 | -0.00073173 | 48.7024
72 | 0.33978 | 0.16452 | -0.33978 | -0.16456 | 8.4333e-06 | -4.2263e-05 | 0.0109 | 0.0109 | 0.0109 | 0.99985 | 0.0013132 | 0.99982 | 0.0011495 | 5.1906
73 | 0.47098 | 0.22671 | -0.47098 | -0.22749 | 4.3356e-07 | -0.00078779 | 0.015119 | 0.015129 | 0.015129 | 0.99802 | -0.063155 | 0.99802 | -0.063173 | 1.7968
74 | 0.31892 | 0.15264 | -0.31891 | -0.15413 | 8.7685e-06 | -0.0014882 | 0.010227 | 0.010245 | 0.010245 | 0.99802 | -0.063155 | 0.99799 | -0.062919 | 4.657
75 | -0.69981 | -0.33797 | 0.70054 | 0.31286 | 0.00073829 | -0.025108 | 0.022718 | 0.022406 | 0.022718 | 0.98752 | -0.23422 | 0.9885 | -0.24257 | 10.3262
76 | 0.3538 | 0.17118 | -0.3538 | -0.17135 | 1.304e-06 | -0.00017187 | 0.011489 | 0.011492 | 0.011492 | 0.98752 | -0.23422 | 0.98752 | -0.23418 | 5.2235
77 | 0.346 | 0.16679 | -0.34585 | -0.1675 | 0.00015685 | -0.00071353 | 0.011228 | 0.011239 | 0.011239 | 0.98752 | -0.23422 | 0.98705 | -0.23723 | 5.3517
78 | -0.70054 | -0.31286 | 0.70056 | 0.31285 | 1.1137e-05 | -7.5491e-06 | 0.022406 | 0.022406 | 0.022406 | 0.9885 | -0.24257 | 0.98851 | -0.24243 | 10.6694
79 | -1.0638 | -0.48878 | 1.0638 | 0.48878 | 3.5851e-05 | 2.3726e-06 | 0.034188 | 0.034188 | 0.034188 | 0.98851 | -0.24243 | 0.98855 | -0.24217 | 16.28
80 | -1.0638 | -0.48878 | 1.0639 | 0.4872 | 0.00010749 | -0.0015765 | 0.034188 | 0.034168 | 0.034188 | 0.98855 | -0.24217 | 0.98864 | -0.24294 | 15.5399
81 | -0.17469 | -0.084606 | 0.17469 | 0.084494 | 4.9312e-07 | -0.00011233 | 0.0056164 | 0.0056149 | 0.0056164 | 0.99766 | -0.07256 | 0.99766 | -0.072434 | 0.68492
82 | -0.17469 | -0.084494 | 0.17469 | 0.063467 | 1.5248e-06 | -0.021027 | 0.0056149 | 0.005378 | 0.0056149 | 0.99766 | -0.072434 | 0.99767 | -0.072224 | 0.66686
83 | 0.20573 | 0.099557 | -0.20573 | -0.099641 | 2.0683e-07 | -8.4114e-05 | 0.0066132 | 0.0066143 | 0.0066143 | 0.99767 | -0.072224 | 0.99767 | -0.072216 | 3.0065
84 | -0.38043 | -0.16302 | 0.38043 | 0.16258 | 9.1407e-06 | -0.00044776 | 0.011976 | 0.01197 | 0.011976 | 0.99767 | -0.072224 | 0.9977 | -0.071038 | 1.4605
85 | 0.21855 | 0.10556 | -0.21855 | -0.10585 | 8.0767e-07 | -0.00029115 | 0.0070226 | 0.0070263 | 0.0070263 | 0.99768 | -0.070039 | 0.99768 | -0.070006 | 3.1938
86 | -0.21855 | -0.10556 | 0.21856 | 0.10199 | 9.8195e-06 | -0.0035643 | 0.0070226 | 0.0069784 | 0.0070226 | 0.99768 | -0.070039 | 0.99772 | -0.070413 | 3.1921
87 | 0.22088 | 0.064678 | -0.22088 | -0.10687 | 4.7725e-06 | -0.042194 | 0.0066592 | 0.0070997 | 0.0070997 | 0.99772 | -0.070413 | 0.9977 | -0.070983 | 0.84319
88 | -1.0559 | -0.4434 | 1.056 | 0.4113 | 8.4084e-05 | -0.032099 | 0.033134 | 0.032785 | 0.033134 | 0.99772 | -0.070413 | 0.99781 | -0.0684 | 3.9352
89 | 0.61643 | 0.27673 | -0.61642 | -0.27687 | 8.087e-06 | -0.00014126 | 0.01955 | 0.019552 | 0.019552 | 0.99772 | -0.070413 | 0.9977 | -0.071038 | 2.3844
90 | 0.22088 | 0.10687 | -0.22088 | -0.10697 | 7.2346e-07 | -0.0001027 | 0.0070997 | 0.007101 | 0.007101 | 0.9977 | -0.070983 | 0.99769 | -0.071129 | 0.86597
91 | -1.056 | -0.4113 | 1.056 | 0.40952 | 4.6082e-06 | -0.0017789 | 0.032785 | 0.032766 | 0.032785 | 0.99781 | -0.0684 | 0.99782 | -0.068285 | 3.8937
92 | 0.38693 | 0.18679 | -0.38693 | -0.18682 | 7.2053e-07 | -3.2708e-05 | 0.012428 | 0.012428 | 0.012428 | 0.99802 | -0.063173 | 0.99802 | -0.063257 | 1.5156
93 | 0.31891 | 0.15413 | -0.3189 | -0.15445 | 1.8975e-06 | -0.00032131 | 0.010245 | 0.010249 | 0.010249 | 0.99799 | -0.062919 | 0.99799 | -0.062867 | 4.6589
94 | 0.17458 | 0.083975 | -0.17458 | -0.083987 | 5.4942e-07 | -1.1334e-05 | 0.0056034 | 0.0056036 | 0.0056036 | 0.99802 | -0.063257 | 0.99801 | -0.063278 | 2.6684
95 | -0.081965 | -0.039698 | 0.081965 | 0.039134 | 2.1917e-07 | -0.00056407 | 0.0026343 | 0.0026272 | 0.0026343 | 0.99801 | -0.063255 | 0.99801 | -0.063278 | 1.1974
96 | -1.292 | -0.59364 | 1.2921 | 0.5923 | 0.00013685 | -0.001349 | 0.041509 | 0.041492 | 0.041509 | 0.98881 | -0.24432 | 0.98891 | -0.24513 | 18.8678
97 | 1.1544 | 0.52704 | -1.1543 | -0.52897 | 0.00015532 | -0.0019311 | 0.037049 | 0.037073 | 0.037073 | 0.98881 | -0.24432 | 0.98868 | -0.24329 | 16.8515
98 | 0.11138 | 0.051885 | -0.11137 | -0.053941 | 1.5233e-06 | -0.0020559 | 0.0035867 | 0.0036125 | 0.0036125 | 0.98891 | -0.24513 | 0.9889 | -0.24502 | 1.642
99 | -1.4035 | -0.64418 | 1.4036 | 0.64313 | 0.0001269 | -0.001055 | 0.045079 | 0.045066 | 0.045079 | 0.98891 | -0.24513 | 0.98899 | -0.24582 | 20.4904
100 | 1.1543 | 0.52897 | -1.1542 | -0.52962 | 5.2529e-05 | -0.0006524 | 0.037073 | 0.037081 | 0.037081 | 0.98868 | -0.24329 | 0.98864 | -0.24294 | 16.8552
101 | -1.8723 | -0.86756 | 1.8724 | 0.86715 | 9.1986e-05 | -0.0004163 | 0.060233 | 0.060228 | 0.060233 | 0.98899 | -0.24582 | 0.98904 | -0.24621 | 27.3787
102 | 0.37865 | 0.1822 | -0.37865 | -0.18253 | 2.8398e-06 | -0.00032925 | 0.012265 | 0.01227 | 0.01227 | 0.98899 | -0.24582 | 0.98898 | -0.24576 | 5.5771
103 | 0.090076 | 0.042239 | -0.090075 | -0.043625 | 6.7248e-07 | -0.0013865 | 0.0029039 | 0.0029213 | 0.0029213 | 0.98899 | -0.24582 | 0.98898 | -0.24576 | 1.3279
104 | 0.090305 | 0.042422 | -0.090305 | -0.043736 | 6.4204e-07 | -0.0013148 | 0.0029133 | 0.0029298 | 0.0029298 | 0.98864 | -0.24294 | 0.98864 | -0.24288 | 1.3317
105 | 0.37865 | 0.18253 | -0.37864 | -0.18338 | 7.3843e-06 | -0.00085508 | 0.01227 | 0.01228 | 0.01228 | 0.98898 | -0.24576 | 0.98897 | -0.24559 | 5.582
106 | -1.2747 | -0.51546 | 1.2747 | 0.51456 | 3.4259e-06 | -0.00089708 | 0.039779 | 0.039769 | 0.039779 | 0.99782 | -0.068285 | 0.99782 | -0.068217 | 4.7243

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.4314 | 5.7128

## res_load
| p_mw | q_mvar
0 | 0.24078 | 0.11662
1 | 0.29645 | 0.14358
2 | 0.37208 | 0.18021
3 | 0.096368 | 0.046673
4 | 0.29217 | 0.14151
5 | 0.29722 | 0.14395
6 | 0.16172 | 0.078322
7 | 0.15806 | 0.076551
8 | 0.18949 | 0.091774
9 | 0.22029 | 0.10669
10 | 0.075148 | 0.036396
11 | 0.12626 | 0.061149
12 | 0.24773 | 0.11998
13 | 0.24556 | 0.11893
14 | 0.3258 | 0.15779
15 | 0.071983 | 0.034863
16 | 0.7113 | 0.3445
17 | 0.1063 | 0.051483
18 | 0.1347 | 0.065236
19 | 0.12339 | 0.05976
20 | 0.38288 | 0.18544
21 | 0.41139 | 0.19924
22 | 0.33829 | 0.16384
23 | 0.18349 | 0.088869
24 | 0.33345 | 0.1615
25 | 0.38238 | 0.1852
26 | 0.24693 | 0.11959
27 | 0.31778 | 0.15391
28 | 0.10925 | 0.052911
29 | 0.25627 | 0.12412
30 | 0.41204 | 0.19956
31 | 0.077899 | 0.037728
32 | 0.20567 | 0.099611
33 | 0.25721 | 0.12457
34 | 0.33978 | 0.16456
35 | 0.41457 | 0.20079
36 | 0.27004 | 0.13079
37 | 0.3538 | 0.17135
38 | 0.34585 | 0.1675
39 | 0.36323 | 0.17592
40 | 0.17469 | 0.084606
41 | 0.21855 | 0.10585
42 | 0.20573 | 0.099641
43 | 0.23598 | 0.11429
44 | 0.084048 | 0.040706
45 | 0.21235 | 0.10285
46 | 0.3189 | 0.15445
47 | 0.081965 | 0.039698
48 | 0.09261 | 0.044853
49 | 0.13752 | 0.066604
50 | 0.11137 | 0.053941
51 | 0.090075 | 0.043625
52 | 0.090305 | 0.043736
53 | 0.37864 | 0.18338
54 | 0.22088 | 0.10697
55 | 0.21874 | 0.10594

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1